## EPS Inventory
Pos. | Invent.-No. | Code | Bldg-No. | Floor | Item | belonging to: | Manufacturer | Model-No.: / Ident-No.: | Capacity | Manufacture Year | Additional System Components | Remarks
1 | EPS 1 | GEN13 | Clay #01060 | Container | Diesel Engine I | Diesel-Generating | Iveco/Mecc alte | TNA 60-4 IWE 70183 | 48 kW; 60kVA | 2020 | 1 ea. Starter Batteries for Generator System ( ) exhaust system ( ) cooling system ( ) Diesel control cabinet ( ) Generator, devices and cabling Master control Panel, devices and cabling Load banks, load bank connections, load bank switches, and load bank cabinets Vaccuum leak detector for fuel tank and pipe and all connected and relevant items (e.g. pipes, valves, mech. & electr. switches etc.) | supplied 1062
[5 empty] | Fuel Oil Day Tank for Diesel Engine |  |  |  | 1000 l
[5 empty] | Generator |  | TNA |  | Power: 60kVA
Master Control Panel
2 | EPS 2 | 7850GEN1 | Haineberg PX #07850 | Technic-Room | Diesel Engine | Diesel-Generator-System | Perkins (Diesel Engine) / Perkins | Model: / Engine No.: | P= 800 kW; Speed: 1500/1800 rpm | 2014 | see above | supplied 7850
[5 empty] | Fuel Oil Day Tank for Diesel Engine | Diesel-Generator-System | Krampitz Tanksystem GmbH | Manufacturer-No.: | 0.98 m3
[5 empty] | Additional Fuel Oil Tank for Diesel Engine | Diesel-Generator-System | CEMO Tanksystem GmbH | Manufacturer-No.: | 2000 l
[5 empty] | secondary containment for Fuel Oil Day Tank for Diesel Engine | Diesel-Generator-System | Krampitz Tanksystem GmbH | Manufacturer-No.: | 1.09 m3
[5 empty] | Generator | Diesel-Generator-System | Kunzler Generators | Type: Model: | Power: 800 kVA
[5 empty] | Master Control Panel | for Generator ( ) | Kunzler | Type: Model:
|  |  |  | buried tank / outside | Fuel storage tank Steel cylinder tank | Diesel-Generator-System
3 | EPS 3 | GEN02 | Clay North #03377 | Outside | Diesel Engine | Diesel Engine | MTU (Diesel Engine) / MTU | Model: / Engine No.: | P= 1000 kW; Speed: 1500/1800 rpm | 2012 | s/a | Supplied also Bldg.: 03376, 03378, 03374, 01072, 03370, 03371, 03394, 03373 (Clay Nord) Not listed on Master Planing List ( Spindler).
[5 empty] | Generator | Generator |  | Type: Model: | Power: 1000 kVA
[5 empty] | Master Control Panel | Master Control Panel |  | Type: Model:
[5 empty] | Fuel tank | Fuel tank |  |  | 1000 l
4 | EPS 4 |  | Clay #01757 | Outside See ESP AECOM | Diesel Engine | Diesel Engine | Caterpillar | Type: Model: | Power: 500 KVA | 2007 | s/a
[5 empty] | Generator | Generator | Caterpillar | Type: Model:
[5 empty] | Master Control Panel | Master Control Panel | Caterpillar | Type: Model:
[5 empty] | Fuel tank | Fuel tank |  |  | 800 l
5 | EPS 5 | 7915GEN1 | Hainerberg #07915 | Outside See ESP AECOM | Diesel Engine I | Diesel-Generating | mecc alte | ECO38 2L4 | P= 300kVA; 240kW |  | s/a | Supplied Bldg.: 7315 SCHOOL Sprinkler,
[5 empty] | Fuel Oil Day Tank for Diesel Engine |  |  |  | 1500 l
[5 empty] | Generator |  | NEF67TM4.S500 |  | Power: 300kVA
Master Control Panel
6 | EPS 6 | 7560GEN1 | Kastel Annex #07560 | Kastel Annex Guard Check | Diesel Engine I | Diesel-Generating | Iveco/Mecc alte | TNA 60-4 IWE 70183 | P= 120 kW;150 kVA | 2024 | s/a | Kastel Annex Guard Check
[5 empty] | Fuel Oil Day Tank for Diesel Engine |  |  |  | 1000 l
[5 empty] | Generator |  | TNA |  | Power: 150kVA
Master Control Panel
7 | EPS 7 | GEN008 | Clay #01736 | #01036 Tower | Diesel Engine I | Diesel-Generating | Iveco/Mecc alte | TNA 60-4 IWE 70183 | P= 120 kW;150 kVA | 2024 | s/a | Tower #01036
[5 empty] | Fuel Oil Day Tank for Diesel Engine |  |  |  | 1000 l
[5 empty] | Generator |  | TNA |  | Power: 150kVA
Master Control Panel
8 | EPS 8 | 1050GEN1 | Clay #01050 | See ESP AECOM | Diesel Engine | Diesel Engine | DB | TA 3160S4 | 310 KVA | 2009 | s/a | Supplied also Bldg.: 01532/Clay,
[5 empty] | Generator | Generator | Leroy-Somer
[5 empty] | Master Control Panel | Master Control Panel
[5 empty] | Fuel tank | Fuel tank |  |  | 2000l Day Tank 300 l
9 | EPS 9 | 1086GEN1 | Clay Airfield #01086 | See ESP AECOM | Diesel Engine | Diesel Engine | MAN | D2542MLE | 400 KVA Speed: 1500/1800 rpm | 1986 | s/a | Supplied also Bldg.: 03005/Wasserwerk, 01686, 01036/Tower,
[5 empty] | Generator | Generator | AEG
[5 empty] | Master Control Panel | Master Control Panel
[5 empty] | Fuel tank | Fuel tank |  |  | 5000l Day Tank 300 l
10 | EPS 10 | 1059GEN1 | Clay #1059 | See ESP AECOM | Diesel Engine | Diesel Engine | FPT |  | 40kVA; 32kW | 2024 | s/a | Supplied also Bldg.: 01059
[5 empty] | Generator | Generator
[5 empty] | Master Control Panel | Master Control Panel
[5 empty] | Fuel tank | Fuel tank |  |  | 600 l
11 | EPS 11 | GEN12 | Clay AFN #01217 | See ESP AECOM | Diesel Engine | Diesel Engine | DB |  | 250 KVA Speed: 1500/1800 rpm | 1984 | s/a | Supplied also Bldg.: 01217, 01417/Clay,
[5 empty] | Generator | Generator | Leroy-Samer
[5 empty] | Master Control Panel | Master Control Panel
[5 empty] | Fuel tank | Fuel tank |  |  | 700 l
12 | EPS 12 | 1507GEN1 | Clay #01507 | Container Weiler | Diesel Engine | Diesel Engine | Deutz | 47.2047C6/4 | 500 KVA Speed: 1500/1800 rpm | 2005 | s/a | Supplied also Bldg.: 01007, 01008, 01009/Clay, and ACP Clay
| EPS 12.2 |  |  |  | Generator | Generator | Leroy-Samer
| EPS 12.3 |  |  |  | Master Control Panel | Master Control Panel
| EPS 12.4 |  |  |  | Fuel tank | Fuel tank |  |  | 4000 l + day tank 500 l
13 | EPS 13 | 5115GEN1 | AEC #05315 | Container | Diesel Engine | Diesel Engine | MTU |  | 850 KVA Speed: 1500/1800 rpm | 2007 | s/a | Supplied Bldg. 05301 AEC
| EPS 13.2 |  | AEC #05315 |  | Generator | Generator | Marelli
| EPS 13.3 |  | AEC #05315 |  | Master Control Panel | Master Control Panel
| EPS 13.4 |  | AEC #05315 |  | Fuel tank | Fuel tank |  |  | 12500l + day tank 500 l
14 | EPS 14 | 7898GEN1 | Haineberg Lodge #07898 | #07898 | Diesel Engine | Diesel Engine | Iveco |  | 450 KVA Speed: 1500/1800 rpm | 2010 | s/a | Supplied Bldg. 07890 HBG Lodge
| EPS 14.2 |  | Haineberg Lodge #07898 |  | Generator | Generator | Mecalte
| EPS 14.3 |  | Haineberg Lodge #07898 |  | Master Control Panel | Master Control Panel
| EPS 14.4 |  | Haineberg Lodge #07898 |  | Fuel tank | Fuel tank |  |  | 2000l Day Tank 250 l
15 | EPS 15 | 3341GEN1 | Clay North #03341 | #03341 | Diesel Engine | Diesel Engine | MTU | 12V 2000 G65 | 800kVA; 640kW | 2011 | s/a | 3340;3341
[5 empty] | Generator | Generator | Leroy-Somer
[5 empty] | Master Control Panel | Master Control Panel
[5 empty] | Fuel tank | Fuel tank |  |  | 8500l + day tank 750l
16 | EPS 16 | 1569GEN1 | Clay TACAN #01569 | #01569 | Diesel Engine | Diesel Engine | IVECO/Leroy Somer |  | 160kVA; 128 kW |  | s/a | Supplied Bldg. 1569 TACAN
[5 empty] | Generator | Generator | Leroy Somer
[5 empty] | Master Control Panel | Master Control Panel
[5 empty] | Fuel tank | Fuel tank |  |  | 1080 l
17 | EPS 17 | GEN10 | Clay Head Quarter #01205 | Container | Diesel Engine | Diesel Engine | Deutz |  | 104 kW |  | s/a | Supplied also Bldg.: 1205,1209 Not listed on Master Planing List ( Spindler). Listed as GEN01
| EPS 17.2 |  | Clay Head Quarter #01205 |  | Generator | Generator | Marelli
| EPS 17.3 |  | Clay Head Quarter #01205 |  | Master Control Panel | Master Control Panel
| EPS 17.4 |  | Clay Head Quarter #01205 |  | Fuel tank | Fuel tank |  |  | 2000l
18 | EPS 18 | GEN06 | Clay, Cont. Fire Department #01627 | #01627 | Diesel Engine | Diesel Engine | Iveco |  | 84 kW |  | s/a | Supplied also Bldg.: 1001,1002 and 1627 Not listed on Master Planing List ( Spindler). Listed as GEN06
| EPS 18.2 |  | Clay, Cont. Fire Department #01027 |  | Generator | Generator | Meccalte
| EPS 18.3 |  | Clay, Cont. Fire Department #01027 |  | Master Control Panel | Master Control Panel
| EPS 18.4 |  | Clay, Cont. Fire Department #01027 |  | Fuel tank | Fuel tank |  |  | 735l
19 | EPS 19 | HBACPGEN | Haineberg Guard Check #07821 | Near Guard Check | Diesel Engine | Diesel Engine | Deutz |  | 104 kW |  | s/a | Supplied also Bldg.: 07821-07825 Not listed on Master Planing List ( Spindler).
| EPS 19.2 |  | Haineberg Guard Check #07821 |  | Generator | Generator | Leroy-Somer
| EPS 19.3 |  | Haineberg Guard Check #07821 |  | Master Control Panel | Master Control Panel
| EPS 19.4 |  | Haineberg Guard Check #07821 |  | Fuel tank | Fuel tank |  |  | 500l
20 | EPS 20 | GEN10 | Clay North/ Wilson #01571 | ADN | Diesel Engine | Diesel Engine | FG Wilson |  | 48 kW |  | s/a | Supplied also Bldg.: 1571 Signal Not listed on Master Planing List ( Spindler). Listed as 01072
| EPS 20.2 |  | Clay North/ Wilson #01071 |  | Generator | Generator
| EPS 20.3 |  | Clay North/ Wilson #01071 |  | Master Control Panel | Master Control Panel
| EPS 20.4 |  | Clay North/ Wilson #01071 |  | Fuel tank | Fuel tank |  |  | 360l
21 | EPS 21 | 6208GEN1 | McCully Cont. #06208 | ADN Container | Diesel Engine | Diesel Engine | Iveco |  | 48 kW |  | s/a | Supplied Bldg.: 06208 Signal
| EPS 21.2 |  | McCully Cont. #06280 |  | Generator | Generator | Meccalte
| ESP 21.3 |  | McCully Cont. #06280 |  | Master Control Panel | Master Control Panel
| ESP 21.4 |  | McCully Cont. #06280 |  | Fuel tank | Fuel tank |  |  | 900l
22 | EPS 22 | 4062GEN1 | Kastel St. #04062 | ADN Container | Diesel Engine | Diesel Engine | Himoinsa - 75 T5 |  | 73kVA; 58kW |  | s/a | Supplied Bldg.: ADN Signal
| ESP 22.2 |  |  |  | Generator | Generator
| ESP 22.3 |  |  |  | Master Control Panel | Master Control Panel
| 22.4 |  |  |  | Fuel tank | Fuel tank |  |  | 300l
23 | EPS 23 | 4508GEN1 | Kastel St. #04508 |  | Diesel Engine | Diesel Engine | Iveco |  | 40kVA; 32kW |  | s/a | Supplied also Bldg.:ACP POND Guard/Wache
| 23.2 |  | Kastel St. #04508 |  | Generator | Generator | Meccalte
| 23.3 |  | Kastel St. #04508 |  | Master Control Panel | Master Control Panel
| 23.4 |  | Kastel St. #04508 |  | Fuel tank | Fuel tank |  |  | 500l
24 | EPS 24 |  | McCully Guard Check #07203 | Guard Check | Diesel Engine | Diesel Engine | Iveco |  | 40kVA; 32kW |  | s/a | Supplied also Bldg.: POND Guard/Wache Not listed on Master Planing List ( Spindler).
| 24.2 |  | McCully Guard Check #07203 |  | Generator | Generator | Meccalte
| 24.3 |  | McCully Guard Check #07203 |  | Master Control Panel | Master Control Panel
| 24.4 |  | McCully Guard Check #07203 |  | Fuel tank | Fuel tank |  |  | 60l
25 | EPS 25 |  | Haineberg Guard Check #07810 |  | Diesel Engine | Diesel Engine | Iveco |  | 40kVA; 32kW |  | s/a | Supplied also Bldg.: POND Guard/Wache
| 25.2 |  | Haineberg Guard Check #07762 |  | Generator | Generator | Meccalte
| 25.3 |  | Haineberg Guard Check #07762 |  | Master Control Panel | Master Control Panel
| 25.4 |  | Haineberg Guard Check #07762 |  | Fuel tank | Fuel tank |  |  | 500l
26 | EPS 26 | GEN10 | Clay North Cont. #01070 |  | Diesel Engine | Diesel Engine | Iveco |  | 60kVA; 48kW |  | s/a
| 26.2 |  | Clay North Cont. #01070 |  | Generator | Generator | Marelli
| 26.3 |  | Clay North Cont. #01070 |  | Master Control Panel | Master Control Panel
| 26.4 |  | Clay North Cont. #01070 |  | Fuel tank | Fuel tank |  |  | 500l
27 | EPS 27 | 4061GEN1 | Kastel St. #04061 | ADN Container | Diesel Engine | Diesel Engine | Himoinsa - 75 T5 |  | 73kVA; 58kW |  | s/a | Supplied Bldg.: AND 4061 Signal
| 26.2 |  | Clay North Cont. #01070 |  | Generator | Generator
| 26.3 |  | Clay North Cont. #01070 |  | Master Control Panel | Master Control Panel
| 26.4 |  | Clay North Cont. #01070 |  | Fuel tank | Fuel tank |  |  | 300l
28 | EPS 28 | 2604GEN1 | Egelsbach GEN Building #02604 |  | Diesel Engine | Diesel Engine | Caterpillar | SR4B Engine: 3512B |  |  | s/a
| 26.2 |  | Clay North Cont. #01070 |  | Generator | Generator
| 26.3 |  | Clay North Cont. #01070 |  | Master Control Panel | Master Control Panel
| 26.4 |  | Clay North Cont. #01070 |  | Fuel tank | Fuel tank
29 | EPS 29 | 2604GEN2 | Egelsbach GEN Building #02604 |  | Diesel Engine | Diesel Engine | Caterpillar | SR4B Engine: 3512B |  |  | s/a
| 26.2 |  | Clay North Cont. #01070 |  | Generator | Generator
| 26.3 |  | Clay North Cont. #01070 |  | Master Control Panel | Master Control Panel
| 26.4 |  | Clay North Cont. #01070 |  | Fuel tank | Fuel tank
30 | EPS 30 | 2604GEN3 | Egelsbach GEN Building #02604 |  | Diesel Engine | Diesel Engine | Caterpillar | SR4B Engine: 3512B |  |  | s/a
| 26.5 |  | Clay North Cont. #01070 |  | Generator | Generator
| 26.6 |  | Clay North Cont. #01070 |  | Master Control Panel | Master Control Panel
| 26.7 |  | Clay North Cont. #01071 |  | Fuel tank | Fuel tank
31 | EPS 31 |  | Clay #01761 | Mobile Container Polyma | Diesel Engine | Diesel Engine | Polyma |  | 250kVA |  | s/a | mob. GEN
| 26.8 |  |  |  | Generator | Generator
| 26.9 |  |  |  | Master Control Panel | Master Control Panel
| 26.10 |  |  |  | Fuel tank | Fuel tank

## Generatoren
Generatoren Wiesbaden Übersicht
Geb. | Installation | Ort | EPS | Structure/ GFEBS | Contract | supplied | MFG | Model | SN | Bj | Sprit | Ges.Tank | Haupttank | Tagestank | Stand L | Stand % | Ges.h | fehlt L | Rest.h | kVA | Leist. kW | Last kW | L.bank | Last % | l/h | l/72h | l/1Jahr | Wartung | Firma | Geb. | Ort | etc.
1060 | Clay | Flugleitung | 1 | GEN13 | DPW EPS&UPS | 1060 Flugleitung | TNA/ IVECO/mecc alte | TNA 60-4 IWE 70183 |  |  | Heizöl | 1000 | 1000 | x | 760 | 76 | 226.2443 | 190 | 171.9457 | 60 | 48 | 17 | 28.8 | 35.4167 | 5.27 | 379.44 | 442.68 | 2024 | Frerk | 1060 | Flugleitung
7850 | Hainerberg | PX | 2 | 7850GEN1 | DPW EPS&UPS | PX | Perkins/meccalte | DGDF6002 U19862X | 4006-23TAG3A | 2014 | SDiesel | 3000 | 2000 | 1000 | 1880 | 94 | 64.5161 | 20 | 61.9355 | 800 | 640 | 150 | 384 | 23.4375 | 46.5 | 3348 | 3906 | 2024 | Frerk | 7850 | Heinerberg PX
3377 | Clay | Nordseite MTU bl | 3 | GEN02 | DPW EPS&UPS | Sat-Com | MTU / Meccalte | 16V 2000 G65 | 536110790 |  | Heizöl | 1000 | 1000 | x | 900 | 90 | 54.6747 | 50 | 49.2072 | 1000 | 800 | 59 | 480 | 7.375 | 18.29 | 1316.88 | 1536.36 | 2024 | Frerk | 3377 | Nordseite MTU bl
1757 | Clay | mob. Zeppelin MA | 4 |  | DPW EPS&UPS | mobil | Cat/Zeppelin | 3412 TT | 81Z22389 | 1998 | Heizöl | 800 | 800 | x | 640 | 80 | 21.4823 | 120 | 17.1858 | 500 | 400 | 133 | 240 | 33.25 | 37.24 | 2681.28 | 3128.16 | 2023 | Frerk | 5 | mob. Zeppelin MA
7915 | Hainerberg | Elementary | 5 | 7915GEN1 | DPW EPS&UPS | 7915 | mecc alte | ECO38 2L4 | [11 empty] | 300 | 240 |  | 144
7560 | Kastel Annex | Guard Check | 6 | 7560GEN1 | DPW EPS&UPS | Kastel Annex Wache | FPT/Nidec | NEF67TM4.S500 | 1951729 | 2022 | Heizöl | 1500 | 1500 | x | 1425 | 95 | 288.4615 | 0 | 274.0385 | 150 | 120 | 20 | 72 | 16.6667 | 5.2 | 374.4 | 436.8 | 2024 | Frerk | 7560 | Kastel Annex Wache
1736 | Clay | Tower | 7 | GEN08 | DPW EPS&UPS | 1036 Tower | FPT/Reoy Somer | GX180F | 210419-1 | 2021 | Heizöl | 1040 |  |  | 1000 |  |  |  |  | 150 | 120 |  | 72 | [5 empty] | Frerk | 1036 | Betongeb. 1036
1050 | Clay | Gen. Shop | 8 | 1050GEN1 | DPW EPS&UPS | 1050.1532 | DB/Leroy-Somer | OM 404 A | 404.901-400-006607 | 1985 | Heizöl | 2500 | 2000 | 500 | 1650 | 82.5 | 230.4147 | 250 | 198.1567 | 310 | 248 | 35 | 148.8 | 14.1129 | 10.85 | 781.2 | 911.4 | 2024 | Frerk | 1050 | Gen. Shop
1086 | Clay | Airfield | 9 | 1086GEN1 | DPW EPS&UPS | 1086,Tow.,Airf.,1686,3005 | MAN/AEG | D2542 MLE | 347390/032 | 1986 | Heizöl | 5200 | 5000 | 200 | 4070 | 81.4 | 279.5699 | 680 | 229.5699 | 400 | 320 | 60 | 192 | 18.75 | 18.6 | 1339.2 | 1562.4 | 2024 | Frerk | 1086 | Airfield Thomas
1059 | Clay | EOC | 10 | 1059GEN1 | DPW EPS&UPS | 1059 EOC | FPT | NEF45AM1A.S500 | 2279909 | 2024 | Heizöl | 600 | 600 | x | 492 | 82 | 120.9677 | 78 | 99.1935 | 40 | 32 | 16 | 19.2 | 50 | 4.96 | 357.12 | 416.64 | 2024 | Frerk | 1059 | EOC | Nach Testlauf Display einschalten
1217 | Clay | AFN | 11 | GEN12 | DPW EPS&UPS | AFN, AND | DB |  |  |  | Heizöl | 700 | 700 | x | 455 | 65 | 76.9231 | 210 | 50 | 96 | 76.8 | 35 | 46.08 | 45.5729 | 9.1 | 655.2 | 764.4 | 2024 | Frerk | 1222 | AFN new
1507 | Clay | Cont. MA-Weiler | 12 | 1507GEN1 | DPW EPS&UPS | ACP,1007 - 1009 | Deutz/Leroy-Somer | BF8M 1015 CP | BF8M 1015 | 2005 | Heizöl | 4500 | 4000 | 500 | 3800 | 95 | 96.7742 | 0 | 92.4731 | 500 | 400 | 150 | 240 | 37.5 | 46.5 | 3348 | 3906 | 2024 | Frerk | 1507 | Cont. MA-Weiler
5315 | AEC | AEC 2 Cont,Grün | 13 | 5315GEN1 | DPW EPS&UPS | AEC | MTU/Marelli | 18V 2000 | 539 101 978 |  | Heizöl | 13000 | 12500 | 500 | 11000 | 88 | 209.6774 | 875 | 185.4839 | 800 | 640 | 200 | 384 | 31.25 | 62 | 4464 | 5208 | 2024 | Frerk | 5301 | AEC 2 Cont,Grün
7898 | Hainerberg | Lodge Hotel | 14 | 7898GEN1 | DPW EPS&UPS | Hotel | Iveco/Mecalte | F3AE9685B*E | 121105 | 2008 | Heizöl | 2250 | 2000 | 250 | 1900 | 95 | 330.8824 | 0 | 316.1765 | 400 | 320 | 17 | 192 | 5.3125 | 6.8 | 489.6 | 571.2 | 2024 | Frerk | 7890 | Heinerberg Hotel | wegen Probleme bei Lift Manager anfragen
3341 | Clay | Container NAU | 15 | 3341GEN3 | DPW EPS&UPS | NAU | MTU/Leroy-Somer | 12V 2000 G65 | 535 108 596 | 2011 | Heizöl | 9250 | 8500 | 750 | 7650 | 90 | 142.0891 | 425 | 117.5115 | 800 | 640 | 210 | 384 | 32.8125 | 65.1 | 4687.2 | 5468.4 | 2024 | Frerk | 3341 | Container NAU
1569 | Clay | Airfield Tacan | 16 | 1569GEN1 | DPW EPS&UPS | Tacan | Iveco/Leroy Somer |  |  |  | Heizöl | 1080 | 1080 | x | 990 | 91.6667 | 226.8908 | 36 | 207.9832 | 160 | 128 | 17 | 76.8 | 13.2812 | 4.76 | 342.72 | 399.84 | 2024 | Frerk | 1569 | Airfield Tacan | Tankanzeige def.
1205 | Clay | Command | 17 | GEN10 | DPW EPS&UPS | 1205.1209 | Deutz/Marelli |  |  |  | Heizöl | 2000 | 2000 | x | 1900 | 95 | 255.102 | 0 | 242.3469 | 130 | 104 | 28 | 62.4 | 26.9231 | 7.84 | 564.48 | 658.56 | 2024 | Frerk | 1205 | Command
1027 | Clay | Container Feuerwehr | 18 | GEN06 | DPW EPS&UPS | 100110021627 | Iveco/Meccalte |  |  |  | Heizöl | 735 | 735 | x | 661.5 | 90 | 47.1154 | 36.75 | 42.4038 | 105 | 84 | 60 | 50.4 | 71.4286 | 15.6 | 1123.2 | 1310.4 | 2024 | Frerk | 1027 | Container Feuerwehr | Bei Lastlauf Network Div. (Hausser) Informieren Blg.1627
7821 | Hainerberg | Guard Check | 19 | GEN02 | DPW EPS&UPS | Wache Ost 7821-7825 | Deutz/Leroy-Somer |  |  |  | Heizöl | 500 | 500 | x | 400 | 80 | 76.9231 | 75 | 61.5385 | 130 | 104 | 25 | 62.4 | 24.0385 | 6.5 | 468 | 546 | 2024 | Frerk | 7821 | Heinerbg. Wache O
1071 | Clay | Nordseite Wilson | 20 | GEN10 | DPW EPS&UPS | 1571 | FG Wilson |  |  |  | Heizöl | 360 | 360 | x | 324 | 90 | 75 | 18 | 67.5 | 60 | 48 | 16 | 28.8 | 33.3333 | 4.8 | 345.6 | 403.2 | 2024 | Frerk | 1071 | Nordseite Wilson
6280 | MCCully | Container Signal | 21 | 6280GEN1 | DPW EPS&UPS | Telefoner | Iveco/Creazzo |  |  |  | Heizöl | 300 | 300 | x | 240 | 80 | 46.1538 | 45 | 36.9231 | 85 | 68 | 25 | 40.8 | 36.7647 | 6.5 | 468 | 546 | 2024 | Frerk | 4008 | Kastel St.Tel. | Tankanzeige def.
4062 | Kastel Station | AND | 22 | 4062GEN1 | DPW EPS&UPS | AND Signal | Himoinsa | HFW - 75 T5 |  | 2024 | [9 empty] | 73 | 58.4 |  | 35.04
4508 | Kastel Station | Guard Check | 23 | 4508GEN1 | DPW EPS&UPS | Wache | Iveco/Meccalte |  |  |  | Heizöl | 500 | 500 | x | 450 | 90 | 96.1538 | 25 | 86.5385 | 40 | 32 | 20 | 19.2 | 62.5 | 5.2 | 374.4 | 436.8 | 2024 | Frerk | 4508 | Kastel St.Wache | Bei Lastlauf Strassenbel. Zuschalten, Auspuffklappe beachten
7203 | MCCully | Guard Check | 24 |  | DPW EPS&UPS | Wache | Iveco/Meccalte |  |  |  | Diesel | 60 | 60 | x | 38.4 | 64 | 15.3846 | 18.6 | 9.8462 | 40 | 32 | 15 | 19.2 | 46.875 | 3.9 | 280.8 | 327.6 | 2024 | Frerk | 7203 | McCully Wache | Wache bescheid sagen, Rampe und Schranken nicht benutzen
7810 | Hainerberg | Guard Check | 25 |  | DPW EPS&UPS | Wache (nicht besetzt) | Iveco/Meccalte |  |  |  | Heizöl | 500 | 500 | x | 300 | 60 | 128.2051 | 175 | 76.9231 | 40 | 32 | 15 | 19.2 | 46.875 | 3.9 | 280.8 | 327.6 | 2024 | Frerk | 7762 | Heinerberg Wache N | Bei Lastlauf Bel. zuschalten, Auspuffklappe beachten
1070 | Clay | Nord Cont. B. | 26 | GEN10 | DPW EPS&UPS | kein Anschluss | Iveco/Marelli |  |  |  | Heizöl | 700 | 700 | x | 595 | 85 | 168.2692 | 70 | 143.0288 | 60 | 48 | 16 | 28.8 | 33.3333 | 4.16 | 299.52 | 349.44 | 2024 | Frerk | 1070 | Nord Cont. B.
4061 | Kastel Station | AND | 27 | 4061GEN1 | DPW EPS&UPS | AND Signal | Himoinsa | HFW - 75 T5 |  | 2024 | [9 empty] | 73 | 58.4 |  | 35.04
2604 | Egelsbach | GEN Building | 28 | 2604GEN1 | DoD/E-Netze |  | Caterpillar | SR4B Engine: 3512B | GEN:8HM0599
2604 | Egelsbach | GEN Building | 29 | 2604GEN2 | DoD/E-Netze |  | Caterpillar | SR4B Engine: 3512B | GEN:8HM0598
2604 | Egelsbach | GEN Building | 30 | 2604GEN3 | DoD/E-Netze |  | Caterpillar | SR4B Engine: 3512B | GEN:8HM0597
1761 | Clay | Gen. Container | 31 |  | DoD/E-Netze |  | Polyma |  |  | 2025 | [9 empty] | 250kVA
1024 | Clay | Bushalte | N/A | 1024GEN1 | DPW SCIF | 1024 | WA | D 200 "S" | 1215310 | 2010 | Heizöl | 700 | 700 | x | 630 | 90 | 35.7143 | 35 | 32.1429 | 200 | 160 | 70 | 96 | 43.75 | 19.6 | 1411.2 | 1646.4 | 2023 | Frerk | 1024 | Bushalte
1000 | Clay | MCC 11 | N/A | 1000GEN1 | DPW SCIF | MCC | MTU/Marelli | 20V 4000 G23 | 528102001 | 2011 | Heizöl | 18666 | 16666 | 2000 | 15300 | 92.1687 | 150.5323 | 532.7 | 139.5161 | 2500 | 2000 | 400 | 1200 | 20 | 124 | 8928 | 10416 | 2022 | Frerk | 1000 | MCC 11
1000 | Clay | MCC 12 | N/A | 1000GEN1 | DPW SCIF | MCC | MTU/Marelli | 20V 4000 G23 | 528102002 | 2011 | Heizöl | 18666 | 16666 | 2000 | 15300 | 92.1687 | 150.5323 | 532.7 | 139.5161 | 2500 | 2000 | 400 | 1200 | 20 | 124 | 8928 | 10416 | 2022 | Frerk | 1000 | MCC 12
1000 | Clay | MCC 13 | N/A | 1000GEN1 | DPW SCIF | MCC | MTU/Marelli | 20V 4000 G23 | 528102003 | 2011 | Heizöl | 18666 | 16666 | 2000 | 15300 | 92.1687 | 150.5323 | 532.7 | 139.5161 | 2500 | 2000 | 400 | 1200 | 20 | 124 | 8928 | 10416 | 2022 | Frerk | 1000 | MCC 13
1183 | Clay | Shelter | N/A |  | DPW SCIF | 1183 | KHD Ansaldo |  |  |  | Heizöl | 500 | 500 | x | 100 | 20 | 192.3077 | 375 | 38.4615 | 40 | 32 | 10 | 19.2 | 31.25 | 2.6 | 187.2 | 218.4 |  |  | 1183 | Shelter
1186 | Clay | Shelter | N/A |  | DPW SCIF | 1186 | KHD Ansaldo |  |  |  | Heizöl | 500 | 500 | x | 125 | 25 | 192.3077 | 350 | 48.0769 | 40 | 32 | 10 | 19.2 | 31.25 | 2.6 | 187.2 | 218.4 |  |  | 1186 | Shelter
1191 | Clay | Shelter | N/A |  | DPW SCIF | 1191 | KHD/Ansaldo |  |  |  | Heizöl | 500 | 500 | x | 100 | 20 | 192.3077 | 375 | 38.4615 | 40 | 32 | 10 | 19.2 | 31.25 | 2.6 | 187.2 | 218.4 | 2082015 |  | 1191 | Shelter
1500 | Clay | IPC | N/A | 1500GEN1 | DPW SCIF | 1012,1812,1500 | MTU / Marelli | 16V 4000 G63 | 527 110 467 | 2013 | Heizöl | 31000 | 30000 | 1000 | 27000 | 90 | 259.7403 | 1500 | 234.6041 | 1856 | 1484.8 | 385 | 890.88 | 25.9294 | 119.35 | 8593.2 | 10025.4 | 2022 | Frerk | 1500 | IPC
77695 | Hainerberg | Commissary | N/A |  | DoD/IMCOM
4367 | Dagger | 4367 | N/A | 4367GEN1 | E-Netze | Dagger | AvK | DSG 62M2-4 | 6622307 A001 | [7 empty] | 154
4367 | Dagger | 4367 | N/A | 4367GEN2 | E-Netze | Dagger | AvK | DSG 62M2-4 | 6622307 A002 | [7 empty] | 150
4367 | Dagger | 4367 | N/A | 4367GEN3 | E-Netze | Dagger | AvK | DSG 62M2-4 | 6622307 A003 | [7 empty] | 148
4367 | Dagger | 4367 | N/A | 4367GEN4 | E-Netze | Dagger | Marelli | MJB 355SA4 B | MZ18513 | [7 empty] | 149
4367 | Dagger | GEN Area | N/A | GEN1 | E-Netze | Dagger | Marelli | V375A | 6664/1
4367 | Dagger | GEN Area | N/A | GEN2 | E-Netze | Dagger | Marelli | V375A | 6664/2
.

## Leistung Last
Leistung und Verbraucherleistung der Generatoren DPW Wiesbaden
Geb./Nr. | Ort | EPS | Datum | Versorgt | MFG | kVA | kW | Verbr. kW | Verbr. %
5 | mob. Zeppelin MA | 4.1 | 2024-09-11 | mobil | Cat/Zeppelin | 500 | 400 | 133 | 33.25
1000 | MCC 11 | x | 2024-10-23 | MCC | MTU/Marelli | 2500 | 2000 | 400 | 20
1000 | MCC 12 | x | 2024-10-23 | MCC | MTU/Marelli | 2500 | 2000 | 400 | 20
1000 | MCC 13 | x | 2024-10-23 | MCC | MTU/Marelli | 2500 | 2000 | 400 | 20
1024 | Bushalte | 5.1 | 2024-10-02 | 1024 | WA | 200 | 160 | 70 | 43.75
1027 | Container Feuerwehr | 18.1 | 2024-10-02 | 1001,1002,1627 | Iveco/Meccalte | 105 | 84 | 60 | 71.4286
1050 | Gen. Shop | 8.1 | 2024-10-15 | 1050.1532 | DB/Leroy-Somer | 310 | 248 | 35 | 14.1129
1059 | EOC | x | 2024-10-29 | 1059 EOC | FPT | 40 | 32 | 16 | 50
1060 | Flugleitung | 1.1 | 2024-10-07 | 1060 Flugleitung | 0 | 60 | 48 | 17 | 35.4167
1070 | Nord Cont. B. | 26.1 | 2024-10-28 | kein Anschluss | Iveco/Marelli | 60 | 48 | 16 | 33.3333
1071 | Nordseite Wilson | 20.1 | 2024-10-28 | 1571 | FG Wilson | 60 | 48 | 16 | 33.3333
1086 | Airfield Thomas | 9.1 | 2024-10-16 | 1086,Tow.,Airf.,1686,3005 | MAN/AEG | 400 | 320 | 60 | 18.75
1183 | Shelter | x | 2024-10-29 | 1183 | KHD Ansaldo | 40 | 32 | 10 | 31.25
1186 | Shelter | x | 2024-10-29 | 1186 | KHD Ansaldo | 40 | 32 | 10 | 31.25
1191 | Shelter | x | 2024-10-30 | 1191 | KHD/Ansaldo | 40 | 32 | 10 | 31.25
1205 | Command | 17.1 | 2024-10-09 | 1205.1209 | Deutz/Marelli | 130 | 104 | 28 | 26.9231
1222 | AFN | 11.1 | 2024-10-09 | AFN, AND | 0 | 96 | 76.8 | 35 | 45.5729
1500 | IPC | x | 2024-10-07 | 1012,1812,1500 | MTU / Marelli | 1856 | 1484.8 | 385 | 25.9294
1507 | Cont. MA-Weiler | 12.1 | 2024-10-08 | ACP,1007 - 1009 | Deutz/Leroy-Somer | 500 | 400 | 150 | 37.5
1569 | Airfield Tacan | 16.1 | 2024-10-17 | Tacan | Iveco/Leroy Somer | 160 | 128 | 17 | 13.2812
3341 | Container NAU | 15.1 | 2024-10-30 | NAU | MTU/Leroy-Somer | 800 | 640 | 210 | 32.8125
3377 | Nordseite MTU bl | 3.1 | 2024-10-31 | Sat-Com | MTU / Meccalte | 1000 | 800 | 59 | 7.375
4008 | Kastel St.Tel. | 22.1 | 2024-10-01 | Telefoner | Iveco/Creazzo | 85 | 68 | 25 | 36.7647
4508 | Kastel St.Wache | 23.1 | 2024-10-01 | Wache | Iveco/Meccalte | 40 | 32 | 20 | 62.5
5301 | AEC 2 Cont,Grün | 13.1 | 2024-10-23 | AEC | MTU/Marelli | 800 | 640 | 200 | 31.25
6208 | McCully Cont. Tel. | 21.1 | 2024-10-01 | Telefoner | Iveco/Meccalte | 60 | 48 | 25 | 52.0833
7203 | McCully Wache | 24.1 | 2024-10-01 | Wache | Iveco/Meccalte | 40 | 32 | 15 | 46.875
7560 | Kastel Annex Wache | x | 2024-10-30 | Kastel Annex Wache | FPT/Nidec | 150 | 120 | 20 | 16.6667
7762 | Heinerberg Wache N | 25.1 | 2024-10-21 | Wache (nicht besetzt) | Iveco/Meccalte | 40 | 32 | 15 | 46.875
7821 | Heinerbg. Wache O | 19.1 | 2024-10-22 | Wache Ost 7821-7825 | Deutz/Leroy-Somer | 130 | 104 | 25 | 24.0385
7850 | Heinerberg PX | 2.1 | 2024-10-22 | PX | Perkins/meccalte | 800 | 640 | 150 | 23.4375
7890 | Heinerberg Hotel | 14.1 | 2024-10-22 | Hotel | Iveco/Mecalte | 400 | 320 | 17 | 5.3125
1761 | 1761 | 31 |  | mob. Gen. | Polyma | 250
Formulas:
Datum = [1]Generatoren!D4

## Tanks Verbrauch
Generatoren Tanks Leistung und Verbrauch
Ort |  |  | Datum | Tank | [6 empty] | Leistung |  |  | Zeit
Geb. | Ort | EPS | Check | Sprit | Ges.Tank | Haupttank | Tagestank | Stand L | Stand % | fehlt L | Leist. kW | Last kW | Last % | Ges.h | Rest.h | l/h | l/72h | l/1Jahr
5 | mob. Zeppelin MA | 4.1 | 2024-09-11 | Heizöl | 800 | 800 | x | 640 | 80 | 120 | 400 | 133 | 33.25 | 21.4823 | 17.1858 | 37.24 | 2681.28 | 3128.16
1000 | MCC 11 | x | 2024-10-23 | Heizöl | 18666 | 16666 | 2000 | 15300 | 92.1687 | 532.7 | 2000 | 400 | 20 | 150.5323 | 139.5161 | 124 | 8928 | 10416
1000 | MCC 12 | x | 2024-10-23 | Heizöl | 18666 | 16666 | 2000 | 15300 | 92.1687 | 532.7 | 2000 | 400 | 20 | 150.5323 | 139.5161 | 124 | 8928 | 10416
1000 | MCC 13 | x | 2024-10-23 | Heizöl | 18666 | 16666 | 2000 | 15300 | 92.1687 | 532.7 | 2000 | 400 | 20 | 150.5323 | 139.5161 | 124 | 8928 | 10416
1024 | Bushalte | 5.1 | 2024-10-02 | Heizöl | 700 | 700 | x | 630 | 90 | 35 | 160 | 70 | 43.75 | 35.7143 | 32.1429 | 19.6 | 1411.2 | 1646.4
1027 | Container Feuerwehr | 18.1 | 2024-10-02 | Heizöl | 735 | 735 | x | 661.5 | 90 | 36.75 | 84 | 60 | 71.4286 | 47.1154 | 42.4038 | 15.6 | 1123.2 | 1310.4
1050 | Gen. Shop | 8.1 | 2024-10-15 | Heizöl | 2500 | 2000 | 500 | 1650 | 82.5 | 250 | 248 | 35 | 14.1129 | 230.4147 | 198.1567 | 10.85 | 781.2 | 911.4
1059 | EOC | x | 2024-10-29 | Heizöl | 600 | 600 | x | 492 | 82 | 78 | 32 | 16 | 50 | 120.9677 | 99.1935 | 4.96 | 357.12 | 416.64
1060 | Flugleitung | 1.1 | 2024-10-07 | Heizöl | 1000 | 1000 | x | 760 | 76 | 190 | 48 | 17 | 35.4167 | 226.2443 | 171.9457 | 5.27 | 379.44 | 442.68
1070 | Nord Cont. B. | 26.1 | 2024-10-28 | Heizöl | 700 | 700 | x | 595 | 85 | 70 | 48 | 16 | 33.3333 | 168.2692 | 143.0288 | 4.16 | 299.52 | 349.44
1071 | Nordseite Wilson | 20.1 | 2024-10-28 | Heizöl | 360 | 360 | x | 324 | 90 | 18 | 48 | 16 | 33.3333 | 75 | 67.5 | 4.8 | 345.6 | 403.2
1086 | Airfield Thomas | 9.1 | 2024-10-16 | Heizöl | 5200 | 5000 | 200 | 4070 | 81.4 | 680 | 320 | 60 | 18.75 | 279.5699 | 229.5699 | 18.6 | 1339.2 | 1562.4
1183 | Shelter | x | 2024-10-29 | Heizöl | 500 | 500 | x | 100 | 20 | 375 | 32 | 10 | 31.25 | 192.3077 | 38.4615 | 2.6 | 187.2 | 218.4
1186 | Shelter | x | 2024-10-29 | Heizöl | 500 | 500 | x | 125 | 25 | 350 | 32 | 10 | 31.25 | 192.3077 | 48.0769 | 2.6 | 187.2 | 218.4
1191 | Shelter | x | 2024-10-30 | Heizöl | 500 | 500 | x | 100 | 20 | 375 | 32 | 10 | 31.25 | 192.3077 | 38.4615 | 2.6 | 187.2 | 218.4
1205 | Command | 17.1 | 2024-10-09 | Heizöl | 2000 | 2000 | x | 1900 | 95 | 0 | 104 | 28 | 26.9231 | 255.102 | 242.3469 | 7.84 | 564.48 | 658.56
1222 | AFN | 11.1 | 2024-10-09 | Heizöl | 700 | 700 | x | 455 | 65 | 210 | 76.8 | 35 | 45.5729 | 76.9231 | 50 | 9.1 | 655.2 | 764.4
1500 | IPC | x | 2024-10-07 | Heizöl | 31000 | 30000 | 1000 | 27000 | 90 | 1500 | 1484.8 | 385 | 25.9294 | 259.7403 | 234.6041 | 119.35 | 8593.2 | 10025.4
1507 | Cont. MA-Weiler | 12.1 | 2024-10-08 | Heizöl | 4500 | 4000 | 500 | 3800 | 95 | 0 | 400 | 150 | 37.5 | 96.7742 | 92.4731 | 46.5 | 3348 | 3906
1569 | Airfield Tacan | 16.1 | 2024-10-17 | Heizöl | 1080 | 1080 | x | 990 | 91.6667 | 36 | 128 | 17 | 13.2812 | 226.8908 | 207.9832 | 4.76 | 342.72 | 399.84
3341 | Container NAU | 15.1 | 2024-10-30 | Heizöl | 9250 | 8500 | 750 | 7650 | 90 | 425 | 640 | 210 | 32.8125 | 142.0891 | 117.5115 | 65.1 | 4687.2 | 5468.4
3377 | Nordseite MTU bl | 3.1 | 2024-10-31 | Heizöl | 1000 | 1000 | x | 900 | 90 | 50 | 800 | 59 | 7.375 | 54.6747 | 49.2072 | 18.29 | 1316.88 | 1536.36
4008 | Kastel St.Tel. | 22.1 | 2024-10-01 | Heizöl | 300 | 300 | x | 240 | 80 | 45 | 68 | 25 | 36.7647 | 46.1538 | 36.9231 | 6.5 | 468 | 546
4508 | Kastel St.Wache | 23.1 | 2024-10-01 | Heizöl | 500 | 500 | x | 450 | 90 | 25 | 32 | 20 | 62.5 | 96.1538 | 86.5385 | 5.2 | 374.4 | 436.8
5301 | AEC 2 Cont,Grün | 13.1 | 2024-10-23 | Heizöl | 13000 | 12500 | 500 | 11000 | 88 | 875 | 640 | 200 | 31.25 | 209.6774 | 185.4839 | 62 | 4464 | 5208
6208 | McCully Cont. Tel. | 21.1 | 2024-10-01 | Heizöl | 900 | 700 | 200 | 560 | 80 | 105 | 48 | 25 | 52.0833 | 138.4615 | 116.9231 | 6.5 | 468 | 546
7203 | McCully Wache | 24.1 | 2024-10-01 | Diesel | 60 | 60 | x | 38.4 | 64 | 18.6 | 32 | 15 | 46.875 | 15.3846 | 9.8462 | 3.9 | 280.8 | 327.6
7560 | Kastel Annex Wache | x | 2024-10-30 | Heizöl | 1500 | 1500 | x | 1425 | 95 | 0 | 120 | 20 | 16.6667 | 288.4615 | 274.0385 | 5.2 | 374.4 | 436.8
7762 | Heinerberg Wache N | 25.1 | 2024-10-21 | Heizöl | 500 | 500 | x | 300 | 60 | 175 | 32 | 15 | 46.875 | 128.2051 | 76.9231 | 3.9 | 280.8 | 327.6
7821 | Heinerbg. Wache O | 19.1 | 2024-10-22 | Heizöl | 500 | 500 | x | 400 | 80 | 75 | 104 | 25 | 24.0385 | 76.9231 | 61.5385 | 6.5 | 468 | 546
7850 | Heinerberg PX | 2.1 | 2024-10-22 | SDiesel | 3000 | 2000 | 1000 | 1880 | 94 | 20 | 640 | 150 | 23.4375 | 64.5161 | 61.9355 | 46.5 | 3348 | 3906
7890 | Heinerberg Hotel | 14.1 | 2024-10-22 | Heizöl | 2250 | 2000 | 250 | 1900 | 95 | 0 | 320 | 17 | 5.3125 | 330.8824 | 316.1765 | 6.8 | 489.6 | 571.2
Formulas:
Datum = [1]Generatoren!D4

## BlackBuilding
Black Building Test
BLDG | Installation | Floor | EPS | Structure/ GFEBS | Contract | supplied | Year | fuel | kVA | Power kW | Load kW | L.bank | Load% | l/h | Last BBT | etc.
1060 | Clay | Flugleitung | 1 | GEN13 | DPW EPS&UPS | 1060 Flugleitung |  | fuel oil | 60 | 48 | 17 | 28.8 | 35.4167 | 5.27
7850 | Hainerberg | PX | 2 | 7850GEN1 | DPW EPS&UPS | PX | 2014 | diesel | 800 | 640 | 150 | 384 | 23.4375 | 46.5
3377 | Clay | Nordseite MTU bl | 3 | GEN02 | DPW EPS&UPS | Sat-Com |  | fuel oil | 1000 | 800 | 59 | 480 | 7.375 | 18.29
1757 | Clay | mob. Zeppelin MA | 4 |  | DPW EPS&UPS | mobil | 1998 | fuel oil | 500 | 400 | 133 | 240 | 33.25 | 37.24
7915 | Hainerberg | Elementary | 5 | 7915GEN1 | DPW EPS&UPS | 7915 |  |  | 300 | 240 |  | 144
7560 | K. Annex | Guard Check | 6 | 7560GEN1 | DPW EPS&UPS | Kastel Annex Wache | 2022 | fuel oil | 150 | 120 | 20 | 72 | 16.6667 | 5.2
1036 | Clay | Tower | 7 | GEN08 | DPW EPS&UPS | 1036 Tower | 2021 | fuel oil | 150 | 120 |  | 72
1050 | Clay | Gen. Shop | 8 | 1050GEN1 | DPW EPS&UPS | 1050.1532 | 1985 | fuel oil | 310 | 248 | 35 | 148.8 | 14.1129 | 10.85
1086 | Clay | Airfield | 9 | 1086GEN1 | DPW EPS&UPS | 1086,Tow.,Airf.,1686,3005 | 1986 | fuel oil | 400 | 320 | 60 | 192 | 18.75 | 18.6
1059 | Clay | EOC | 10 | 1059GEN1 | DPW EPS&UPS | 1059 EOC | 2024 | fuel oil | 40 | 32 | 16 | 19.2 | 50 | 4.96
1222 | Clay | AFN | 11 | GEN12 | DPW EPS&UPS | AFN, ADN |  | fuel oil | 96 | 76.8 | 35 | 46.08 | 45.5729 | 9.1
1507 | Clay | Cont. MA-Weiler | 12 | 1507GEN1 | DPW EPS&UPS | ACP,1007 - 1009 | 2005 | fuel oil | 500 | 400 | 150 | 240 | 37.5 | 46.5
5315 | AEC | AEC 2 Cont,Grün | 13 | 5315GEN1 | DPW EPS&UPS | AEC |  | fuel oil | 800 | 640 | 200 | 384 | 31.25 | 62
7898 | Hainerberg | Lodge Hotel | 14 | 7898GEN1 | DPW EPS&UPS | Hotel | 2008 | fuel oil | 400 | 320 | 17 | 192 | 5.3125 | 6.8
3341 | Clay | Container NAU | 15 | 3341GEN3 | DPW EPS&UPS | NAU | 2011 | fuel oil | 800 | 640 | 210 | 384 | 32.8125 | 65.1
1569 | Clay | Airfield Tacan | 16 | 1569GEN1 | DPW EPS&UPS | Tacan |  | fuel oil | 160 | 128 | 17 | 76.8 | 13.2812 | 4.76
1205 | Clay | Commander | 17 | GEN10 | DPW EPS&UPS | 1205.1209 |  | fuel oil | 130 | 104 | 28 | 62.4 | 26.9231 | 7.84
1027 | Clay | Container Feuerwehr | 18 | GEN06 | DPW EPS&UPS | 100110021627 |  | fuel oil | 105 | 84 | 60 | 50.4 | 71.4286 | 15.6
7821 | Hainerberg | Guard Check | 19 | GEN02 | DPW EPS&UPS | Wache Ost 7821-7825 |  | fuel oil | 130 | 104 | 25 | 62.4 | 24.0385 | 6.5
1071 | Clay | Nordseite Wilson | 20 | GEN10 | DPW EPS&UPS | 1571 |  | fuel oil | 60 | 48 | 16 | 28.8 | 33.3333 | 4.8
6280 | MCCully | Container Signal | 21 | 6280GEN1 | DPW EPS&UPS | Telefoner |  | fuel oil | 85 | 68 | 25 | 40.8 | 36.7647 | 6.5
4062 | K. Station | ADN | 22 | 4062GEN1 | DPW EPS&UPS | ADN Signal | 2024 |  | 73 | 58.4 |  | 35.04
4508 | K. Station | Guard Check | 23 | 4508GEN1 | DPW EPS&UPS | Wache |  | fuel oil | 40 | 32 | 20 | 19.2 | 62.5 | 5.2
7203 | MCCully | Guard Check | 24 |  | DPW EPS&UPS | Wache |  | diesel | 40 | 32 | 15 | 19.2 | 46.875 | 3.9
7762 | Hainerberg | Guard Check | 25 |  | DPW EPS&UPS | Wache (nicht besetzt) |  | fuel oil | 40 | 32 | 15 | 19.2 | 46.875 | 3.9
1070 | Clay | Nord Cont. B. | 26 | GEN10 | DPW EPS&UPS | kein Anschluss |  | fuel oil | 60 | 48 | 16 | 28.8 | 33.3333 | 4.16
4061 | K. Station | ADN | 27 | 4061GEN1 | DPW EPS&UPS | ADN Signal | 2024 |  | 73 | 58.4 |  | 35.04
2604 | Egelsbach | GEN Building | 28 | 2604GEN1 | DoD/E-Netze
2604 | Egelsbach | GEN Building | 29 | 2604GEN2 | DoD/E-Netze
2604 | Egelsbach | GEN Building | 30 | 2604GEN3 | DoD/E-Netze
1761 | Clay | Gen. Container | 31 |  | DoD/E-Netze |  | 2025 |  | 250kVA
1024 | Clay | Bushalte | N/A | 1024GEN1 | DPW SCIF | 1024 | 2010 | fuel oil | 200 | 160 | 70 | 96 | 43.75 | 19.6 | 2023
1000 | Clay | MCC 11 | N/A | 1000GEN1 | DPW SCIF | MCC | 2011 | fuel oil | 2500 | 2000 | 400 | 1200 | 20 | 124 | 2022
1000 | Clay | MCC 12 | N/A | 1000GEN1 | DPW SCIF | MCC | 2011 | fuel oil | 2500 | 2000 | 400 | 1200 | 20 | 124 | 2022
1000 | Clay | MCC 13 | N/A | 1000GEN1 | DPW SCIF | MCC | 2011 | fuel oil | 2500 | 2000 | 400 | 1200 | 20 | 124 | 2022
1183 | Clay | Shelter | N/A |  | DPW SCIF | 1183 |  | fuel oil | 40 | 32 | 10 | 19.2 | 31.25 | 2.6
1186 | Clay | Shelter | N/A |  | DPW SCIF | 1186 |  | fuel oil | 40 | 32 | 10 | 19.2 | 31.25 | 2.6
1191 | Clay | Shelter | N/A |  | DPW SCIF | 1191 |  | fuel oil | 40 | 32 | 10 | 19.2 | 31.25 | 2.6 | 2082015
1500 | Clay | IPC | N/A | 1500GEN1 | DPW SCIF | 1012,1812,1500 | 2013 | fuel oil | 1856 | 1484.8 | 385 | 890.88 | 25.9294 | 119.35 | 2022
77695 | Hainerberg | Commissary | N/A |  | DoD/IMCOM
4367 | Dagger | 4367 | N/A | 4367GEN1 | E-Netze | Dagger
4367 | Dagger | 4367 | N/A | 4367GEN2 | E-Netze | Dagger
4367 | Dagger | 4367 | N/A | 4367GEN3 | E-Netze | Dagger
4367 | Dagger | 4367 | N/A | 4367GEN4 | E-Netze | Dagger
4367 | Dagger | GEN Area | N/A | GEN1 | E-Netze | Dagger
4367 | Dagger | GEN Area | N/A | GEN2 | E-Netze | Dagger
Black Building Test BBT USAG
BLDG | Installation | Floor | EPS | Structure/ GFEBS | Contract | supplied | BBT schedule
1060 | Clay | Flugleitung | 1 | GEN13 | DPW EPS&UPS | 1060 Base ops
7850 | Hainerberg | PX | 2 | 7850GEN1 | DPW EPS&UPS | PX
3377 | Clay | Nordseite MTU bl | 3 | GEN02 | DPW EPS&UPS | Sat-Com
1757 | Clay | mob. Zeppelin MA | 4 |  | DPW EPS&UPS | mobil | [10 empty] | .
7915 | Hainerberg | Elementary | 5 | 7915GEN1 | DPW EPS&UPS | 7915
7560 | K. Annex | Guard Check | 6 | 7560GEN1 | DPW EPS&UPS | Kastel Annex POND
1036 | Clay | Tower | 7 | GEN08 | DPW EPS&UPS | 1036 Tower
1050 | Clay | Gen. Shop | 8 | 1050GEN1 | DPW EPS&UPS | 1050.1532
1086 | Clay | Airfield | 9 | 1086GEN1 | DPW EPS&UPS | 1086,Tow.,Airf.,1686,3005
1059 | Clay | EOC | 10 | 1059GEN1 | DPW EPS&UPS | 1059 EOC
1222 | Clay | AFN | 11 | GEN12 | DPW EPS&UPS | AFN, ADN
1507 | Clay | Cont. MA-Weiler | 12 | 1507GEN1 | DPW EPS&UPS | ACP,1007 - 1009
5315 | AEC | AEC 2 Cont,Grün | 13 | 5315GEN1 | DPW EPS&UPS | AEC
7898 | Hainerberg | Lodge Hotel | 14 | 7898GEN1 | DPW EPS&UPS | Hotel
3341 | Clay | Container NAU | 15 | 3341GEN3 | DPW EPS&UPS | NAU
1569 | Clay | Airfield Tacan | 16 | 1569GEN1 | DPW EPS&UPS | Tacan
1205 | Clay | Commander | 17 | GEN10 | DPW EPS&UPS | 1205.1209
1027 | Clay | Container Feuerwehr | 18 | GEN06 | DPW EPS&UPS | 100110021627
7821 | Hainerberg | Guard Check | 19 | GEN02 | DPW EPS&UPS | Guard Ost 7821-7825
1071 | Clay | Nordseite Wilson | 20 | GEN10 | DPW EPS&UPS | 1571
6280 | MCCully | Container Signal | 21 | 6280GEN1 | DPW EPS&UPS | Telephone/Signal
4062 | K. Station | ADN | 22 | 4062GEN1 | DPW EPS&UPS | ADN Signal
4508 | K. Station | Guard Check | 23 | 4508GEN1 | DPW EPS&UPS | POND
7203 | MCCully | Guard Check | 24 |  | DPW EPS&UPS | POND
7762 | Hainerberg | Guard Check | 25 |  | DPW EPS&UPS | POND
1070 | Clay | Nord Cont. B. | 26 | GEN10 | DPW EPS&UPS
4061 | K. Station | ADN | 27 | 4061GEN1 | DPW EPS&UPS | ADN Signal
2604 | Egelsbach | GEN Building | 28 | 2604GEN1 | DoD/E-Netze
2604 | Egelsbach | GEN Building | 29 | 2604GEN2 | DoD/E-Netze
2604 | Egelsbach | GEN Building | 30 | 2604GEN3 | DoD/E-Netze
1761 | Clay | Gen. Container | 31 |  | DoD/E-Netze
1024 | Clay | Bus station | N/A | 1024GEN1 | DPW SCIF | 1024
1000 | Clay | MCC 11 | N/A | 1000GEN1 | DPW SCIF | MCC
1000 | Clay | MCC 12 | N/A | 1000GEN1 | DPW SCIF | MCC
1000 | Clay | MCC 13 | N/A | 1000GEN1 | DPW SCIF | MCC
1183 | Clay | Shelter | N/A |  | DPW SCIF | 1183
1186 | Clay | Shelter | N/A |  | DPW SCIF | 1186
1191 | Clay | Shelter | N/A |  | DPW SCIF | 1191
1500 | Clay | IPC | N/A | 1500GEN1 | DPW SCIF | 1012,1812,1500
77695 | Hainerberg | Commissary | N/A |  | DoD/IMCOM
4367 | Dagger | 4367 | N/A | 4367GEN1 | E-Netze | Dagger
4367 | Dagger | 4367 | N/A | 4367GEN2 | E-Netze | Dagger
4367 | Dagger | 4367 | N/A | 4367GEN3 | E-Netze | Dagger
4367 | Dagger | 4367 | N/A | 4367GEN4 | E-Netze | Dagger
4367 | Dagger | GEN Area | N/A | GEN1 | E-Netze | Dagger
4367 | Dagger | GEN Area | N/A | GEN2 | E-Netze | Dagger