| SUBJECT* | Repair Compressor for AHU 21 Chiller |
| --- | --- |

GENERAL INFORMATION

| CONTRACTING OFFICE’S ZIP CODE* | 06516 |
| --- | --- |
| SOLICITATION NUMBER* | 36C24126Q0426 |
| RESPONSE DATE/TIME/ZONE | 05-19-2026 5:00 PM EASTERN TIME, NEW YORK, USA |
| ARCHIVE | 30 DAYS AFTER THE RESPONSE DATE |
| RECOVERY ACT FUNDS | N |
| SET-ASIDE | SDVOSBC |
| PRODUCT SERVICE CODE* | Z1DA |
| NAICS CODE* | 811310 |
| CONTRACTING OFFICE ADDRESS | Department of Veterans Affairs VA Connecticut 950 Campbell Avenue West Haven CT 06516 |
| POINT OF CONTACT* | Contract Specialist Kenya R Mitchell Kenya.Mitchell1@va.gov 860-666-6951 |

PLACE OF PERFORMANCE

| ADDRESS | Togus VAMC |
| --- | --- |
|  | 1 VA Center |
|  | Augusta ME |
| POSTAL CODE | 04330 |
| COUNTRY | USA |

ADDITIONAL INFORMATION

| AGENCY’S URL |  |
| --- | --- |
| URL DESCRIPTION |  |
| AGENCY CONTACT’S EMAIL ADDRESS | Kenya.Mitchell1@va.gov |
| EMAIL DESCRIPTION |  |

DESCRIPTION

#### THE PURPOSE OF THIS AMENDMENT IS TO:


1. Schedule site visit
 
	14, May 2026 at 10:00 AM 
	Togus VA Medical Center
	1 VA Center
	Augusta, ME 04330
	Building B200E
	POC: Abigail Campbell

#### 2.Respond to question received:

I am writing to request clarification regarding the compressor replacement for AHU 21 Chiller. Specifically, we would like to confirm whether the compressor can be isolated during the replacement process, or if the addition of new refrigerant will be required.

Isolating the compressor during replacement is not possible. The refrigerant from the entire circuit must be recovered and, because of the nature of the failure, cannot be reused. Additionally, during installation, the oil equalizer line will need to be drained, and fresh oil should be added to the circuit to ensure proper system functionality

3. Extend the submission due date

Submission of your response shall be received not later than Tuesday, 19 May 2026 by 5:00 PM EST.

Late submissions shall be treated in accordance with the solicitation provision at FAR 52.212-1(f).

Any questions or concerns regarding this solicitation should be forwarded in writing via e-mail to the Point of Contact listed below.

#### Point of Contact

Kenya.Mitchell1@va.gov

See attached document: Attachment - Togus Campus Map.

See attached document: Attachment -PIV Badge Template.

See attached document: FAR 52.212-1-Instructions to Offerors Commercial Products and Commercial Services.

See attached document: FAR 52.212-2-Evaluation Commercial Products and Commercial Services.

See attached document: FAR 852.219-75-Limitation on Subcontracting.