Statement of Work

The project at Detroit River International Wildlife Refuge will repair a failed compressor. This repair is required to maintain cooling needs of the visitor center. Not cooling the building will create unsafe employee conditions and the visitor center will be closed to visitors. The compressor to be replaced will allow HVAC cooling in the building.

Outdoor Scope:
1. Isolate Condensing unit, remove and weigh charge then dispose of contaminated
refrigerant (perform oil analysis, any clean up excluded)
2. Disconnect electrical
3. Disconnect mechanical piping and prep unit for removal
4. Remove existing unit with crane service
5. Provide and set in place new ACCU - 3 unit
6. Reconnect electrical
7. Install suction and liquid line drier external of the unit
8. Pressurize unit with nitrogen and tracer gas
9. Perform refrigerant leak check
10. Remove nitrogen charge and pull vacuum
11. Provide new refrigerant charge and charge unit
12. Perform start up and verify operation
13. Commission to existing indoor units.

No structural, mechanical, electrical or roofing modifications to building or existing system
other than what is included above.
No modifications to existing refrigerant piping other than at point of contact for installation
and what's included above.
No modification to Itouch Manager other than verifying communication once units have been replaced

Work Site Conditions and Hours:

The work covered in this scope will be in an occupied facility, so all work will need to be coordinated with on-site staff.

Work hours at the facility are Monday through Friday; 8:00 AM to 4:30 PM. Excluding Federal Holidays.

Facility Location:

Detroit River International Wildlife Refuge 
5437 West Jefferson Ave
Trenton, MI 48183