|  |  | Description of Requirement To support IPF Alameda project UCGR6AP2A4 - 150 kVA Portable Isolation Transformer Requirement: Vendor will provide and deliver one (1) new 150 kVA 3-phase NEMA 4x (Stainless Steel) encapsulated dry-type transformer (non-ventilated) to IPF Alameda. The primary voltage is 480-volt delta configuration, and the secondary voltage is 450-volt delta configuration. Frequency requirements will be the continental US standard: 60 hertz. Winding conductor construction shall be aluminum. Electrical taps are provided 2 at +2.5% and 4 at -2.5%. The Temperature Rise standard is 150 degrees Celsius with 220 degrees Celsius insulation system. Brand Name or Equal: The baseline standard configuration of the transformer references: Eaton V48M45T49S64X. Proposed transformer builds are not restricted to Eaton brand products. Comparable builds are subject to project design engineer scrutiny due to installed electrical systems and location of installation. No lesser build standards as outlined previously will be accepted. Required Delivery Date: Due to installation timeline restrictions, lead times cannot exceed 15 weeks. |
| --- | --- | --- |