## Water
WATER METER CALIBRATION SCHEDULE
REIMB | BLDG | EMCS Config | EMCS Connect | CUSTOMER | METER # | MAKE/MODEL | IWIMS | SIZE | UTILITY | Quantity of Calibrations | Acutal Calibrations | LOCATION | UNIT | XPLIER | LAST TEST | CALIBRATION METHOD | CALIBRATION REQUIREMENT | Comments | Water By-Pass | Test Port | Confined Space Permit Required
N | 1201 | N | N | Steam Plant | 14360583 | Zenner PMTB04 |  | 4" | WATER | 1 | 1 | Mech Room | GAL | 100 |  | On-Site | Annually |  | Has by-pass | Yes | Yes
Y | 1409 | N | N | MASTER METER - FAMCAMP | 70122912-1 | Neptune | 9100-0092 | 6 | WATER | 1 | 3 | Cmpnd Mtr / HF | FT^3 | 100 |  | On-Site | Annually |  | No by-pass | Yes | Yes
Y | 1409 | N | N | MASTER METER - FAMCAMP | 70122912-2 | Neptune | 9100-0175 | 1 | WATER |  | 0 | Cmpnd Mtr / HF | FT^3 | 0 |  | On-Site | Annually |  | No by-pass | Yes | Yes
N | 1439 | N | Wired | MASTER METER - HARTWELL GATE | 11900927 | Hersey FM3 | 9100-0093 | 8 | WATER | 1 | 3 | Meter Pit | FT^3 | 100 |  | On-Site | Annually |  | Has by-pass | Yes | Yes
N | MM | N | N | MASTER METER - WOOD STREET | 11900926 | Hersey FM3 | 9100-0094 | 8 | WATER | 1 | 3 | Pit / Chestnut St | FT^3 | 100 |  | On-Site | Annually |  | Has by-pass | Yes | Yes
Y | 1065 | N | N | Water Treatment Plant - FAMCAMP | 10808795 | Hersey MVR350 | 0066-0098 | 3 | WATER | 1 | 1 | Mech Room | GAL | 0 |  | On-Site | Annually |  | No by-pass | Yes | No
N | 1106 | N | N | HQ WG | 11801329 | Hersey MVR350 | 0066-0101 | 3 | WATER | 1 | 1 | Mech Room | GAL | 10 |  | On-Site | Annually |  | Has by-pass | Yes | No
N | 1305 | N | Y | Admin Bldg 3 | 11803763 | Hersey MVR350 | 0066-0104 | 3 | WATER | 1 | 1 | Mech Room | GAL | 0 |  | On-Site | Annually |  | Has by-pass | Yes | No
N | 1604 | Y | Y | CONS/LGCA | 70224444 | Neptune | 0066-0181 | 3 | WATER | 1 | 1 | Mech Room | FT^3 | 10 |  | On-Site | Annually |  | No by-pass | Yes | No
N | 1607 | N | N | Electric Research Lab | 10808798 | Hersey MVR350 | 0066-0204 | 3 | WATER | 1 | 1 | Mech Room | GAL | 0 |  | On-Site | Annually |  | No by-pass | Yes | Yes
N | 1614 | N | N | Electronic Systems BLDG - Phase I | 11803762 | Hersey MVR350 | 0066-0105 | 3 | WATER | 1 | 1 | Mech Room | GAL | 0 |  | On-Site | Annually |  | Has by-pass | Yes | No
N | 1614 | N | N | Electronic Systems BLDG - Phase II | 11803764 | Hersey MVR350 | 0066-0145 | 3 | WATER | 1 | 1 | Loading Dock | GAL | 0 |  | On-Site | Annually |  | Has by-pass | Yes | No
N | 1994 | N | N | Child Care Center | 11801340 | Hersey MVR350 | 0066-0108 | 3 | WATER | 1 | 1 | Mech Room | GAL | 0 |  | On-Site | Annually |  | Has by-pass | Yes | No
N | 1102 | N | N | Electric Research Lab | 10808797 | Hersey MVR350 | 0066-0099 | 3 | WATER | 1 | 1 | Mech Room | GAL | 0 |  | On-Site | Annually |  | Has by-pass | Yes | No
N | 1108 | N | N | Electric Research Eng | 10808793 | Hersey MVR350 | 0066-0100 | 3 | WATER | 1 |  | Mech Room | GAL | 100 |  | On-Site | Annually |  | Has by-pass | Yes | No
Y | LSC | N | ? | Lincoln School | 4438-0414 | Neptune |  | 4 |  | 1 |  | Mech Room | GAL |  |  | On-Site | Annually
Y | PIT | N | N | MASSPORT Main Meter | 31944690 | Neptune | 0066-0095 | 8 | WATER | 1 | 1 | Under Runway | FT^3 | 100 |  | On-Site | Annually |  | No by-pass | Yes | Yes
Y | PIT | N | N | MASSPORT Main Meter | 60392470 | Neptune | 0066-0172 | 2 | WATER | 1 |  | Under Runway | GAL | 100 |  | On-Site | Annually |  | No by-pass | Yes | Yes
Total | 18
Calibration Required
[5 empty] | Size | Frequency
[5 empty] | 5/8" | Every 10 years
[5 empty] | 3/4" | Every 8 years
[5 empty] | 1" | Every 6 years
[5 empty] | 1-1/2" | Every 4 years
Meters 3" and above - Annually IAW Manufacturer's Recommendations (Massport has combo meter 8"/2")
Master Meter (6"/1" Combo) - (Manufacturer Recommends Annual Calibration)
Meters 3" and below - Replacement Every 10 years IAW Manufacturer's Recommendations
1102 was 1102C, 1108 was 1105B, Lincoln School is back, Master Meters calib. 1/Yr.. 6/23/16