STATEMENT OF WORK (SOW)

FOR

Replace Fire Alarm system/control panel at USCG ANT Dulac

- GENERAL

The USCG is seeking a contractor to modernize the building fire alarm system, by upgrading the existing Notifier fire alarm system. Prior to submitting a quote, it is mandatory to examine the SOW and it is highly recommended to visit the facility to take field evaluations and become familiar with existing conditions under which the work will be performed. All parts, installation, and repairs shall meet or exceed manufacture’s specifications and industry standards. All work shall be completed by a licensed contractor with in-depth knowledge of Fire alarm systems. All work shall be completed as outlined in this Scope of Work. No work is authorized without the authorization of the Contracting Officer (KO) or the Contracting Officers Representative (COR).

# 1.1 BACKGROUND

The existing Notifier Fire Alarm panel and system are obsolete. Currently the system is fully functioning but constantly produces false alarms activating the local fire department at random times throughout the day/night. This statement of work includes the removal of the old fire alarm control panel and power supply along with all detectors and pull stations connected to the system and replacing/installing a new fire alarm control panel with all new capable detectors, pull stations, and fire alarm cellular communicator.

# 1.2  SCOPE



- Lockout Tagout the equipment

- Removal of old fire panel control panel, power supply panel, detectors, and pull stations

- Furnish & install fire alarm control panel.

- Furnish & install power supply panel

- Furnish & install 21 smoke detectors.

- Furnish & install 5 heat detectors.

- Furnish & install 4 duct smoke detectors.

- Furnish & install 4 duct detector housing.

- Furnish & install 8 relay modules.

- Furnish & install 2 control modules.

- Furnish & install 14 mini-monitor modules.

- Furnish & install 6 monitor modules.

- Furnish & install 6 all-weather conventional heat detectors.

- Furnish & install One-time Fire alarm cellular communicator.

- Furnish & install 1 external antenna for additional signal strength for the cellular communicator.

- Furnish 5 extra heat detectors and 5 extra smoke detectors for spares.

- Provide annual fire alarm monitoring service.

- Cost of necessary labor, material for installation.

- Verify proper operation and testing of newly installed system.

- Schedule the final inspection with the Louisiana State Fire Marshal and provide an NFPA 72 Certificate of Compliance.

- Before the USCG accepts the work, the contractor will complete a function test of the new Fire Alarm panel system, with USCG POC present.

- Attach annual inspection tag after completion of install & function test.

FIRE ALARM EQUIPMENT INFORMATION:

# QTY  DESCRIPTION

- NOTIFIER INTELLIGENT FIRE ALARM CONTROL PANEL

- MAIN FIRE ALARM PANEL BATTERY

- NOTIFIER 10 AMP REMOTE POWER SUPPLY

- FIRE ALARM POWER SUPPLY BATTERY

21  NOTIFIER ADDRESSABLE SMOKE DETECTOR

5  NOTIFIER ADDRESSABLE HEAT DETECTOR

4  NOTIFIER ADDRESSABLE DUCT SMOKE DETECTOR

4  NOTIFIER INTELLIGENT DUCT DETECTOR HOUSING

8  NOTIFIER ADDRESSABLE RELAY MODULE

2  NOTIFIER ADDRESSABLE CONTROL MODULE

14  NOTIFIER ADDRESSANLE MINI-MONITOR MODULE

6  NOTIFIER ADDRESSANLE MONITOR MODULE

6  THERMOTECH 135F ALL WEATHER CONVENTIONAL HEAT DETECTOR

1  DESIGN/STATE FIRE MARSHAL SUBMITTAL FEE

- WIRE/MATERIALS

ONE TIME FIRE ALARM CELLULAR COMMUNICATOR:

# QTY  DESCRIPTION

1  HONEYWELL CLSS PATHWAY DUAL-PATH LTE COMMUNICATOR

1  HONEYWELL RED METAL MOUNTING ENCLOSURE

1  HONEYWELL EXTERNAL ANTENNA KIT

1  ALTRONIX VOLTAGE REGULATOR

1  NOTIFIER MULTI-VOLTAGE RELAY MODULE

1  NOTIFIER ADDRESSABLE MONITOR MODULE

1  DESIGN/STATE FIRE MARSHAL SUBMITTAL FEE

1  WIRE/MATERIALS

1.3 OBJECTIVE

The goal is to modernize fire alarm system with an up to date fully functioning installed system for crew safety and property protection.

# 1.4 APPLICABLE DOCUMENTS

N/A

# 2.0 SPECIFIC REQUIREMENTS/TASKS

Please see the Scope of the SOW

# 3.0 CONTRACTOR PERSONNEL

Contractor personnel will have the appropriate certifications for working on a fire alarm control systems and/or NFPA (National Fire Protection Association) certified.

# 3.1 QUALIFIED PERSONNEL

The Contractor shall provide qualified personnel to perform all requirements specified in this SOW.

# 3.2 EMPLOYEE CONDUCT

Contractor’s employees shall comply with all applicable Government regulations, policies and procedures (e.g., fire, safety, sanitation, environmental protection, security, “off limits” areas, wearing of parts of DHS uniforms, and possession of weapons) when visiting or working at Government facilities.  The Contractor shall ensure Contractor employees always present a professional appearance and that their conduct shall not reflect discredit on the United States or the Department of Homeland Security.  The Project Manager shall ensure Contractor employees understand and abide by Department of Homeland Security established rules, regulations and policies concerning safety and security.

# 3.4 REMOVING EMPLOYEES FOR MISCONDUCT OR SECURITY REASONS

The Government may, at its sole discretion (via the Contracting Officer*), direct the Contractor to remove any Contractor employee from DHS facilities for misconduct or security reasons.  Removal does not relieve the Contractor of the responsibility to continue providing the services required under the contract. The Contracting Officer will provide the Contractor with a written explanation to support any request to remove an employee.

# 4.1 PERIOD OF PERFORMANCE

The period of performance for this contract shall not exceed 60 calendar days from the date of award.

# 4.2 PLACE OF PERFORMANCE

United States Coast Guard ANT Dulac at 241 Coast Guard Road, Dulac, LA 70360

4.3 SITE VISIT: All site visits should be scheduled with the Contracting Officers Representative:

    - Contracting Officers Representative (COR)

MK1 Joseph Fodor

Cell: (619)-733-1066

Email: Joseph.A.Fodor@uscg.mil

# 4.4 HOURS OF OPERATION

Contractor employees shall generally perform all work between the hours of 7:30 am – 1:30 pm EST, Monday through Thursday (except Federal holidays).  However, there may be occasions when Contractor employees shall be required to work other than normal business hours, including weekends and holidays, to fulfill requirements under this SOW.

4.5 TRAVEL

Contractor travel shall not be required for this requirement.

5.0 GOVERNMENT FURNISHED RESOURCES

The Government will not furnish any resources to the Contractor in support of this contract.

# 6.0 CONTRACTOR FURNISHED PROPERTY

  - The Contractor will furnish all materials, equipment, instruments, tools, safety lines and harnesses, and other items necessary for accomplishment of these services.

  - Materials shall be delivered to the jobsite in their original unopened packages, clearly marked with the manufacturer’s name, brand name, and description of contents.  Storage shall be in accordance with manufacturers’ recommendations in a clean, dry, well-ventilated area. Stored materials shall be protected from sunlight and kept away from excessive heat.  The contractor shall not store any highly flammable materials in the work area and all chemicals used shall be preapproved by POC.  Laydown areas and parking should be in non-vegetated areas when possible.

  - The Contractor is required to comply with local VOC laws and regulations.  All applicable Safety Data Sheets shall be available upon request.

# 7.0 CONTRACT TIMELINE:

- The Contractor shall provide all required information and complete this contract within this time schedule, unless approved by the Contracting Officer.

  - Provide all required submittals to the Contracting Officer within 14 calendar days after contract award.

  - The U.S. Coast Guard will have 7 calendar days to review the submittals and respond to Contractor.

  - Contractor shall provide projected delivery schedule during proposal and provide a firm delivery date within 14 calendar days after the contract has been awarded.

  - The Contractor, upon receiving notification that the U.S. Coast Guard has approved the submittals and having received the Contractors firm delivery date schedule, will have 14 Calendar days to begin work on the project & 30 Calendar days to complete.  The Contractor shall notify the Contracting Officer of any long lead time delivery of equipment, so that the Contracting Officer can modify the delivery date of the contract.

8.0 ENVIRONMENTAL COMPLIANCE:

Any waste generated because of the project shall either be recycled or be disposed of IAW the Resource Conservation and Recovery Act (RCRA). Any Hazardous Waste shall be manifested off site with ANT Dulac listed as the Generator and signatory. Any hazardous waste shall be analyzed, characterized, stored and disposed of IAW RCRA and all applicable federal, state (i.e. DOT) and local laws and ordinances. All solid waste/trash shall be removed from site and not disposed of in onsite dumpsters.  Waste and recycling areas are reserved for RCF Tenants and shall not be used by Contractors at any time.  All chemicals required for this project shall be preapproved by the contract POC along with SDS’s. All solid waste shall be removed from the RCF after each working day. All extra chemicals and products shall be removed from the site upon work completion, as the Emergency Planning and Community Right-To-Know Act requires the Coast Guard to maintain an inventory of all Hazardous Materials located at the site. A laydown area as required and an Erosion and Sediment Control Plan, shall be preapproved by the COR as needed. Nothing shall be discharged to a storm drain at any time during the project. All storm drains within range of a potential discharge shall be covered/sealed during installation and kept covered until the work has been completed and the system has been deemed fully operational and compliant with all applicable CG policies/plans/permits/laws/ordinances.  All storm drains and waterways within range of a potential discharge shall be covered/sealed or protected by silt fence.

9.0 EXECUTION: Installation, workmanship, fabrication, assembly, erection, examination, inspection and testing shall be in accordance with appropriate sections of 29 CFR 1910, 1926.

  - The Contractor shall schedule all work with the Technical Representative.  The Contractor shall understand the importance to schedule and complete all work in a timely fashion. The Contractor shall minimize the impact for the command and/or mission of the personnel located at the unit.

  - The Contractor shall perform all work IAW all Federal, EPA, OSHA, and State of Louisiana laws and regulations.

10.0 WARRANTY: Contractor shall provide a 1-year workmanship and provide information for manufacturer’s warranty.