## Comment-Response Log
Project Name: |  | Montgomery Legionella Design
VA Project Number: |  | 619-23-105
ACG Project Number: |  | 23-039 | [6 empty] | 0
Pre-Bid RFI Response Log
|  | REQUIRED | [6 empty] | Tracking |  | Backcheck
Item # | Sheet / Page # | Pre-Bid RFI | Entry Date | Finish Date | Discipline | AE Responder Initials | AE Accept/ Reject? | AE Response | Status CLOSED / OPEN | Days Open | RFI? | Backcheck | Back Checker | Location of update | Column1
1 |  | Will the Mechanical system need to be tested and balanced? Please advise. |  |  | Mech | SMR |  | Yes, testing and balancing will have to be performed. Spec section 23 05 93- Testing, Adjusting, and Balancing for HVAC will be added. |  | 0
2 |  | Will Pro Press plumbing joints be allowed? Please advise. |  |  | VA |  |  | No, pro press fittings are not allowed at VA. Spec section 22 11 00 paragraph 2.2.B.3. |  | 0
3 |  | Is any commissioning required on this project? |  |  | VA |  |  | Yes. |  | 0
4 |  | Can the Superintendent also be the Prime Contractor’s Commissioning Manager during commissioning? |  |  | VA |  |  | Refer to specifications. |  | 0
5 |  | Is a full-time on-site quality control manager required for this project? |  |  | VA |  |  | Refer to specifications. |  | 0
6 |  | Can the Superintendent also be the quality control manager? |  |  | VA |  |  | Yes |  | 0
7 |  | Is a full-time on-site Safety and Health Officer required for this project? |  |  | VA |  |  | Refer to specifications. |  | 0
8 |  | Can the Superintendent also be the site safety and Health Officer? |  |  | VA |  |  | Refer to specifications. |  | 0
9 |  | Can the Superintendent be Triple hatted as the SSHO and QC Manager? |  |  | VA |  |  | Refer to specifications. |  | 0
10 |  | As is typical for most VA projects can the QC plan be implemented by the onsite superintendent and administrated by the PM without additional staff (other than what is required for commissioning) as call for in 01 45 00.? |  |  | VA |  |  | Yes |  | 0
11 |  | Has this funding request been approved and available to the NCO station? |  |  | VA |  |  | Yes |  | 0
12 |  | When does the VA expect this project to start? |  |  | VA |  |  | Q4 FY2026 |  | 0
13 |  | Will any of this work have to be performed after hours or weekends? |  |  |  | SMR |  | Yes, work in patient areas, common areas, offices, conference rooms, exam rooms, consultation rooms, and other similar areas that are occupied on a regular basis during business hours shall be performed after business hours from 4 pm to 12:00 am, or during the weekends. Please also refer to G-003. |  | 0
14 |  | Will this project be done in phases? |  |  |  | SMR |  | Yes, this project shall be phased. Please refer to General Phasing Notes on P-001 for phasing requirements. Contractor shall submit a detailed phasing plan for review by the COR, architect and engineer. Phasing plan shall include, but not be limited to, start and end dates of all tasks throughout the entire project, and date and duration of suggested shutdowns. |  | 0
15 |  | Will each phase have to be fully completed before moving to the next or can some phases be completed simultaneously? |  |  |  | SMR |  | Each phase shall be fully completed before moving to the next. The contactor shall finish work in one area before starting work in another area. |  | 0
16 |  | How many areas will we be given at a time? |  |  |  | SMR |  | One area at a time. No more than half of a wing shall be shut down at the same time without approval. The area of work shall be minimized and shall coincide with a logical domestic water cut off point. The contactor shall finish work in one area before starting work in another area. |  | 0
17 |  | Will the contractor have to ask for access to certain areas weeks ahead of time in order to be given access to some areas? |  |  |  | SMR |  | Yes, schedule all shutdowns with the contracting officer's representative (COR) a minimum of three (3) weeks in advance. |  | 0
18 |  | Can the VA provide some indication of how they expect the contractor to maintain ICRA throughout the project since the project involves the entire building? |  |  |  | SMR |  | No more than half of a wing shall be shut down at the same time without approval. The area of work shall be minimized and shall coincide with a logical domestic water cut off point. The contactor shall finish work in one area before starting work in another area. Please refer to G-003 for areas where work inside the walls, above hard ceiling, or other activities that create increased dust level compared to the rest of the above ceiling work is expected. These areas are classified by ICRA class. Refer to G-002 for ICRA class precausions and requirements. In addition, any area caring for immunocompromised patients, Cardiac Cath Lab/IR, Central Sterile Supply, Sterile Processing Service, Intensive Care Units, Medical/Surgical Units, Negative pressure isolation Rooms, Outpatient Chemotherapy Areas, Operating rooms, Post Anesthesia Care Unit, Dialysis, Dental Areas will need ICRA barriers in accordance with G-002. |  | 0
19 |  | Will all work need to be performed from HEPA carts? |  |  |  | SMR |  | No, please refer to question above and the following. Where ICRA barrier in accordance with NFPA 241 is not required, work above the ceiling in HIGH Risk Group 3 shall be performed using HEPA carts. LOW Risk Group 1 and Medium Risk Group 2 do not require HEPA carts but the contractor still needs to provide Infection control precausions in accordance with table on G-002. |  | 0
20 |  | Will the contractor be required to turn the existing sprinkler heads up during construction once the ceiling is removed? |  |  |  | SMR |  | Yes, sprinkler heads shall be temporarily turned up within the area of work. Please refer to General phasing note 6 on P-001. Contractor shall provide fire watch for the sprinkler / fire alarm imparements more than 4 hours in a 24 hr period. Please refer to BUILDING AND OCCUPANT SAFETY - INTERRUPTION OF FIRE PROTECTION SERVICE on FX001. |  | 0
21 |  | Who is the manufacturer of the current Fire Alarm system |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
22 |  | Please provide contact name and phone number for who services the current Fire Alarm System | [5 empty] | Not relevant to plumbing project. |  | 0
23 |  | Who is the manufacturer of the current Security and Access Control system? |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
24 |  | Please provide contact name and phone number for who services the current Security and Access Control System? |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
25 |  | Please confirm whether the Access Control work in this project is to be CFCI, OFCI, or OFOI? | [5 empty] | Not relevant to plumbing project. |  | 0
26 |  | Who is the manufacturer of the current CCTV system? |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
27 |  | Please provide contact name and phone number for who services the current CCTV System? |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
28 |  | Please confirm whether the CCTV work in this project is to be CFCI, OFCI, or OFOI? | [5 empty] | Not relevant to plumbing project. |  | 0
29 |  | Who is the manufacturer of the current Telecommunications system? |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
30 |  | Please provide contact name and phone number for who services the current Telecommunications System? |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
31 |  | Who is the manufacturer of the current HVAC Controls? |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
32 |  | Please provide contact name and phone number for who services the current HVAC Controls? |  |  | VA |  |  | Not relevant to plumbing project. |  | 0
33 |  | Who is the manufacturer of the current Building Automation System? |  |  | VA |  |  | Metays |  | 0
34 |  | Please provide contact name and phone number for who services the current Building Automation System? |  |  | VA |  |  | Johnson Control |  | 0
35 |  | Is there any chance of uncovering hazardous materials? a. If so please provide the latest hazardous materials survey report for the area of construction? |  |  |  | SMR |  | Yes. Please refer to Asbestos Note on P-001 and specification section 02 82 13.13 paragraph 1.1.B. |  | 0
36 |  | Who is the existing signage contractor for this VA? |  |  | VA |  |  | VA Manages |  | 0
37 |  | Will the contractor be responsible for any permits? |  |  | VA |  |  | Yes. Hot work permits. Confined space.Etc. |  | 0
38 |  | Does the VA currently have a water monitoring system in place? |  |  | Plumb | SMR |  | There are existing PHIGENICS water quality monitoring stations are located at water service entracnces. Please also refer to P-503 details 4 and 5. |  | 0
39 |  | If so, please provide the contact name and phone number for who services the current Water Monitoring System? |  |  | VA |  |  | Phigenics LLC, 38701 West Ave, Suite 100, Warrenville, IL 60555 |  | 0
40 |  | Please provide a basis of design product for the Chlorination Injection Stations? |  |  | Plumb | SMR |  | There are no new chlorination injection stations. The end of loop monitoring stations only monitor chlorine residual and water temperatures (on hot and cold) as indicated on detail 4 and 5, P-503. |  | 0
41 |  | Please provide a basis of design product for the Continuous Water Monitoring System? |  |  | Plumb | SMR |  | Basis of design is Phigenics panel. Panels WQMS-2 through 6 shall include chlorine analyzers for hot and cold water, temperature monitoring for hot and cold water. Panel WQMS-1 shall include chlorine analyzer for cold water, temperature monitoring for cold water.The system must continuously monitor these sensors and make the data available securely using any Internet connected device. Each water quality monitoring station must be pre-wired and pre-plumbed on a single panel to ensure high quality and a simple installation. |  | 0
42 |  | Is the VA wanting to include maintenance of the new water monitoring system, including chemical injections, in this contract for a period of time? |  |  | VA |  |  | No |  | 0
43 |  | Is the VA intending for this water monitoring system to have an online monitoring system similar to what PhiGenics provides? |  |  | Plumb | SMR |  | Yes. |  | 0
44 |  | When installing the new chiller, please confirm that NO temporary chiller or AHU’s will be required by the contractor? |  |  | Mech | SMR |  | No temporary chiller or AHUs will be required by the contractor. |  | 0
45 |  | In the scope of work, section 2.1.1 Removal of Dead-Leg Piping, it states “Identify and remove all sections of domestic water “dead-leg” piping” Have all sections of dead-leg piping not already been identified and called out on the plumbing demolition drawings? |  |  | Plumb | SMR |  | Dead legs are identified on drawings. Demolish dead-leg piping as indicated on drawings. |  | 0
46 |  | Will the contractor have to provide exploratory services to Identify more dead-leg piping? |  |  | Plumb | SMR |  | No, however if new dead legs are identified during demolition and/or new work, contractor shall submit an RFI to confirm course of action for the new dead legs. |  | 0
47 |  | Will the VA please provide existing Reflected Ceiling Plans for all of the Areas in the Plumbing demolition drawings, as it is likely that most all of these ceilings will have to be removed and replaced for this work? |  |  | VA |  |  | No recent plans can be provided with this information. |  | 0
48 |  | There is no Division 9 specifications, does the VA not intend for the contractor to have to perform any ceiling, drywall, or painting work? |  |  | Arch | KC |  | Yes, this work is expected to happen. division 9 spec will be added. Please also refer to details 7, 8, 9 on G-002. |  | 0
49 |  | Where can we stage materials on the site? |  |  | VA |  |  | Discussed at Notice to Proceed |  | 0
50 |  | Will the site need to be fenced off during construction? |  |  | VA |  |  | Materials site? Yes. |  | 0
51 |  | What is the height from finished floor to bottom of deck above on each floor of Building 1? |  |  | VA |  |  | Refer to plans. |  | 0
52 |  | Will the VA have the different rooms cleared enough for the contractor to perform their work before the contractor begins? |  |  | VA |  |  | Personnel will be out of the way. |  | 0
53 |  | Will the contractor be required to move any of the existing furniture or equipment? |  |  | VA |  |  | If it is needed to be moved yes. |  | 0
54 |  | If the contractor is responsible for moving the existing furniture, will storage be available from the VA for the furniture, equipment, or casework? |  |  | VA |  |  | Yes. |  | 0
55 |  | Has the VA performed a structural analysis on the existing third floor roof to confirm it can support the 2000 gallon storage tank, AHU, and Chiller? |  |  | Structural | HD |  | Yes, the existing structure has been checked/evaluated to support new penthouse and all new loads. |  | 0
56 |  | Keynote 1 on sheet E-401 is <Varies>. Please clarify what Keynote 1 is supposed to say? |  |  | Electrical | KTK |  | Key note 1 should read: PROVIDE ONE 3-PHASE 400A MCB 480/277V SURFACE MOUNTED PANELBOARD. SEE E-601 FOR PANEL SCHEDULE AND SINGLE-LINE DIAGRAM. |  | 0
57 |  | Can the bid date for the project be extended to provide more time for contractors? |  |  | VA |  |  | RFP due date unchanged |  | 0
58 |  | Can a second round of RFIs be submitted once the initial RFI answers are provided as usually these answers call for more clarifications in most cases? |  |  | VA |  |  | RFI's have closed, no additonial RFI's will be accepted. |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Responsibility Matrix (hidden)
The Project Scope of work defines who is responsible for what aspects. Definitions are listed below the table. Modify what is necessary in the scope and the description of work for each party responsible. Level of Development for each project, per the company standard, is LOD 300, as the ultimate objective to convey design intent and produce construction documentation. However, depending on the scope, budget, schedule, and the team assembled to execute the project, it may be necessary to complete a Model Element LOD Breakdown worksheet to create a detailed plan of the elements to either be modeled or excluded from modeling for this project, depending on which is more expedient. |  |  | BIM Use Chart - What is BIM being used to accomplish on this project. Remove items from this chart that are doing being done utilizing a Building Information Modeling process on this project. If an entire column is not being used (i.e. Operations), remove that whole column as necessary. *It is important to define the final "Model" delivery to the owner at the end of the project. The simplist is to provide the owner with the individual deisgn models and invidual construction models, along with a Navisworks coordinated full design/construction model. Understand how the owner plans to use the models and keep them updated. Also note that creation of a fully updated, as-built project model can be very expensive to create. If required, meet with the project manager and the BIM manager to discuss how best to accomplish this deliverable.
Project Scope | Description of Work | Responsible Party | Scope | Planning | Design | Construction | Operations
Site | Benchmark, Design, CD's | Civil Engineer Consultant | Model Creation | Laser Scan Existing Conditions | Architectural | Building Enclosure | Energy, Control, and Facility Management
Landscape | Existing and New site and element creation, Design, CD's | ACG |  | Site Layout | Civil | Framing and Drywall | Record Update*
Structure | Model Creation, Analysis, Design, CD's Shop drawings, Model Coordination |  |  | Programming Options | Mechanical | Mechanical | As-Built Update
Architecture | Existing and New Building Model Creation, LEED Evaluation, Design, CD's, Model Coordination, Record Drawings | ACG |  | Existing Building Modeling | Electrical | Electrical
Mechanical | Existing and New Building Model Creation, Energy Analysis, Daylighting, Design, CD's, Model Coordination | ACG |  |  | Plumbing | Plumbing
Plumbing | Existing and New Building Model Creation, Design, CD's, Model Coordination | ACG |  |  | Fire Protection | Fire Protection
Electrical | Existing and New Building Model Creation, Design, CD's, Model Coordination | ACG |  |  | Interiors | Owner Furnished Equipment
Fire Protection | Existing and New Building Model Creation, Design, CD's, Model Coordination | ACG |  |  | Landscaping
[5 empty] | Structural | Structural and Supports
Model Creation: | Model Creation is the act by a Project Participant in creating a Model that represents their physical scope of work. Each Project Participant will design utilizing the models from other participants to mitigate design conflicts as they arise. |  | Model Analysis | LEED Evaluation | LEED Evaluation | LEED Documentation | Building Operation Optimization
Model Analysis: | Model Analysis consists of a Project Participant analyzing models for a specific purpose. e.g. structural analysis, energy analysis, cost analysis, logistics planning, etc. |  |  | Logistics (4D) | Logistics (4D) | Logistics (4D) | Space Management Planning
Model Coordination: | Model coordination consists of a formal review process by the Project Participants at project milestones, or more frequently if project needs dictate, to resolve physical and sequence clashes that could not be resolved by Participants during Model Creation. |  |  | Cost Estimation (5D) | Cost Estimation (5D) | Digital Fabrication Planning | Disaster Planning
[5 empty] | Air Distribution | Pre-Con Cost Estimate
Water/Mechanical Piping
Structural
Code Validation
Lighting and Daylighting
Energy Use
|  |  | Model Coordination |  | Underground MEP | Underground MEP
[5 empty] | Overhead MEP | Overhead MEP
[5 empty] | In-Wall MEP | In-Wall MEP
[5 empty] | On-Wall Equip and Furnishings | On-Wall Equipment and Furnishings
[5 empty] | Exterior Enclosure | Exterior Enclosure
|  |  | Documentation | Programming | Contract Documentation | Change Order Updates | Record Drawings
[5 empty] | Coordinated Shop Drawings/Models | Coordinated Shop Drawings/Models | As-Built Models
|  |  |  | Model Walk Through | Model Walk Through | Model Walk Through

## Software Dropdown (hidden)
Design Software | Collaboration Methods
AutoCAD 2016 | Aconex
AutoCAD 2017 | Ajera
AutoCAD 2019 | BIM 360
AutoCAD 2020 | Newforma
Civil 3D 2017 | PlanGrid
Civil 3D 2019 | Procore
Civil 3D 2020 | Sharepoint
Revit 2016
Revit 2017
Revit 2019
Revit 2020
Revit 2021
AutoCAD MEP 2017
AutoCAD MEP 2019
AutoCAD MEP 2020
RISA
Hourly Analysis Program
Green Building Studio
STAAD Pro
SAFE
TRACE 700
Visual Lighting Software
AGI
Robot
Insight
ElumTools
SAP
Navisworks 2019
Navisworks 2020
Revizto
Solibri
Tekla
Vectorworks
ArchiCAD
Microstation
Solidworks
Catia
TRNSYS
HVAC Solution
BricsCAD
3D Studio Max
Enscape
Rhino
Grasshopper
Lumion
Maya

## DynamoInfo (hidden)
ACG Project Number | #REF!
Project Issue Date | #REF!
Project Status | #REF!
Client Name | #REF!
VA Project Number | #REF!
Project Name | #REF!
Project Address | #REF!
Code: Building Code | #REF!
Code: Plumbing Code | #REF!
Code: Mechanical Code | #REF!
Code: Electrical Code | #REF!
Code: Fire Code | #REF!
Code: Energy Code | #REF!
Code: Other Code 1 | #REF!
Code: Other Code 2 | #REF!
Code: Other Code 3 | #REF!
Code: Existing Building Code | #REF!
Code: Construction Type | #REF!
Code: Primary Occupancy | #REF!
Code: Proposed Use | #REF!
Code: Secondary Use | #REF!
Code: Accessibility Code | #REF!
Code: Life Safety Code | #REF!
Code: Accessibility Code 2 | #REF!
Organization Name | #REF!
Organization Description | #REF!
Building Name | #REF!
Author | #REF!
Managing Office Address | Place Managing Office Address Here City, State and Zip Code
Milestone: Milestone 1 Date | #REF!
Milestone: Milestone 1 Description | #REF!
Milestone: Milestone 2 Date | #REF!
Milestone: Milestone 2 Description | #REF!
Milestone: Milestone 3 Date | #REF!
Milestone: Milestone 3 Description | #REF!
Milestone: Milestone 4 Date | #REF!
Milestone: Milestone 4 Description | #REF!
Milestone: Milestone 5 Date | #REF!
Milestone: Milestone 5 Description | #REF!
Milestone: Milestone 6 Date | #REF!
Milestone: Milestone 6 Description | #REF!
Milestone: Milestone 7 Date | #REF!
Milestone: Milestone 7 Description | #REF!
Team: Architecture | #REF!
Team: Architecture Contact | #REF!
Team: Audio Visual | #REF!
Team: Audio Visual Contact | #REF!
Team: Civil | #REF!
Team: Civil Contact | #REF!
Team: Electrical | #REF!
Team: Electrical Contact | #REF!
Team: Fire Protection | #REF!
Team: Fire Protection Contact | #REF!
Team: Food Service | #REF!
Team: Food Service Contact | #REF!
Team: Interiors | #REF!
Team: Interiors Contact | #REF!
Team: Landscape | #REF!
Team: Landscape Contact | #REF!
Team: Low Voltage | #REF!
Team: Low Voltage Contact | #REF!
Team: Mechanical | #REF!
Team: Mechanical Contact | #REF!
Team: Plumbing | #REF!
Team: Plumbing Contact | #REF!
Team: Structural | #REF!
Team: Structural Contact | #REF!
Team: Surveillance | #REF!
Team: Surveillance Contact | #REF!
Team: Lighting | #REF!
Team: Lighting Contact | #REF!
Team: Process | #REF!
Team: Process Contact | #REF!
Building Number | #REF!
Approved Project Director | #REF!
Project CO | #REF!
Project CO Contact | #REF!
Project COR | #REF!
Project COR Contact | #REF!
Project Manager | #REF!
Project Manager Contact | #REF!

## Building Codes List (hidden)
Column1
2018 International Building Code
2018 International Residential Code
2018 International Energy Conservation Code
2018 International Mechanical Code
2018 International Fuel Gas Code
2018 International Swimming Pool and Spa Code
2018 International Existing Building Code
2018 International Plumbing Code
2019 NFPA 13 Standard for Installation of Sprinkler Systems
2019 NFPA 14 Standard for installation of standpipe
2019 NFPA 20 Standard for stationary pumps for fire protection
2018 NFPA 70E Standard for electrical safety in the workplace
2017 NFPA 70 National Electrical Code
2019 NFPA 72 National Fire Alarm and Signaling Code
2017 NFPA 75 Standard for the fire protection of information technology
2016 NFPA 76 Standard for the fire protection of Telecommunications Facilities
2019 NFPA 77 Recommended practice on static electricity
2019 NFPA 88A Standard for Parking Structures
2018 NFPA 90A Standard for Air Conditioning and Ventilating
2018 NFPA 99 Health Care Facilities code
2018 NFPA 101 Life Safety Code
2019 NFPA 110 Standard for emergency and standby power systems
2018 NFPA 730 Guide for Premises Security
2017 NFPA 731 Standard for installation of electronic premises security systems
2017 NFPA 780 Standard for installation of lighting protection systems
2018 NFPA 790 Standard for competency of third party field evaluation
2018 NFPA 791 Recommendation practictice and procedures for unlabeled electrical eq. eval
ASHRAE 90.1-2016
ASHRAE 170-2017
ASHRAE 62.1-2016
VA Design Guide HVAC Design Manual 2017 November 01
VA Design Guide Plumbing Design Manual 2018 May 01
VA Design Guide Electrical Design Manual 2015 December 01
VA Design Guide Architectural Manual 2014 August 01
VA Design Guide Fire Protection Manual 2015 December
VA BIM Manual Version 2.2
2010 ADA Standards for Accessible Design