|  | DIVISION 00 - SPECIAL SECTIONS | DATE |
| --- | --- | --- |
| 00 01 10 | Table of Contents | 05-10 |
| 00 01 07 | Seals Page | n/a |
| 00 01 15 | List of Drawing Sheets | 05-10 |
|  | DIVISION 01 - GENERAL REQUIREMENTS |  |
| 01 00 00 | General Requirements | 11-21 |
| 01 10 00 | Summary | - |
| 01 22 00 | Unit Prices | - |
| 01 32 16.15 | Network Analysis Schedules (Small Projects – Design/Bid/Build) | 05-22 |
| 01 33 23 | Shop Drawings, Product Data, and Samples | 11-23 |
| 01 35 26 | Safety Requirements for Major Projects | 05-24 |
| 01 42 19 | Reference Standards | 11-20 |
| 01 45 00 | Quality Control | 02-21 |
| 01 45 29 | Testing Laboratory Services | 05-24 |
| 01 57 19 | Temporary Environmental Controls | 10-23 |
| 01 58 16 | Temporary Interior Signage | 07-15 |
| 01 73 29 | Cutting and Patching | n/a |
| 01 74 19 | Construction Waste Management | 10-23 |
| 01 91 00 | General Commissioning Requirements | 10-23 |
|  | DIVISION 02 – EXISTING CONDITIONS |  |
| 02 21 13 | Site Surveys | 10-23 |
| 02 41 10 | Demolition and Site Clearing | 10-23 |
| 02 83 11.13 | Glovebag Asbestos Abatement | 01-21 |
| 02 83 33.13 | Lead-Based Paint Removal and Disposal | 01-21 |
|  | DIVISION 07 THERMAL AND MOISTURE PROTECTION |  |
| 07 81 00 | Applied Fireproofing | 10-23 |
| 07 84 00 | Firestopping | 10-23 |
| 07 92 00 | Joint Sealants | 10-23 |
|  | DIVISION 09 – FINISHES |  |
| 09 91 00 | Painting | 10-23 |
|  | DIVISION 27 – COMMUNICATIONS |  |
| 27 05 11 | Requirements for Communications Installations | n/a |

|  | DIVISION 00 - SPECIAL SECTIONS | DATE |
| --- | --- | --- |
| 00 01 10 | Table of Contents | 05-10 |
| 00 01 07 | Seals Page | n/a |
| 00 01 15 | List of Drawing Sheets | 05-10 |
|  | DIVISION 01 - GENERAL REQUIREMENTS |  |
| 01 00 00 | General Requirements | 11-21 |
| 01 10 00 | Summary | - |
| 01 22 00 | Unit Prices | - |
| 01 23 00 | Alternates | - |
| 01 32 16.13 | Network Analysis Schedules | 05-22 |
| 01 33 23 | Shop Drawings, Product Data, and Samples | 11-23 |
| 01 35 26 | Safety Requirements for Major Projects | 05-24 |
| 01 42 19 | Reference Standards | 11-20 |
| 01 45 00 | Quality Control | 02-21 |
| 01 45 29 | Testing Laboratory Services | 05-24 |
| 01 57 19 | Temporary Environmental Controls | 10-23 |
| 01 58 16 | Temporary Interior Signage | 07-15 |
| 01 74 19 | Construction Waste Management | 10-23 |
| 01 91 00 | General Commissioning Requirements | 10-23 |
|  | DIVISION 02 – EXISTING CONDITIONS |  |
| 02 21 00 | Site Surveys | 10-23 |
| 02 41 10 | Demolition and Site Clearing | 10-23 |
| 02 83 11.13 | Glovebag Asbestos Abatement | 01-21 |
| 02 83 33.13 | Lead-Based Paint Removal and Disposal | 01-21 |
|  | DIVISION 03 – CONCRETE |  |
|  | DIVISION 04 – MASONRY |  |
|  | DIVISION 05 – METALS |  |
| 05 50 00 | Metal Fabrications | 10-23 |
|  | DIVISION 06 – WOOD,PLASTICS AND COMPOSITES |  |
|  | DIVISION 07 THERMAL AND MOISTURE PROTECTION |  |
| 07 81 00 | Applied Fireproofing | 10-23 |
| 07 84 00 | Firestopping | 10-23 |

| 07 92 00 | Joint Sealants | 10-23 |
| --- | --- | --- |
|  | DIVISION 08 OPENINGS |  |
|  | DIVISION 09 – FINISHES |  |
| 09 91 00 | Painting | 10-23 |
|  | DIVISION 10 – SPECIALTIES |  |
|  | DIVISION 11 - EQUIPMENT |  |
|  | DIVISION 12 – FURNISHINGS |  |
|  | DIVISION 13 - SPECIAL CONSTRUCTION |  |
|  | DIVISION 22 – PLUMBING |  |
|  | DIVISION 23 – HEATING, VENTILATING, AND AIR CONDITIONING (HVAC) |  |
|  | DIVISION 25 – INTEGRATED AUTOMATION |  |
|  | DIVISION 26 – ELECTRICAL |  |
|  | DIVISION 27 – COMMUNICATIONS |  |
| 27 05 11 | Requirements for Communications Installations | n/a |
| 27 05 26 | Grounding and Bonding for Communications Systems | 12-22 |
| 27 05 33 | Conduits and Backboxes for Communications Systems | 12-22 |
| 27 05 36 | Cable Trays for Communications Systems | 12-22 |
| 27 05 53 | Identification for Communications Systems | 12-22 |
| 27 10 00 | Structured Cabling | 12-22 |
| 27 11 19 | Communications Termination Blocks and Patch Panels | 12-22 |
| 27 11 26 | Communications Rack-Mounted Power Protection and Power Strips | 12-22 |
| 27 13 13.13 | Communications Copper Cable Splicing and Terminations | 12-22 |
| 27 15 13 | Communications Copper Horizontal Cabling | 12-22 |
| 27 16 19 | Communications Patch Cords, Station Cords, and Cross- Connect Wire | 12-22 |
|  | DIVISION 28 – ELECTRONIC SAFETY AND SECURITY |  |
| 27 05 00 | Common Work Results for Electronic Security Systems | 04-18 |

| 28 05 01 | Statement of Work for Electronic Safety and Security Installations | n/a |
| --- | --- | --- |
| 28 05 13 | Conductors and Cables for Electronic Security Systems | 10-18 |
| 28 05 26 | Grounding and Bonding for Electronic Security Systems | 09-11 |
| 28 05 28 33 | Conduits and Backboxes for Electronic Security Systems | 09-11 |
| 28 23 00 | Video Surveillance | 03-18 |
|  | DIVISION 31 – EARTHWORK |  |
| 31 20 00 | Earth Moving | 08-23 |
|  | DIVISION 32 – EXTERIOR IMPROVEMENTS |  |
| 32 05 23 | Cement and Concrete for Exterior Improvements | 11-16 |
| 32 12 16 | Asphalt Paving | 09-15 |
| 32 90 00 | Planting | 11-16 |
|  | DIVISION 33 – UTILITIES |  |

End of Section

SECTION 00 01 15 LIST OF DRAWING SHEETS

The drawings listed below accompanying this specification form a part of

the contract.

Drawing No.	Title

GI001	COVER SHEET

GI002	DEMOLITION INFORMATION AND SHEET INDEX

GI003	GENERAL - ICRA GUIDLINES

GI004	FIRE/SMOKE BARRIER LEGEND

| GI-1-500-00A | INFECTION | CONTROL | PLAN | LEVEL | 00 | - OVERALL |
| --- | --- | --- | --- | --- | --- | --- |
| GI-1-500-00B | INFECTION | CONTROL | PLAN | LEVEL | 01 | - OVERALL- BG-107 |
| GI-1-500-01A | INFECTION | CONTROL | PLAN | LEVEL | 01 | - OVERALL |
| GI-1-500-01B | INFECTION | CONTROL | PLAN | LEVEL | 01 | - OVERALL CONT. |
| GI-1-500-02A | INFECTION | CONTROL | PLAN | LEVEL | 02 | - OVERALL |
| GI-1-500-02B | INFECTION | CONTROL | PLAN | LEVEL | 02 | - OVERALL CONT. |
| GI-1-500-03A | INFECTION | CONTROL | PLAN | LEVEL | 03 | - PART A |
| GI-1-500-03D | INFECTION | CONTROL | PLAN | LEVEL | 03 | - PART D |
| GI-1-500-04 | INFECTION | CONTROL | PLAN | LEVEL | 04 |  |
| GI-1-500-05 | INFECTION | CONTROL | PLAN | LEVEL | 05 |  |
| GI-1-501-00 | INFECTION | CONTROL | PLAN | LEVEL | 00 | - OVERALL |
| GI-1-507-00 GENERAL - INFECTION CONTROL PLAN |  |  |  |  |  |  |
| GI-1-509-00 | INFECTION | CONTROL | PLAN | LEVEL | 00 | - OVERALL |
| GI-1-509-01 | INFECTION | CONTROL | PLAN | LEVEL | 01 | - OVERALL |
| GI-1-511-00 | INFECTION | CONTROL | PLAN | LEVEL | 00 | - OVERALL |
| GI-1-512-00 | INFECTION | CONTROL | PLAN | LEVEL | 00 | - OVERALL |
| GI-1-512-01 | INFECTION | CONTROL | PLAN | LEVEL | 01 | - OVERALL |
| GI-1-513-00 | INFECTION | CONTROL | PLAN | LEVEL | 00 | - OVERALL |
| GI-1-514-00 | INFECTION | CONTROL | PLAN | LEVEL | 00 | - OVERALL |
| GI-1-515-00 | INFECTION | CONTROL | PLAN | LEVEL | 00 | - OVERALL |
| GI-1-515-01 | INFECTION | CONTROL | PLAN | LEVEL | 01 | - OVERALL |

AE-1-518-00

OVERALL FLOOR PLAN - LICENSE PLATE CAMERA MOUNT DETAILS

GI-1-518-00   INFECTION CONTROL PLAN LEVEL 00 - OVERALL GI-1-519-00   INFECTION CONTROL PLAN LEVEL 00 - OVERALL GI-1-519-00   INFECTION CONTROL PLAN LEVEL 00 - OVERALL GI-1-520-00   INFECTION CONTROL PLAN LEVEL 00 - OVERALL GI-1-521-00   INFECTION CONTROL PLAN LEVEL 00 - OVERALL GI-1-521-01   INFECTION CONTROL PLAN LEVEL 01 - OVERALL CD-1-S01     CAMPUS SITE PLAN - DEMOLITION

CU-1-S01     CAMPUS SITE PLAN - NEW WORK

| TD-1-500-00 | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 00 | - OVERALL |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TD-1-500-00A | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 00 | - PART A |
| TD-1-500-00B | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 00 | - PART B |
| TD-1-500-00C | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 00 | - PART C |
| TD-1-500-00D | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 00 | - PART D |
| TD-1-500-00E | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 00 | - PART E |
| TD-1-500-01 | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 01 | - OVERALL |
| TD-1-500-01A | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 01 | - PART A |
| TD-1-500-01B | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 01 | - PART B |
| TD-1-500-01C | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 01 | - PART C |
| TD-1-500-01D | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 01 | - PART D |
| TD-1-500-01E | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 01 | - PART E |
| TD-1-500-02 | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 02 | - OVERALL |
| TD-1-500-02A | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 02 | - PART A |
| TD-1-500-02B | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 02 | - PART B |
| TD-1-500-02C | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 02 | - PART C |
| TD-1-500-02D | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 02 | - PART D |
| TD-1-500-03A | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 03 | - PART A |
| TD-1-500-03D | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 03 | - PART D |
| TD-1-500-04A | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 04 | - PART A |
| TD-1-500-04D | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 04 | - PART D |
| TD-1-500-05A | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 05 | - PART A |
| TD-1-500-05D | SECURITY | FLOOR | PLAN | - DEMOLITION LEVEL |  |  |  |  | 05 | - PART D |
| TY-0-01 | SECURITY | COVER | SHEET |  |  |  |  |  |  |  |
| TY-1-500-00 | SECURITY | FLOOR | PLAN | LEVEL 00 - OVERALL |  |  |  |  |  |  |
| TY-1-500-00A | SECURITY | FLOOR | PLAN | LEVEL | 00 | - | PART | A |  |  |
| TY-1-500-00B | SECURITY | FLOOR | PLAN | LEVEL | 00 | - | PART | B |  |  |
| TY-1-500-00C | SECURITY | FLOOR | PLAN | LEVEL | 00 | - | PART | C |  |  |
| TY-1-500-00D | SECURITY | FLOOR | PLAN | LEVEL | 00 | - | PART | D |  |  |
| TY-1-500-00E | SECURITY | FLOOR | PLAN | LEVEL | 00 | - | PART | E |  |  |
| TY-1-500-01 | SECURITY | FLOOR | PLAN | LEVEL | 01 | - OVERALL |  |  |  |  |
| TY-1-500-01A | SECURITY | FLOOR | PLAN | LEVEL | 01 | - PART A |  |  |  |  |
| TY-1-500-01B | SECURITY | FLOOR | PLAN | LEVEL | 01 | - PART B |  |  |  |  |
| TY-1-500-01C | SECURITY | FLOOR | PLAN | LEVEL | 01 | - PART C |  |  |  |  |
| TY-1-500-01D | SECURITY | FLOOR | PLAN | LEVEL | 01 | - PART D |  |  |  |  |
| TY-1-500-01E | SECURITY | FLOOR | PLAN | LEVEL | 01 | - PART E |  |  |  |  |
| TY-1-500-02 | SECURITY | FLOOR | PLAN | LEVEL | 02 | - OVERALL |  |  |  |  |
| TY-1-500-02A | SECURITY | FLOOR | PLAN | LEVEL | 02 | - PART A |  |  |  |  |
| TY-1-500-02B | SECURITY | FLOOR | PLAN | LEVEL | 02 | - PART B |  |  |  |  |
| TY-1-500-02C | SECURITY | FLOOR | PLAN | LEVEL | 02 | - PART C |  |  |  |  |
| TY-1-500-02D | SECURITY | FLOOR | PLAN | LEVEL | 02 | - PART D |  |  |  |  |
| TY-1-500-03A | SECURITY | FLOOR | PLAN | LEVEL | 03 | - PART A |  |  |  |  |

TY-1-500-03D	SECURITY FLOOR PLAN LEVEL 03 - PART D TY-1-500-04	SECURITY FLOOR PLAN LEVEL 04

TY-1-500-05	SECURITY FLOOR PLAN LEVEL 05

TY-1-S01	SECURITY SITE PLAN - DEMOLITION

TY-1-S02	SECURITY SITE PLAN - NEW WORK

TY-5-01	SECURITY DETAILS

TY-5-02	SECURITY DETAILS

TY-5-03	SECURITY DETAILS

TY-5-04	SECURITY DETAILS

TY-6-500-01   SECURITY CCTV RISER DIAGRAM TY-6-500-02   SECURITY CCTV RISER DIAGRAM TY-6-500-03   SECURITY CCTV RISER DIAGRAM TY-6-500-04    SECURITY CCTV RISER DIAGRAM

| TY-7-01 TY-7-02 | CAMERA SCHEDULE CAMERA SCHEDULE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| TD-1-501-01 TY-1-501-01 TY-6-501-01 TD-1-507-00 | SECURITY FLOOR PLAN - DEMOLITION LEVEL SECURITY FLOOR PLAN LEVEL 01 SECURITY CCTV RISER DIAGRAM SECURITY FLOOR PLAN - DEMOLITION LEVEL |  |  |  |  | 01 00 |
| TY-1-507-00 TY-6-507-00 | SECURITY FLOOR PLAN LEVEL 00 SECURITY CCTV RISER DIAGRAM |  |  |  |  |  |
| TD-1-509-00 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 00 |
| TD-1-509-01 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 01 |
| TY-1-509-00 | SECURITY | FLOOR | PLAN | LEVEL 00 |  |  |
| TY-1-509-01 | SECURITY | FLOOR | PLAN | LEVEL 01 |  |  |
| TY-6-509-01 | SECURITY | CCTV | RISER | DIAGRAM |  |  |
| TD-1-511-00 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 00 |
| TY-1-511-00 | SECURITY | FLOOR | PLAN | LEVEL 00 |  |  |
| TY-6-511-00 | SECURITY | CCTV | RISER | DIAGRAM |  |  |
| TD-1-512-00 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 00 |
| TD-1-512-01 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 01 |
| TY-1-512-00 | SECURITY | FLOOR | PLAN | LEVEL 00 |  |  |
| TY-1-512-01 | SECURITY | FLOOR | PLAN | LEVEL 01 |  |  |
| TY-6-512-01 | SECURITY | CCTV | RISER | DIAGRAM |  |  |
| TD-1-513-00 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 00 |
| TY-1-513-00 | SECURITY | FLOOR | PLAN | LEVEL 00 |  |  |
| TY-6-513-00 | SECURITY | CCTV | RISER | DIAGRAM |  |  |
| TD-1-514-00 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 00 |
| TY-1-514-00 | SECURITY | FLOOR | PLAN | LEVEL 00 |  |  |
| TY-6-514-00 | SECURITY | CCTV | RISER | DIAGRAM |  |  |
| TD-1-515-00 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 00 |
| TD-1-515-01 | SECURITY | FLOOR | PLAN | - DEMOLITION | LEVEL | 01 |

| TY-1-515-00 | SECURITY | FLOOR PLAN | LEVEL 00 |  |  |
| --- | --- | --- | --- | --- | --- |
| TY-1-515-01 | SECURITY | FLOOR PLAN | LEVEL 01 |  |  |
| TY-6-515-00 | SECURITY | CCTV RISER | DIAGRAM |  |  |
| TD-1-518-01 | SECURITY | FLOOR PLAN | - DEMOLITION | LEVEL | 01 |
| TD-1-518-02 | SECURITY | FLOOR PLAN | - DEMOLITION | LEVEL | 02 |
| TD-1-518-03 | SECURITY | FLOOR PLAN | - DEMOLITION | LEVEL | 03 |
| TD-1-518-04 | SECURITY | FLOOR PLAN | - DEMOLITION | LEVEL | 04 |
| TY-1-518-01 | SECURITY | FLOOR PLAN | LEVEL 01 |  |  |
| TY-1-518-02 | SECURITY | FLOOR PLAN | LEVEL 02 |  |  |
| TY-1-518-03 | SECURITY | FLOOR PLAN | LEVEL 03 |  |  |
| TY-1-518-04 | SECURITY | FLOOR PLAN | LEVEL 04 |  |  |
| TY-6-518-00 | SECURITY | CCTV RISER | DIAGRAM |  |  |
| TD-1-519-00 | SECURITY | FLOOR PLAN | - DEMOLITION | LEVEL | 00 |
| TY-1-519-01 | SECURITY | FLOOR PLAN | LEVEL 00 |  |  |
| TY-6-519-00 | SECURITY | CCTV RISER | DIAGRAM |  |  |
| TD-1-520-00 | SECURITY | FLOOR PLAN | - DEMOLITION | LEVEL | 00 |
| TY-1-520-00 | SECURITY | FLOOR PLAN | LEVEL 00 |  |  |
| TY-6-520-00 | SECURITY | CCTV RISER | DIAGRAM |  |  |
| TD-1-521-00 | SECURITY | FLOOR PLAN | - DEMOLITION | LEVEL | 00 |
| TD-1-521-01 | SECURITY | FLOOR PLAN | - DEMOLITION | LEVEL | 01 |
| TY-1-521-00 | SECURITY | FLOOR PLAN | LEVEL 00 |  |  |
| TY-1-521-01 | SECURITY | FLOOR PLAN | LEVEL 01 |  |  |
| TY-6-521-00 | SECURITY | CCTV RISER | DIAGRAM |  |  |

- - - E N D - - -

SECTION 01 00 00 GENERAL REQUIREMENTS

GENERAL

  - SAFETY REQUIREMENTS

    - Refer to section 01 35 26, SAFETY REQUIREMENTS for safety and infection control requirements.

  - GENERAL INTENTION

    - Contractor shall completely prepare site for building operations, including demolition and removal of existing cameras, and furnish labor and materials and perform work for Campus Wide Security Camera Replacement as required by drawings and specifications.

    - Visits to the site by Bidders may be made only by appointment with the Medical Center Engineering Officer.

    - Offices of Logos BZ, LLC, as Architect-Engineers, will render certain technical services during construction. Such services shall be considered as advisory to the Government and shall not be construed as expressing or implying a contractual act of the Government without affirmations by Contracting Officer or his duly authorized representative.

    - Before placement and installation of work subject to tests by testing laboratory retained by Department of Veterans Affairs, the Contractor shall notify the COR in sufficient time to enable testing laboratory personnel to be present at the site in time for proper taking and testing of specimens and field inspection. Such prior notice shall be not less than three workdays unless otherwise designated by the COR.

    - All employees of general contractor and subcontractors shall comply with VA security management program and obtain permission of the VA police, be identified by project and employer, and restricted from unauthorized access.

  - STATEMENT OF BID ITEM(S)

    - ITEM I, BASE BID Work includes alterationsnecessary removal of existing (stored for the VA) and construction of other items to perform construction of

the CAMPUS WIDE SECURITY CAMERA REPLACEMENT as indicated in the drawings and specifications.

    - ALTERNATE DEDUCT NO.1: BASE BID and delete_30% of the outside fixtures.   Alternate 1’s value should reduce the number of “fish eye” cameras from 252 to 170 and “Multisensor” cameras from 173 to 121. The VA will establish which cameras are to be removed from scope.

    - ALTERNATE DEDUCT NO.2: BASE BID except includes changes associated withALTERNATE DEDUCT NUMBER 1 and remove 30% of the Indoor fixtures reducing “dome cameras” from 215 to 150.  The VA will establish which cameras are to be removed from scope.

  - SPECIFICATIONS AND DRAWINGS FOR CONTRACTOR

Drawings and contract documents may be obtained from the website where the solicitation is posted. Additional copies will be at Contractor's expense.

  - CONSTRUCTION SECURITY REQUIREMENTS

    - Security Plan:

      - The security plan defines both physical and administrative security procedures that will remain effective for the entire duration of the project.

      - The General Contractor is responsible for assuring that all sub- contractors working on the project and their employees also comply with these regulations.

    - Security Procedures:

      - General Contractor’s employees shall not enter the project site without appropriate badge. They may also be subject to inspection of their personal effects when entering or leaving the project site.

      - Before starting work the General Contractor shall give one week’s notice to the Contracting Officer so that security arrangements can be provided for the employees. This notice is separate from any notices required for utility shutdown described later in this section.

      - No photography of VA premises is allowed without written permission of the Contracting Officer. Patients and staff are not to be photographed at any time.

      - VA reserves the right to close down or shut down the project site and order General Contractor’s employees off the premises in the event of a national emergency. The General Contractor may return to the site only with the written approval of the Contracting Officer.

    - Key Control:

      - The General Contractor shall provide duplicate keys and lock combinations to the Contracting officers representative (COR) for the purpose of security inspections of every area of project including tool boxes and parked machines and take any emergency action.

    - Document Control:

      - Before starting any work, the General Contractor/Sub Contractors shall submit an electronic security memorandum describing the approach to following goals and maintaining confidentiality of “sensitive information”.

      - The General Contractor is responsible for safekeeping of all drawings, project manual and other project information. This information shall be shared only with those with a specific need to accomplish the project.

      - Certain documents, sketches, videos or photographs and drawings may be marked “Law Enforcement Sensitive” or “Sensitive Unclassified”. Secure such information in separate containers and limit the access to only those who will need it for the project. Return the information to the Contracting Officer upon request.

      - These security documents shall not be removed or transmitted from the project site without the written approval of Contracting Officer.

      - All paper waste or electronic media such as CD’s and diskettes shall be shredded and destroyed in a manner acceptable to the VA.

      - Notify Contracting Officer and Site Security Officer immediately when there is a loss or compromise of “sensitive information”.

      - All electronic information shall be stored in specified location following VA standards and procedures using an Engineering Document Management Software (EDMS).

        - Security, access and maintenance of all project drawings, both scanned and electronic shall be performed and tracked through the EDMS system.

        - “Sensitive information” including drawings and other documents may be attached to e-mail provided all VA encryption procedures are followed.

    - Motor Vehicle Restrictions

      - Vehicle authorization request shall be required for any vehicle entering the site and such request shall be submitted 24 hours before the date and time of access. Access shall be restricted to picking up and dropping off materials and supplies.

      - A limited number of (2 to 5) permits shall be issued to the General Contractor and its employees for parking in designated areas only. Contractor to coordinate with VA Medical Center Facility Manager.

  - OPERATIONS AND STORAGE AREAS (FAR 52.236-10)

    - The Contractor shall confine all operations (including storage of materials) on Government premises to areas authorized or approved by the Contracting Officer. The Contractor shall hold and save the Government, its officers and agents, free and harmless from liability of any nature occasioned by the Contractor's performance.

    - Temporary buildings (e.g., storage sheds, shops, offices) and utilities may be erected by the Contractor with the approval of the Contracting Officer and shall be built with labor and materials furnished by the Contractor without expense to the Government. The temporary buildings and utilities shall remain the property of the Contractor and shall be removed by the Contractor at its expense upon completion of the work. With the written consent of the Contracting Officer, the buildings and utilities may be abandoned and need not be removed.

    - The Contractor shall, under regulations prescribed by the Contracting Officer, use only established roadways, or use temporary roadways constructed by the Contractor when and as authorized by the Contracting Officer. When materials are transported in prosecuting the work, vehicles shall not be loaded beyond the loading capacity recommended by the manufacturer of the vehicle or prescribed by any Federal, State, or

local law or regulation. When it is necessary to cross curbs or sidewalks, the Contractor shall protect them from damage. The Contractor shall repair or pay for the repair of any damaged curbs, sidewalks, or roads.

    - Working space and space available for storing materials shall be as determined by the COR.

    - Workers are subject to rules of Medical Center applicable to their conduct.

    - Execute work in such a manner as to interfere as little as possible with work being done by others. Keep roads clear of construction materials, debris, standing construction equipment and vehicles at all times.

    - Execute work so as to interfere as little as possible with normal functioning of Medical Center as a whole, including operations of utility services, fire protection systems and any existing equipment, and with work being done by others. Use of equipment and tools that transmit vibrations and noises through the building structure, are not permitted in buildings that are occupied, during construction, jointly by patients or medical personnel, and Contractor's personnel, except as permitted by COR where required by limited working space.

      - Do not store materials and equipment in other than assigned areas.

      - Schedule delivery of materials and equipment to immediate construction working areas within buildings in use by Department of Veterans Affairs in quantities sufficient for not more than two work days. Provide unobstructed access to Medical Center areas required to remain in operation.

      - Where access by Medical Center personnel to vacated portions of buildings is not required, storage of Contractor's materials and equipment will be permitted subject to fire and safety requirements.

    - Utilities Services: Where necessary to cut existing pipes, electrical wires, conduits, cables, etc., of utility services, or of fire protection systems or communications systems (except telephone), they shall be cut and capped at suitable places where shown; or, in absence of such indication, where directed by COR. All such actions shall be coordinated with the COR or Utility Company involved:

      - Whenever it is required that a connection fee be paid to a public utility provider for new permanent service to the construction project, for such items as water, sewer, electricity, gas or steam, payment of such fee shall be the responsibility of the Government and not the Contractor.

    - Phasing:

      - The Medical Center must maintain its operation 24 hours a day 7 days a week. Therefore, any interruption in service must be scheduled and coordinated with the COR to ensure that no lapses in operation occur. It is the CONTRACTOR'S responsibility to develop a work plan and schedule detailing, at a minimum, the procedures to be employed, the equipment and materials to be used, the interim life safety measure to be used during the work, and a schedule defining the duration of the work with milestone subtasks. The work to be outlined shall include, but not be limited to:

      - To ensure such executions, Contractor shall furnish the COR with a schedule (3 week lookahead) of approximate phasing dates on which the Contractor intends to accomplish work in each specific area of site, building or portion thereof. In addition, Contractor shall notify the COR two weeks in advance of the proposed date of starting work in each specific area of site, building or portion thereof. Arrange such phasing dates to ensure accomplishment of this work in successive phases mutually agreeable to COR and Contractor, as follows:

    - Phase IA: Building No.(s) 500, ICRA areas where after-hours work will occur as indicated on drawings. These areas may require additional provision by the VA Police. Coordinate as required with the VA for scheduling.

    - Phase IB: Building No.(s) 500, ICRA areas where work does not occur after- hours as indicated on drawings.

    - Phase II: Site cameras not on buildings.

    - Phase III: Building(s) No.(s) 501, 507, 509, 511, 512, 513, 514, 515,

515, 518, 519, 520, and 521. These buildings will be occupied during performance of work; but immediate areas of alterations will be vacated where possible. Building 507 areas may require additional provision by the VA Police. Coordinate as required with the VA for scheduling.

    - Work Requirements for all Phases: Contractor shall take all measures and provide all material necessary for protecting existing equipment and property in affected areas of construction against dust and debris, so that equipment and affected areas to be used in the Medical Centers operations will not be hindered. Contractors shall permit access to Department of Veterans Affairs personnel and patients through other construction areas that serve as routes of access to such affected areas and equipment. These routes, whether access or egress shall be isolated from the construction area by temporary partitions and have walking surfaces, lighting etc. to facilitate patient and staff access. Coordinate alteration work in areas occupied by Department of Veterans Affairs so that Medical Center operations will continue during the construction period.

    - When a construction site is turned over to Contractor, Contractor shall accept entire responsibility including upkeep and maintenance therefore:

      - Contractor shall maintain a minimum temperature of 4 degrees C (40 degrees F) at all times, except as otherwise specified.

      - Contractor shall maintain in operating condition existing fire protection and alarm equipment. In connection with fire alarm equipment, Contractor shall make arrangements for pre-inspection of site with Fire Department or Company (Department of Veterans Affairs or municipal) whichever will be required to respond to an alarm from Contractor's employee or watchman.

    - Utilities Services: Maintain existing utility services for Medical Center at all times. Provide temporary facilities, labor, materials, equipment, connections, and utilities to assure uninterrupted services. Where necessary to cut existing water, steam, gases, sewer or air pipes, or conduits, wires, cables, etc. of utility services or of fire protection systems and communications systems (including telephone), they shall be cut and capped at suitable places where shown; or, in absence of such indication, where directed by COR.

      - No utility service such as water, gas, steam, sewers or electricity, or fire protection systems and communications systems may be

interrupted without prior approval of COR. Electrical work shall be accomplished with all affected circuits or equipment de-energized.

When an electrical outage cannot be accomplished, work on any energized circuits or equipment shall not commence without a detailed work plan, the Medical Center Director’s prior knowledge and written approval. Refer to specification Sections 26 05 11, REQUIREMENTS FOR ELECTRICAL INSTALLATIONS, 27 05 11 REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS and 28 05 00, COMMON WORK RESULTS FOR

ELECTRONIC SAFETY AND SECURITY for additional requirements.

      - Contractor shall submit a request to interrupt any such services to COR, in writing, 14 days in advance of proposed interruption. Request shall state reason, date, exact time of, and approximate duration of such interruption.

      - Contractor will be advised (in writing) of approval of request, or of which other date and/or time such interruption will cause least inconvenience to operations of Medical Center. Interruption time approved by Medical Center may occur at other than Contractor's normal working hours.

      - Major interruptions of any system must be requested, in writing, at least 15 calendar days prior to the desired time and shall be performed as directed by the COR.

      - In case of a contract construction emergency, service will be interrupted on approval of COR. Such approval will be confirmed in writing as soon as practical.

      - Whenever it is required that a connection fee be paid to a public utility provider for new permanent service to the construction project, for such items as water, sewer, electricity, gas or steam, payment of such fee shall be the responsibility of the Government and not the Contractor.

    - Abandoned Lines: All service lines such as wires, cables, conduits, ducts, pipes and the like, and their hangers or supports, shall be removed back to their source. Those that are indicated to be abandoned but are not required to be entirely removed, shall be sealed, capped or plugged at the main, branch or panel they originate from. The lines shall not be capped in finished areas, but shall be removed and sealed, capped or plugged in ceilings, within furred spaces, in unfinished

areas, or within walls or partitions; so that they are completely behind the finished surfaces.

    - To minimize interference of construction activities with flow of Medical Center traffic, comply with the following:

      - Keep roads, walks and entrances to grounds, to parking and to occupied areas of buildings clear of construction materials, debris and standing construction equipment and vehicles. Wherever excavation for new utility lines cross existing roads, at least one lane must be open to traffic at all times with approval.

      - Method and scheduling of required cutting, altering and removal of existing roads, walks and entrances must be approved by the COR.

    - Coordinate the work for this contract with other construction operations as directed by COR. This includes the scheduling of traffic and the use of roadways, as specified in Article, USE OF ROADWAYS.

  - ALTERATIONS

    - Survey: Before any work is started, the Contractor shall make a thorough survey with the COR and a representative of VA Supply Service, of buildingsin which alterations occur and areas which are anticipated routes of access, and furnish a report, signed by both, to the Contracting Officer. This report shall list by rooms and spaces:

      - Existing condition and types of resilient flooring, doors, windows, walls and other surfaces not required to be altered throughout affected areas of buildings.

      - Existence and conditions of items such as plumbing fixtures and accessories, electrical fixtures, equipment, venetian blinds, shades, etc., required by drawings to be either reused or relocated, or both.

      - Shall note any discrepancies between drawings and existing conditions at site.

      - Shall designate areas for working space, materials storage and routes of access to areas within buildings where alterations occur and which have been agreed upon by Contractor and COR.

    - Any items required by drawings to be either reused or relocated or both, found during this survey to be nonexistent, or in opinion of COR

and/or Supply Representative, to be in such condition that their use is impossible or impractical, shall be furnished and/or replaced by Contractor with new items in accordance with specifications which will be furnished by Government. Provided the contract work is changed by reason of this subparagraph B, the contract will be modified accordingly, under provisions of clause entitled "DIFFERING SITE CONDITIONS" (FAR 52.236-2) and "CHANGES" (FAR 52.243-4).

    - Re-Survey: Thirty days before expected partial or final inspection date, the Contractor and COR together shall make a thorough re-survey of the areas of buildings involved. They shall furnish a report on conditions then existing, of resilient flooring, doors, windows, walls and other surfaces as compared with conditions of same as noted in first condition survey report:

      - Re-survey report shall also list any damage caused by Contractor to such flooring and other surfaces, despite protection measures; and, will form basis for determining extent of repair work required of Contractor to restore damage caused by Contractor's workers in executing work of this contract.

    - Protection: Provide the following protective measures:

      - Wherever existing roof surfaces are disturbed they shall be protected against water infiltration. In case of leaks, they shall be repaired immediately upon discovery.

      - Temporary protection against damage for portions of existing structures and grounds where work is to be done, materials handled and equipment moved and/or relocated.

      - Protection of interior of existing structures at all times, from damage, dust and weather inclemency. Wherever work is performed, floor surfaces that are to remain in place shall be adequately protected prior to starting work, and this protection shall be maintained intact until all work in the area is completed.

  - DISPOSAL AND RETENTION

    - Materials and equipment accruing from work removed and from demolition of buildings or structures, or parts thereof, shall be disposed of as follows:

      - Reserved items which are to remain property of the Government are noted on drawings or in specifications as items to be stored. Items

that remain property of the Government shall be removed or dislodged from present locations in such a manner as to prevent damage which would be detrimental to re-installation and reuse. Store such items where directed by COR.

      - Items not reserved shall become property of the Contractor and be removed by Contractor from Medical Center.

      - Items of portable equipment and furnishings located in rooms and spaces in which work is to be done under this contract shall remain the property of the Government. When rooms and spaces are vacated by the Department of Veterans Affairs during the alteration period, such items which are NOT required by drawings and specifications to be either relocated or reused will be removed by the Government in advance of work to avoid interfering with Contractor's operation.

      - PCB Transformers and Capacitors: The Contractor shall be responsible for disposal of the Polychlorinated Biphenyl (PCB) transformers and capacitors. The transformers and capacitors shall be taken out of service and handled in accordance with the procedures of the Environmental Protection Agency (EPA) and the Department of Transportation (DOT) as outlined in Code of Federal Regulation (CFR), Titled 40 and 49 respectively. The EPA's Toxic Substance Control Act (TSCA) Compliance Program Policy Nos. 6-PCB-6 and 6-PCB-7 also apply. Upon removal of PCB transformers and capacitors for disposal, the "originator" copy of the Uniform Hazardous Waste Manifest (EPA Form 8700-22), along with the Uniform Hazardous Waste Manifest Continuation Sheet (EPA Form 8700-22A) shall be returned to the Contracting Officer who will annotate the contract file and transmit the Manifest to the Medical Center'sChief.

        - Copies of the following listed CFR titles may be obtained from the Government Printing Office:

| 40 | CFR | 261 | .......Identification and Listing of Hazardous Waste |
| --- | --- | --- | --- |
| 40 | CFR | 262 | .......Standards Applicable to Generators of Hazardous |

Waste

40 CFR 263 .......Standards Applicable to Transporters of

Hazardous Waste

40 CFR 761 .......PCB Manufacturing, Processing, Distribution in Commerce, and use Prohibitions

49 CFR 172 .......Hazardous Material tables and Hazardous

Material Communications Regulations

49 CFR 173 .......Shippers - General Requirements for Shipments and Packaging

| 49 | CRR | 173 | .......Subpart A General |
| --- | --- | --- | --- |
| 49 | CFR | 173 | .......Subpart B Preparation of Hazardous Material for |

Transportation

49 CFR 173 .......Subpart J Other Regulated Material; Definitions and Preparation

TSCA Compliance Program Policy Nos. 6- PCB-6 and 6-PCB-7

  - PROTECTION OF EXISTING VEGETATION, STRUCTURES, EQUIPMENT, UTILITIES, AND IMPROVEMENTS (FAR 52.236-9)

    - The Contractor shall preserve and protect all structures, equipment, and vegetation (such as trees, shrubs, and grass) on or adjacent to the work site, which are not to be removed, and which do not unreasonably interfere with the work required under this contract. The Contractor shall only remove trees when specifically authorized to do so and shall avoid damaging vegetation that will remain in place. If any limbs or branches of trees are broken during contract performance, or by the careless operation of equipment, or by workers, the Contractor shall trim those limbs or branches with a clean cut and paint the cut with a tree-pruning compound as directed by the Contracting Officer.

    - The Contractor shall protect from damage all existing improvements and utilities at or near the work site and on adjacent property of a third party, the locations of which are made known to or should be known by the Contractor. The Contractor shall repair any damage to those facilities, including those that are the property of a third party, resulting from failure to comply with the requirements of this contract or failure to exercise reasonable care in performing the work.

    - If the Contractor fails or refuses to repair the damage promptly, the Contracting Officer may have the necessary work performed and charge the cost to the Contractor.

    - Refer to Section 01 57 19, TEMPORARY ENVIRONMENTAL CONTROLS, for

additional requirements on protecting vegetation, soils and the environment. Refer to Articles, "Alterations", "Restoration", and "Operations and Storage Areas" for additional instructions concerning repair of damage to structures and site improvements.

  - RESTORATION

    - Remove, cut, alter, replace, patch and repair existing work as necessary to install new work. Except as otherwise shown or specified, do not cut, alter or remove any structural work, and do not disturb any ducts, plumbing, steam, gas, or electric work without approval of the COR. Existing work to be altered or extended and that is found to be defective in any way, shall be reported to the COR before it is disturbed. Materials and workmanship used in restoring work, shall conform in type and quality to that of original existing construction, except as otherwise shown or specified.

    - Upon completion of contract, deliver work complete and undamaged. Existing work (walls, ceilings, partitions, floors, mechanical and electrical work, lawns, paving, roads, walks, etc.) disturbed or removed as a result of performing required new work, shall be patched, repaired, reinstalled, or replaced with new work, and refinished and left in as good condition as existed before commencing work.

    - At Contractor's own expense, Contractor shall immediately restore to service and repair any damage caused by Contractor's workers to existing piping and conduits, wires, cables, etc., of utility services or of fire protection systems and communications systems (including telephone) which are not scheduled for discontinuance or abandonment.

    - Expense of repairs to such utilities and systems not shown on drawings or locations of which are unknown will be covered by adjustment to contract time and price in accordance with clause entitled "CHANGES" (FAR 52.243-4) and "DIFFERING SITE CONDITIONS" (FAR 52.236-2).

  - PHYSICAL DATA – SITE AND SOIL CONDITIONS

    - Available Data: The subsurface data, site surveys, and investigation results provided in the contract documents are for informational purposes. This data represents the conditions at the specific locations and times indicated.

    - Subsurface Investigations:

      - Subsurface conditions were determined via core borings and test pits as shown in the [Insert Drawing/Attachment Reference].

      - The Government does not warrant that these conditions are continuous across the entire site or that the proportions of materials will remain constant between boring locations.

    - Contractor Responsibility: In accordance with the Site Investigation and Conditions Affecting the Work requirements, the Contractor is responsible for:

      - Reviewing all provided logs and site data.

      - Conducting an independent site visit to evaluate surface and visible conditions.

      - Forming independent conclusions regarding the character and difficulty of the work.

    - Supplemental Exploration: Upon written request to the Department of Veterans Affairs, bidders may be permitted to conduct independent subsurface explorations at their own expense, subject to agency security and scheduling requirements.

  - PROFESSIONAL SURVEYING SERVICES

    - A registered professional land surveyor or registered civil engineer whose services are retained and paid for by the Contractor shall perform services specified herein and in other specification sections. The Contractor shall certify that the land surveyor or civil engineer is not one who is a regular employee of the Contractor, and that the land surveyor or civil engineer has no financial interest in this contract.

  - LAYOUT OF WORK

    - The Contractor shall lay out the work from Government established base lines and bench marks, indicated on the drawings, and shall be responsible for all measurements in connection with the layout. The Contractor shall furnish, at Contractor's own expense, all stakes, templates, platforms, equipment, tools, materials, and labor required to lay out any part of the work. The Contractor shall be responsible for executing the work to the lines and grades that may be established or indicated by the Contracting Officer. The Contractor shall also be

responsible for maintaining and preserving all stakes and other marks established by the Contracting Officer until authorized to remove them. If such marks are destroyed by the Contractor or through Contractor's negligence before their removal is authorized, the Contracting Officer may replace them and deduct the expense of the replacement from any amounts due or to become due to the Contractor.

(FAR 52.236-17)

    - Establish and plainly mark center lines for each building and corner of column lines and/or addition to each existing building, and such other lines and grades that are reasonably necessary to properly assure that location, orientation, and elevations established for each such structure and/or addition, roads, and parking lots are in accordance with lines and elevations shown on contract drawings.

    - During progress of work, and particularly as work progresses from floor to floor, Contractor shall have line grades and plumbness of all major form work checked and certified by a registered land surveyor or registered civil engineer as meeting requirements of contract drawings. Furnish such certification to the COR before any major items of concrete work are placed. In addition, Contractor shall also furnish to the COR certificates from a registered land surveyor or registered civil engineer that the following work is complete in every respect as required by contract drawings.

      - Lines of each building and/or addition.

      - Elevations of bottoms of footings and tops of floors of each building and/or addition.

      - Lines and elevations of sewers and of all outside distribution systems.

      - Lines of elevations of all swales and interment areas.

      - Lines and elevations of roads, streets and parking lots.

    - Upon completion of the work, the Contractor shall furnish the COR one electronic copy and reproducible drawings at the scale of the contract drawings, showing the finished grade on the grid developed for constructing the work, fifty foot stationing along new road

centerlines. These drawings shall bear the seal of the registered land surveyor or registered civil engineer.

    - The Contractor shall perform the surveying and layout work of this and other articles and specifications in accordance with the provisions of Article "Professional Surveying Services".

  - AS-BUILT DRAWINGS

    - The contractor shall maintain two full size sets of as-built drawings which will be kept current during construction of the project, to include all contract changes, modifications and clarifications. All Red Lines (changes) to be provided to the A/E so that they can be incorporated into .pdf As-Builts.

    - All variations shall be shown in the same general detail as used in the contract drawings. To ensure compliance, as-built drawings shall be made available for the COR review, as often as requested.

    - Contractor shall deliver two approved completed sets of as-built drawings in the electronic version (scanned PDF) to the COR within 15 calendar days after each completed phase and after the acceptance of the project by the COR.

    - Paragraphs A, B, & C shall also apply to all shop drawings.

  - WARRANTY MANAGEMENT

    - Warranty Management Plan: Develop a warranty management plan which contains information relevant to FAR 52.246-21 Warranty of Construction in least 30 days before the planned pre-warranty conference, submit one set of the warranty management plan. Include within the warranty management plan all required actions and documents to ensure that the Government receives all warranties to which it is entitled. The plan must be in narrative form and contain sufficient detail to render it suitable for use by future maintenance and repair personnel, whether tradesman, or of engineering background, not necessarily familiar with this contract. The term “status” as indicated below must include due date and whether item has been submitted or was approved. Warranty information made available during the construction phase must be submitted to the Contracting Officer for approval prior to each monthly invoice for payment. Assemble approved information in a binder and turn over to the Government upon acceptance of the work. The construction warranty period will begin on the date of the project acceptance and continue for the product warranty period. A joint 4 month and 9 month warranty inspection will be conducted, measured from time of

acceptance, by the Contactor and the Contracting Officer. Include in the warranty management plan, but not limited to, the following:

      - Roles and responsibilities of all personnel associated with the warranty process, including points of contact and telephone numbers within the company of the Contractor, subcontractors, manufacturers or suppliers involved.

      - Furnish with each warranty the name, address and telephone number of each of the guarantor’s representatives nearest project location.

      - Listing and status of delivery of all Certificates of Warranty for extended warranty items, to include roofs, HVAC balancing, pumps, motors, transformers and for all commissioned systems such as fire protection and alarm systems, sprinkler systems and lightning protection systems, etc.

      - A list for each warranted equipment item, feature of construction or system indicating:

- Name of item.

- Model and serial numbers.

- Location where installed.

- Name and phone numbers of manufacturers and suppliers.

- Name and phone numbers of manufacturers or suppliers.

- Names, addresses and phone numbers of sources of spare parts.

- Warranties and terms of warranty. Include one-year overall warranty of construction, including the starting date of warranty of construction. Items which have extended warranties must be indicated with separate warranty expiration dates.

- Starting point and duration of warranty period.

- Summary of maintenance procedures required to continue the warranty in force.

- Cross-reference to specific pertinent Operation and Maintenance manuals.

- Organizations, names and phone numbers of persons to call for warranty service.

- Typical response time and repair time expected for various warranted equipment.

      - The plans for attendance at the 4 and 9-month post construction warranty inspections conducted by the government.

      - Procedure and status of tagging of all equipment covered by extended warranties.

      - Copies of instructions to be posted near selected pieces of equipment where operation is critical for warranty and/or safety reasons.

    - Performance & Payment Bonds: The Performance & Payment Bonds must remain effective throughout the construction period

      - In the event the Contractor fails to commence and diligently pursue any construction warranty work required, the Contracting Officer will have the work performed by others, and after completion of the work, will charge the remaining construction warranty funds of expenses incurred by the Government while performing the work, including, but not limited to administrative expenses.

      - In the event sufficient funds are not available to cover the construction warranty work performed by the Government at the contractor’s expenses, the Contracting Officer will have the right to recoup expenses from the bonding company.

      - Following oral or written notification of required construction warranty repair work, the Contractor shall respond in a timely manner. Written verification will follow oral instructions. Failure to respond will be cause for the Contracting Officer to proceed against the Contractor.

    - Pre-Warranty Conference: Prior to contract completion, and at a time designated by the Contracting Officer, the Contractor shall meet with the Contracting Officer to develop a mutual understanding with respect to the requirements of this section. Communication procedures for Contractor notification of construction warranty defects, priorities with respect to the type of defect, reasonable time required for Contractor response, and other details deemed necessary by the Contracting Officer for the execution of the construction warranty will be established/ reviewed at this meeting. In connection with these requirements and at the time of the Contractor’s quality control completion inspection, furnish the name, telephone number and address of a licensed and bonded company which is authorized to initiate and pursue construction warranty work action on behalf of the Contractor. This point of contract will be located within the local service area of

the warranted construction, be continuously available and be responsive to Government inquiry on warranty work action and status. This requirement does not relieve the Contractor of any of its responsibilities in conjunction with other portions of this provision.

    - Contractor’s Response to Construction Warranty Service Requirements:

    - Following oral or written notification by the Contracting Officer, the Contractor shall respond to construction warranty service requirements in accordance with the “Construction Warranty Service Priority List” and the three categories of priorities listed below. Submit a report on any warranty item that has been repaired during the warranty period. Include within the report the cause of the problem, date reported, corrective action taken, and when the repair was completed. If the Contractor does not perform the construction warranty within the timeframe specified, the Government will perform the work and back charge the construction warranty payment item established.

      - First Priority Code 1. Perform onsite inspection to evaluate situation, and determine course of action within 4 hours, initiate work within 6 hours and work continuously to completion or relief.

      - Second Priority Code 2. Perform onsite inspection to evaluate situation, and determine course of action within 8 hours, initiate work within 24 hours and work continuously to completion or relief.

      - Third Priority Code 3. All other work to be initiated within 3 work days and work continuously to completion or relief.

      - The “Construction Warranty Service Priority List” is as follows:

        - Code 1-Life Safety Systems

          - Fire suppression systems.

          - Fire alarm system(s).

        - Code 1-Air Conditioning Systems

          - Air conditioning leak in part of the building, if causing damage.

          - Air conditioning system not cooling properly.

        - Code 1 Doors

          - Overhead doors not operational, causing a security, fire or safety problem.

- Interior, exterior personnel doors or hardware, not functioning properly, causing security, fire or safety problem.

        - Code 3-Doors

          - Overhead doors not operational.

          - Interior/exterior personnel doors or hardware not functioning properly.

        - Code 1-Electrical

          - Power failure (entire area or any building operational after 1600 hours).

          - Security lights.

          - Smoke detectors.

        - Code 2-Electrical

          - Power failure (no power to a room or part of building). Receptacle and lights not operational (in a room or part of building).

        - Code 3-Electrical

          - Exterior lights not operational.

        - Code 1-Gas

          - Leaks and pipeline breaks.

        - Code 1-Heat

          - Power failure affecting heat.

        - Code 1-Plumbing

          - Hot water heater failure.

          - Leaking water supply pipes

        - Code 2-Plumbing

          - Flush valves not operating properly

          - Fixture drain, supply line or any water pipe leaking.

          - Toilet leaking at base.

        - Code 3- Plumbing

          - Leaky faucets.

        - Code 3-Interior

          - Floors damaged.

          - Paint chipping or peeling.

          - Casework damaged.

        - Code 1-Roof Leaks

          - Damage to property is occurring.

        - Code 2-Water (Exterior)

          - No water to facility.

        - Code 2-Water (Hot)

          - No hot water in portion of building listed.

        - Code 3

          - All work not listed above.

    - Warranty Tags: At the time of installation, tag each warranted item with a durable, oil and water-resistant tag approved by the Contracting Officer. Attach each tag with a copper wire and spray with a silicone waterproof coating. Also submit two record copies of the warranty tags showing the layout and design. The date of acceptance and the QC signature must remain blank until the project is accepted for beneficial occupancy. Show the following information on the tag.

Warranty Tags

Type of product/material

Model number

Serial number

Contract number

Warranty period from/to

Inspector’s signature

Construction Contractor

Address

Telephone number

Warranty Contact

Address

Telephone number

Warranty response time priority code

  - USE OF ROADWAYS

    - For hauling, use only established public roads and roads on Medical Center property and, when authorized by the COR, such temporary roads which are necessary in the performance of contract work. Temporary

roads shall be constructed and restoration performed by the Contractor at Contractor's expense. When necessary to cross curbing, sidewalks, or similar construction, they must be protected by well-constructed bridges.

    - When certain buildings (or parts of certain buildings) are required to be completed in advance of general date of completion, all roads leading thereto must be completed and available for use at time set for completion of such buildings or parts thereof.

  - RESIDENT ENGINEER'S FIELD OFFICE –

    - The Contractor shall, within fifteen (15) days after receipt of Notice to Proceed, provide where shown on the drawings a temporary field office, furniture, and two inch deep gravel surfaced area for access for the COR. Office and furniture shall be new.

    - The field office shall provide not less than 67 square meters (720 gross square feet) of floor area in one unit. Installation of the office shall meet all local codes.

    - Provide office with two, 900 mm (three foot) wide exterior doors, including hardware and OSHA approved platform and stairs leading to grade.

    - Enclose the entire perimeter of the office from the floor to the ground and finish to match exterior. Provide R7 insulation and seal tight to ground with a painted 19 mm (3/4 inch) exterior grade plywood skirt.

    - Exterior finishes shall be manufacturer's standards.

    - Provide floor, wall, and roof with not less than R5 insulation.

    - Interior finishes shall consist of resilient flooring, plywood paneling or painted wallboard on walls, and acoustical tile ceilings. Interior doors may be either painted or stained.

    - Interior shall be subdivided with full height partitions to provide one office, one toilet Provide each space with 900 mm (three foot) wide door with master keyed locks.

    - Provide 750 mm (2-1/2 feet) wide by 900 mm (3 feet) high operable windows; two in each room (none required in sample room), except provide only one 600 mm (2 foot) high window in toilet room(s). Window openings shall be fitted with security bars to prevent any forced

entry. The doors/of field office shall have a hasp and padlock and also deadbolts keyed from both sides.

    - Provide sufficient fluorescent lighting in each room to deliver 750 lux (70 foot-candles) of light at desk top height without the aid of daylight. Provide one light switch in each room.

    - Provide one duplex receptacle in each wall of each room. If a wall is

3.0 m (10 feet) long or more, provide two receptacles for each 3.0 m (10 feet), or portion thereof, of wall. Provide two duplex receptacles in low partition at secretary's desk.

    - The Contractor shall provide the following:

      - Electricity, hot and cold water, and necessary utility services (except telephone).

      - All necessary piping, power circuits network cabling, cat 5e or better cabling for phones and computers, electrical fixtures, lighting, and other items necessary to provide a habitable structure for the purpose intended. The number of network and electrical receptacles will be as per attached drawing of the field office.

      - Thermostatically controlled, centralized heating and air conditioning system designed to maintain the temperature between 21 and 27 degrees C (70 and 80 degrees F) with 50 percent relative humidity maintained during the air conditioning season.

      - One water closet, lavatory, mirror, toilet paper dispenser, paper towel dispenser, soap dispenser, towel bar, and two-prong coat hooks

      - The contractor to install a suitable alarm system for the field office.

    - Contractor shall, for the duration of the COR occupancy, provide the following:

      - Satisfactory conditions in and around the field office and parking area.

      - Maintenance of gravel surfaced area, including the area for parking, in an acceptable condition for vehicle and foot traffic at all times.

      - Maintenance of utility services.

      - Daily janitorial services and supplies (toilet paper, soap, etc.).

      - Potable water, fuel and electric power for normal office uses, including lights, heating and air conditioning.

    - The Contractor shall provide the following new items:

QUANTITY REQUIRED MINIMUMS

1 workstation with adjustable keying desk or drawer 738 mm H x 1.5 m W x 760 mm D (size 29-1/2" H x 60" W x 30" D)

3 Office desks, double pedestal

1 Conference table 900 mm x 1.8 m (size 3' x 6')

1 Plan table 1.2 m x 2.1 m (4' x 7')

    - At the completion of all work, including the punch list, the COR field office and facilities shall become the property of the Contractor and

Contractor shall remove same, including utility connections. The site shall be restored to original condition and finished in accordance with contract requirements. Government and be left intact, including utility connections, for future use by Department of Veterans Affairs.

    - The Contractor shall furnish floor plans for approval by the COR prior to furnishing the field office.

  - TEMPORARY USE OF MECHANICAL AND ELECTRICAL EQUIPMENT

    - Use of new installed mechanical and electrical equipment to provide heat, ventilation, plumbing, light and power will be permitted subject to written approval and compliance with the following provisions:

      - Permission to use each unit or system must be given by COR in writing. If the equipment is not installed and maintained in accordance with the written agreement and following provisions, the COR will withdraw permission for use of the equipment.

      - Electrical installations used by the equipment shall be completed in accordance with the drawings and specifications to prevent damage to the equipment and the electrical systems, i.e. transformers, relays, circuit breakers, fuses, conductors, motor controllers and their overload elements shall be properly sized, coordinated and adjusted. Installation of temporary electrical equipment or devices shall be in accordance with NFPA 70, National Electrical Code, (2014 Edition), Article 590, Temporary Installations. Voltage supplied to each item of equipment shall be verified to be correct and it shall be determined that motors are not overloaded. The electrical equipment shall be thoroughly cleaned before using it and again immediately before final inspection including vacuum cleaning and wiping clean interior and exterior surfaces.

      - Units shall be properly lubricated, balanced, and aligned. Vibrations must be eliminated.

      - Automatic temperature control systems for preheat coils shall function properly and all safety controls shall function to prevent coil freeze-up damage.

      - The air filtering system utilized shall be that which is designed for the system when complete, and all filter elements shall be

replaced at completion of construction and prior to testing and balancing   of system.

      - All components of heat production and distribution system, metering equipment, condensate returns, and other auxiliary facilities used in temporary service shall be cleaned prior to use; maintained to prevent corrosion internally and externally during use; and cleaned, maintained and inspected prior to acceptance by the Government.

    - Prior to final inspection, the equipment or parts used which show wear and tear beyond normal, shall be replaced with identical replacements, at no additional cost to the Government.

    - This paragraph shall not reduce the requirements of the mechanical and electrical specifications sections.

    - Any damage to the equipment or excessive wear due to prolonged use will be repaired replaced by the contractor at the contractor’s expense.

  - TEMPORARY USE OF EXISTING ELEVATORS

    - Contractor will not be allowed the use of existing elevators. Outside type hoist shall be used by Contractor for transporting materials and equipment.

    - Use of existing elevators for handling building	materials and Contractor's personnel will be permitted subject to following provisions:

      - Contractor makes all arrangements with the COR for use of elevators. The COR will ascertain that elevators are in proper condition Buildings. Contractor may use non public (loading) elevators in .and for special nonrecurring time intervals when permission is granted. Personnel for operating elevators will not be provided by the Department of Veterans Affairs.

      - Contractor covers and provides maximum protection of following elevator components:

        - Entrance jambs, heads soffits and threshold plates.

        - Entrance columns, canopy, return panels and inside surfaces of car enclosure walls.

        - Finish flooring.

      - Government will accept hoisting ropes of elevator and rope of each speed governor if they are worn under normal operation. However, if

these ropes are damaged by action of foreign matter such as sand, lime, grit, stones, etc., during temporary use, they shall be removed and replaced by new hoisting ropes at the contractors expense.

      - If brake lining of elevators are excessively worn or damaged during temporary use, they shall be removed and replaced by new brake lining at the contractors expense.

      - All parts of main controller, starter, relay panel, selector, etc., worn or damaged during temporary use shall be removed and replaced with new parts at the contractors expense, if recommended by elevator inspector after elevator is released by Contractor.

      - Place elevator in condition equal, less normal wear, to that existing at time it was placed in service of Contractor as approved by Contracting Officer.

  - TEMPORARY TOILETS

    - Provide where directed, (for use of all Contractor's workers) ample temporary sanitary toilet accommodations with suitable sewer and water connections; or, when approved by COR, provide suitable dry closets where directed. Keep such places clean and free from flies and all connections and appliances connected therewith are to be removed prior to completion of contract, and premises left perfectly clean.

      - *Contractor may have for use of Contractor's workers, such toilet accommodations as may be assigned to Contractor by Medical Center., contractor shall keep such places clean and be responsible for any damage done thereto by Contractor's workers. Failure to maintain satisfactory condition in toilets will deprive Contractor of the privilege to use such toilets.

  - AVAILABILITY AND USE OF UTILITY SERVICES

    - The Government shall make all reasonably required amounts of utilities available to the Contractor from existing outlets and supplies, as specified in the contract. The amount to be paid by the Contractor for chargeable electrical services shall be the prevailing rates charged to the Government. The Contractor shall carefully conserve any utilities furnished without charge.

    - The Contractor, at Contractor's expense and in a workmanlike manner, in compliance with code and as satisfactory to the Contracting Officer, shall install and maintain all necessary temporary connections and distribution lines, and all meters required to measure the amount of electricity used for the purpose of determining charges. Before final acceptance of the work by the Government, the Contractor shall remove all the temporary connections, distribution lines, meters, and associated paraphernalia and repair restore the infrastructure as required.

    - Contractor shall install meters at Contractor's expense and furnish the Medical Center a monthly record of the Contractor's usage of electricity as hereinafter specified.

    - Heat: Furnish temporary heat necessary to prevent injury to work and materials through dampness and cold. Use of open salamanders or any temporary heating devices which may be fire hazards or may smoke and damage finished work, will not be permitted. Maintain minimum temperatures as specified for various materials:

      - Obtain heat by connecting to Medical Center heating distribution system.

    - Electricity (for Construction and Testing): Furnish all temporary electric services.

      - Obtain electricity by connecting to the Medical Center electrical distribution system. The Contractor shall meter and pay for electricity required for electric cranes and hoisting devices, electrical welding devices and any electrical heating devices providing temporary heat. Electricity for all other uses is available at no cost to the Contractor.

    - Water (for Construction and Testing): Furnish temporary water service.

      - Obtain water by connecting to the Medical Center water distribution system. Provide reduced pressure backflow preventer at each connection as per code. Water is available at no cost to the Contractor.

      - Maintain connections, pipe, fittings and fixtures and conserve

water-use so none is wasted. Failure to stop leakage or other wastes will be cause for revocation (at COR discretion) of use of water from Medical Center's system.

    - Fuel: Natural and LP gas and burner fuel oil required for boiler cleaning, normal initial boiler-burner setup and adjusting, and for performing the specified boiler tests will be furnished by the Government. Fuel required for prolonged boiler-burner setup, adjustments, or modifications due to improper design or operation of boiler, burner, or control devices shall be furnished and paid by the Contractor at Contractor's expense.

  - NEW TELEPHONE EQUIPMENT

    - The contractor shall coordinate with the work of installation of telephone equipment by others. This work shall be completed before the building is turned over to VA.

  - TESTS

    - As per specification section 23 05 93 the contractor shall provide a written testing plan complete with component level, equipment level, sub-system level and system level breakdowns. The plan will provide a schedule and a written sequence of what will be tested, how and what the expected outcome will be. This document will be submitted for approval prior to commencing work. The contractor shall document the results of the approved plan and submit for approval with the as built documentation.

    - Pre-test mechanical and electrical equipment and systems and make corrections required for proper operation of such systems before requesting final tests. Final test will not be conducted unless pre-tested.

    - Conduct final tests required in various sections of specifications in presence of an authorized representative of the Contracting Officer. Contractor shall furnish all labor, materials, equipment, instruments, and forms, to conduct and record such tests.

    - Mechanical and electrical systems shall be balanced, controlled and coordinated. A system is defined as the entire system which must be coordinated to work together during normal operation to produce results for which the system is designed. For example, air conditioning supply air is only one part of entire system which provides comfort conditions for a building. Other related components are return air, exhaust air, steam, chilled water, refrigerant, hot water, controls and electricity,

etc. Another example of a system which involves several components of different disciplines is a boiler installation. Efficient and acceptable boiler operation depends upon the coordination and proper operation of fuel, combustion air, controls, steam, feedwater, condensate and other related components.

    - All related components as defined above shall be functioning when any system component is tested. Tests shall be completed within a reasonably period of time during which operating and environmental conditions remain reasonably constant and are typical of the design conditions.

    - Individual test result of any component, where required, will only be accepted when submitted with the test results of related components and of the entire system.

  - INSTRUCTIONS

    - Contractor shall furnish Maintenance and Operating manuals (hard copies and electronic) and verbal instructions when required by the various sections of the specifications and as hereinafter specified.

    - Manuals: Maintenance and operating manuals and one compact disc (four hard copies and one electronic copy each) for each separate piece of equipment shall be delivered to the COR coincidental with the delivery of the equipment to the job site. Manuals shall be complete, detailed guides for the maintenance and operation of equipment. They shall include complete information necessary for starting, adjusting, maintaining in continuous operation for long periods of time and dismantling and reassembling of the complete units and sub-assembly components. Manuals shall include an index covering all component parts clearly cross-referenced to diagrams and illustrations. Illustrations shall include "exploded" views showing and identifying each separate item. Emphasis shall be placed on the use of special tools and instruments. The function of each piece of equipment, component, accessory and control shall be clearly and thoroughly explained. All necessary precautions for the operation of the equipment and the reason for each precaution shall be clearly set forth. Manuals must reference the exact model, style and size of the piece of equipment and system being furnished. Manuals referencing equipment similar to but of a

different model, style, and size than that furnished will not be accepted.

    - Instructions: Contractor shall provide qualified, factory-trained manufacturers' representatives to give detailed training to assigned Department of Veterans Affairs personnel in the operation and complete maintenance for each piece of equipment. All such training will be at the job site. These requirements are more specifically detailed in the various technical sections. Instructions for different items of equipment that are component parts of a complete system, shall be given in an integrated, progressive manner. All instructors for every piece of component equipment in a system shall be available until instructions for all items included in the system have been completed. This is to assure proper instruction in the operation of inter-related systems. All instruction periods shall be at such times as scheduled by the COR and shall be considered concluded only when the COR is satisfied in regard to complete and thorough coverage. The contractor shall submit a course outline with associated material to the COR for review and approval prior to scheduling training to ensure the subject matter covers the expectations of the VA and the contractual requirements. The Department of Veterans Affairs reserves the right to request the removal of, and substitution for, any instructor who, in the opinion of the COR, does not demonstrate sufficient qualifications in accordance with requirements for instructors above.

  - GOVERNMENT-FURNISHED PROPERTY

    - The Government shall deliver to the Contractor, the

Government-furnished property shown on the Schedule // drawings //.

    - Equipment furnished by Government to be installed by Contractor will be furnished to Contractor at the Medical Center.

    - //Contractor shall be prepared to receive this equipment from Government and store or place such equipment not less than 90 days before Completion Date of project. //

      - //*Storage space for equipment will be provided by the Government and the Contractor shall be prepared to unload and store such equipment therein upon its receipt at the // Medical Center.

    - Notify Contracting Officer in writing, 60 days in advance, of date on which Contractor will be prepared to receive equipment furnished by Government. Arrangements will then be made by the Government for delivery of equipment.

      - Immediately upon delivery of equipment, Contractor shall arrange for a joint inspection thereof with a representative of the Government. At such time the Contractor shall acknowledge receipt of equipment described, make notations, and immediately furnish the Government representative with a written statement as to its condition or shortages.

      - Contractor thereafter is responsible for such equipment until such time as acceptance of contract work is made by the Government.

    - Equipment furnished by the Government will be delivered in a partially assembled (knock down) condition in accordance with existing standard commercial practices, complete with all fittings, fastenings, and appliances necessary for connections to respective services installed under contract. All fittings and appliances (i.e., couplings, ells, tees, nipples, piping, conduits, cables, and the like) necessary to make the connection between the Government furnished equipment item and the utility stub-up shall be furnished and installed by the contractor at no additional cost to the Government.

    - Completely assemble and install the Government furnished equipment in place ready for proper operation in accordance with specifications and drawings.

    - Furnish supervision of installation of equipment at construction site by qualified factory trained technicians regularly employed by the equipment manufacturer.

  - RELOCATED EQUIPMENT AND ITEMS

    - Contractor shall disconnect, dismantle as necessary, remove and reinstall in new location, all existing equipment and items indicated by symbol "R" or otherwise shown to be relocated by the Contractor.

    - Perform relocation of such equipment or items at such times and in such a manner as directed by the COR.

    - Suitably cap existing service lines, such as steam, condensate return, water, drain, gas, air, vacuum and/or electrical, at the main whenever

such lines are disconnected from equipment to be relocated. Remove abandoned lines in finished areas and cap as specified herein before under paragraph "Abandoned Lines".

    - Provide all mechanical and electrical service connections, fittings, fastenings and any other materials necessary for assembly and installation of relocated equipment; and leave such equipment in proper operating condition.

    - Contractor shall employ services of an installation engineer, who is an authorized representative of the manufacturer of this equipment to supervise assembly and installation of existing equipment, required to be relocated. //

    - All service lines such as noted above for relocated equipment shall be in place at point of relocation ready for use before any existing equipment is disconnected. Make relocated existing equipment ready for operation or use immediately after reinstallation.

  - CONSTRUCTION SIGN

    - Provide a Construction Sign where directed by the COR. All wood members shall be of framing lumber. Cover sign frame with 0.7 mm (24 gage) galvanized sheet steel nailed securely around edges and on all bearings. Provide three 100 by 100 mm (4 inch by 4 inch) posts (or equivalent round posts) set 1200 mm (four feet) into ground. Set bottom of sign level at 900 mm (three feet) above ground and secure to posts with through bolts. Make posts full height of sign. Brace posts with 50 x 100 mm (two by four inch) material as directed.

    - Paint all surfaces of sign and posts two coats of white gloss paint. Border and letters shall be of black gloss paint, except project title which shall be blue gloss paint.

    - Maintain sign and remove it when directed by the COR.

  - SAFETY SIGN

    - Provide a Safety Sign where directed by COR. Face of sign shall be 19 mm (3/4 inch) thick exterior grade plywood. Provide two 100 mm by 100 mm (four by four inch) posts extending full height of sign and 900 mm (three feet) into ground. Set bottom of sign level at 1200 mm (four feet) above ground.

    - Paint all surfaces of Safety Sign and posts with one prime coat and two coats of white gloss paint. Letters and design shall be painted with gloss paint of colors noted.

    - Maintain sign and remove it when directed by COR.

    - Drawing details in VA Signage Design Manual, Section 11 Specialty Signs (found on VA TIL) show required legend and other characteristics of sign and are attached hereto and is made a part of this specification.

    - Post the number of accident free days on a daily basis.

| Number of photographs |  |
| --- | --- |
| Estimated Cost | No. of Photographs |
| Up to $5,000,000 | 250 to 300 |

  - PHOTOGRAPHIC DOCUMENTATION

    - During the construction period through completion, provide photographic documentation of construction progress and at selected milestones including electronic indexing, navigation, storage and remote access to the documentation, as per these specifications. The commercial photographer or the subcontractor used for this work shall meet the following qualifications:

      - Demonstrable minimum experience of three (3) years in operation providing documentation and advanced indexing/navigation systems including a representative portfolio of construction projects of similar type, size, duration and complexity as the Project.

      - Demonstrable ability to service projects throughout North America, which shall be demonstrated by a representative portfolio of active projects of similar type, size, duration and complexity as the Project.

    - Photographic documentation elements:

      - Each digital image shall be taken with a professional grade camera with minimum size of 6 megapixels (MP) capable of producing 200x250mm (8 x 10 inch) prints with a minimum of 2272 x 1704 pixels and 400x500mm (16 x 20 inch) prints with a minimum 2592 x 1944 pixels.

      - Indexing and navigation system shall utilize actual AUTOCAD construction drawings, making such drawings interactive on an on- line interface. For all documentation referenced herein, indexing and navigation must be organized by both time (date-stamped) and location throughout the project.

      - Documentation shall combine indexing and navigation system with inspection-grade digital photography designed to capture actual conditions throughout construction and at critical milestones. Documentation shall be accessible on-line through use of an internet connection. Documentation shall allow for secure multiple-user access, simultaneously, on-line.

      - Before construction, the building pad, adjacent streets, roadways, parkways, driveways, curbs, sidewalks, landscaping, adjacent utilities and adjacent structures surrounding the building pad and site shall be documented. Overlapping photographic techniques shall be used to ensure maximum coverage. Indexing and navigation accomplished through interactive architectural drawings. If site work or pad preparation is extensive, this documentation may be required immediately before construction and at several pre- determined intervals before building work commences.

      - Construction progress for all trades shall be tracked at pre- determined intervals, but not less than once every thirty (30) calendar days (“Progressions”). Progression documentation shall track both the exterior and interior construction of the building. Exterior Progressions shall track 360 degrees around the site and each building. Interior Progressions shall track interior improvements beginning when stud work commences and continuing until Project completion.

      - As-built condition of pre-foundation utilities and site utilities shall be documented prior to pouring footers, placing concrete and/or backfilling. This process shall include all underground and in-slab utilities within the building(s) envelope(s) and utility runs in the immediate vicinity of the building(s) envelope(s). This may also include utilities enclosed in slab-on-deck in multi-story buildings. Overlapping photographic techniques shall be used to

ensure maximum coverage. Indexing and navigation accomplished through interactive site utility plans.

      - As-built conditions of mechanical, electrical, plumbing and all other systems shall be documented post-inspection and pre- insulation, sheet rock or dry wall installation. This process shall include all finished systems located in the walls and ceilings of all buildings at the Project. Overlapping photographic techniques shall be used to ensure maximum coverage. Indexing and navigation accomplished through interactive architectural drawings.

      - As-built finished conditions of the interior of each building including floors, ceilings and walls shall be documented at certificate of occupancy or equivalent, or just prior to occupancy, or both, as directed by the COR. Overlapping photographic techniques shall be used to ensure maximum coverage. Indexing and navigation accomplished through interactive architectural drawings.

      - Miscellaneous events that occur during any Contractor site visit, or events captured by the Department of Veterans Affairs independently, shall be dated, labeled and inserted into a Section in the navigation structure entitled “Slideshows,” allowing this information to be stored in the same “place” as the formal scope.

      - Customizable project-specific digital photographic documentation of other details or milestones. Indexing and navigation accomplished through interactive architectural plans.

      - Weekly (21 Max) Site Progressions - Photographic documentation capturing the project at different stages of construction. These progressions shall capture underground utilities, excavation, grading, backfill, landscaping and road construction throughout the duration of the project, as well as any TR Room documentation and camera installations.

      - Regular (8 max) interior progressions of all walls of the entire project to begin at time of substantial framed or as directed by the COR through to completion.

      - Detailed Exact-Built of all Slab repairs for all project slab pours just prior to placing concrete or as directed by the COR.

      - Detailed Interior exact built overlapping photos of the entire building to include documentation of all mechanical, electrical and

plumbing systems in every wall and ceiling, to be conducted after rough-ins are complete, just prior to insulation and or drywall, or as directed by COR.

      - Finished detailed Interior exact built overlapping photos of all walls, ceilings, and floors to be scheduled by COR prior to occupancy.

      - In event a greater or lesser number of images than specified above are required by the COR, adjustment in contract price will be made in accordance with clause entitled "CHANGES" (FAR 52.243-4).

    - Images shall be taken by a commercial photographer and must show distinctly, at as large a scale as possible, all parts of work embraced in the picture.

    - Coordination of photo shoots is accomplished through COR. Contractor shall also attend construction team meetings as necessary. Contractor’s operations team shall provide regular updates regarding the status of the documentation, including photo shoots concluded, the availability of new Progressions or Exact-Builts viewable on-line and anticipated future shoot dates.

    - Contractor shall provide all on-line domain/web hosting, security measures, and redundant server back-up of the documentation.

    - Contractor shall provide technical support related to using the system or service.

    - Upon completion of the project, final copies of the documentation (the “Permanent Record”) with the indexing and navigation system embedded (and active) shall be provided in an electronic media format, typically a DVD or external hard-drive. Permanent Record shall have Building Information Modeling (BIM) interface capabilities. On-line access terminates upon delivery of the Permanent Record.

- - - E N D - - -

Richmond, VA	Issued For Bids: 10/17/25

011000 SUMMARY OF WORK

PART 1 GENERAL

  - PROJECT

    - Project Name: CAMPUS WIDE CAMERA REPLACEMENT

    - Owner's Name: Veteran Administration Medical Center, Richmond

      - 1201 Broad Rock Boulevard, Richmond VA 23249-4915

    - Architect's Name: Logos BZ, LLC 6405 Sweetwater Meadow Court Laytonsville, MD 20882

    - The Project consists of the construction of new VA cameras and the replacement of TR room racks to patch panels, tested and licensed.

  - CONTRACT DESCRIPTION

    - Contract Type: A single prime contract based on a Fixed Price.

See SECTION STATEMENT OF WORK FOR ELECTRONIC SAFETY AND SECURITY INSTALLATIONS

for additional information on summary of required.

  - OWNER OCCUPANCY

    - VA intends to occupy the Project Site. Work will be done in a manner related to the ICRA drawings.

    - Cooperate with VA to minimize conflict and to facilitate VA Facility Operations.

    - Schedule the Work to accommodate Owner occupancy.

  - CONTRACTOR USE OF SITE AND PREMISES

    - Construction Operations: Limited to areas noted on Drawings.

    - Provide access to and from the site as required by law and by the Owner:

      - Emergency Building Exits During Construction: Keep all exits required by code open during the construction period; provide temporary exit signs if exit routes are temporarily altered.

      - Do not obstruct roadways, sidewalks, or other public ways without a permit.

    - Contractor to utilize control cubes in areas requiring work.

  - WORK SEQUENCE

    - Construct Work in stages during the construction period:

      - Stage 1: Building 500: Interior cameras in After-hours work zones and immediate camera replacement areas first, then the remainder of the building phases/ ICRA Phases.

      - Stage 2: Site Surveys of existing underground routes, site cameras (and as necessary, trenching), specifically for cameras on light poles associated with building 500 TR rooms: Grading and Site Underground.

      - Stage 3: Remainder of Outbuilding cameras.

PART 2 PRODUCTS - NOT USED PART 3 EXECUTION - NOT USED

END OF SECTION

SECTION 012200 UNIT PRICES

PART 1 - GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 01 Specification Sections, apply to this Section.

  - SUMMARY

    - Section includes administrative and procedural requirements for unit prices.

  - DEFINITIONS

    - Unit price is an amount incorporated in the Agreement, applicable during the duration of the Work as a price per unit of measurement for materials, equipment, or services, or a portion of the Work, added to or deducted from the Contract Sum by appropriate modification, if the scope of Work or estimated quantities of Work required by the Contract Documents are increased or decreased.

  - PROCEDURES

    - Unit prices include all necessary material, cost for delivery, installation, insurance, overhead, and profit.

    - Measurement and Payment: Refer to individual Specification Sections

for work that requires establishment of unit prices. Methods of measurement and payment for unit prices are specified in those Sections.

    - Owner reserves the right to reject Contractor's measurement of work- in-place that involves use of established unit prices and to have this work measured, at Owner's expense, by an independent surveyor acceptable to Contractor.

    - List of Unit Prices: A schedule of unit prices is included in Part 3. Specification Sections referenced in the schedule contain requirements for materials described under each unit price.

PART 2 - PRODUCTS (Not Used) PART 3 - EXECUTION

  - SCHEDULE OF UNIT PRICES

    - Unit Price No. 1 " J-Hook Credits". Insert unit price item:

      - Description:	Insert unit-price credit according to drawings and specifications to utilize existing cable trays, j-hooks or ladders in lieu of installing (labor and materials) J-Hooks above ceilings in areas requiring installation in a control cube per ICRA guidelines as indicated in building 500.

      - Unit of Measurement: per 100 linear feet above acoustic tile.

    - Unit Price No. 2 "Rigid Conduit Credits" Insert unit price item:

      - Description:	Insert unit-price credit according to drawings and specifications to utilize existing rigid conduit in lieu of installing (labor and materials) rigid conduit above drywall ceilings in areas requiring installation and including cutting and patching.

      - Unit of Measurement: per 10 linear feet in open ceiling.

    - Unit Price No.3 “Asphalt cutting and patching and pathways” Insert unit price item:

      - Description:	Provide Underground utility to a TR room through the site under existing asphalt requiring cutting and patching. Include 2” conduit - pvc schedule 40 and rigid steel (rgs) for 90- degree turn-ups out of the asphalt conductors (power and low- voltage communications), as required on drawings, as indicated in the base bid. Include Pull strings and spare capacity per specifications. Include Handholes, pull boxes, fittings, and required accessories. Include protection/ detection tape per VA master specifications excavation, bedding, backfill, compaction, and surface restoration including asphalt repair per VA master specifications. Repair of street and paving markings per specifications.

      - Unit of Measurement: cost per 10 linear feet.

    - Unit Price No.4 “Concrete cutting and patching and pathways” Insert unit price item:

      - Description: Provide Underground utility to a TR room through the site under existing concrete, requiring cutting and patching. Include 2” conduit - PVC schedule 40 and rigid steel (rgs) for 90- degree turn-ups out of the concrete conductors (power and low- voltage communications) as required on drawings as indicated in the base bid. Include pull strings and spare capacity per specifications. Include Handholes, pull boxes, fittings, and required accessories. Include protection/ detection tape per VA master specifications excavation, bedding, backfill, compaction, and surface restoration, including concrete repair per va master specifications. Include repair of street and paving markings per specifications.

      - Unit of Measurement: cost per 10 linear feet.

    - Unit Price No.5 “Planting cutting and patching and pathways” Insert unit price item:

      - Description:	Provide Underground utility to a TR room through the site under existing plantings, requiring cutting and patching. Include 2” conduit - PVC schedule 40 and rigid steel (rgs) for 90- degree turn-ups out of the asphalt conductors (power and low- voltage communications) as indicated in the base bid. Include Pull strings and spare capacity per specifications. Handholes, pull boxes, fittings, and required accessories. Include protection/ detection tape per VA master specifications excavation, bedding, backfill, compaction, and surface restoration, including asphalt repair per va master specifications. Include repair of planting per specifications.

      - Unit of Measurement: cost per 10 linear feet.

    - Unit Price No.6 “Cabling” Insert unit price item:

      - Contractor shall provide a per unit cost inclusive of one hundred and fifty (150) linear feet of unshielded twisted pair (TUP) Category 6a plenum rated cabling terminated onto Cat 6a patch panel in the nearest/designated TR room and terminated onto RJ-45 jack installed within a surface mounted 1-port box (biscuit); cable shall be tested and labeled

      - Unit of Measurement: cost per 150 linear feet.

    - Unit Price No.6 “Cameras” Insert unit price item:

      - Contractor shall provide a per unit cost for each type of camera specified on this project; per unit cost shall include camera license, programming, installation and associated mounting bracket to suit condition.

      - Unit of Measurement: cost per camera type installed.

END OF SECTION

### SECTION 01 32 16.15 PROJECT SCHEDULES

#### (SMALL PROJECTS – DESIGN/BID/BUILD)

### PART 1- GENERAL

  - DESCRIPTION:

    - The Contractor shall develop a Critical Path Method (CPM) plan and schedule demonstrating fulfillment of the contract requirements (Project Schedule), and shall keep the Project Schedule up-to-date in accordance with the requirements of this section and shall utilize the plan for scheduling, coordinating and monitoring work under this contract (including all activities of subcontractors, equipment vendors and suppliers). Conventional Critical Path Method (CPM) technique shall be utilized to satisfy both time and cost applications.

  - CONTRACTOR'S REPRESENTATIVE:

    - The Contractor shall designate an authorized representative responsible for the Project Schedule including preparation, review and progress reporting with and to the Contracting Officer's Representative (COR).

    - The Contractor's representative shall have direct project control and complete authority to act on behalf of the Contractor in fulfilling the requirements of this specification section.

    - The Contractor’s representative shall have the option of developing the project schedule within their organization or to engage the services of an outside consultant. If an outside scheduling consultant is utilized, Section 1.3 of this specification will apply.

  - CONTRACTOR'S CONSULTANT:

    - The Contractor shall submit a qualification proposal to the COR, within

10 days of bid acceptance. The qualification proposal shall include:

- The name and address of the proposed consultant.

- Information to show that the proposed consultant has the qualifications to meet the requirements specified in the preceding paragraph.

- A representative sample of prior construction projects, which the proposed consultant has performed complete project scheduling services. These representative samples shall be of similar size and scope.

    - The Contracting Officer has the right to approve or disapprove the proposed consultant, and will notify the Contractor of the VA decision within seven calendar days from receipt of the qualification proposal. In case of disapproval, the Contractor shall resubmit another consultant within 10 calendar days for renewed consideration. The Contractor shall have their scheduling consultant approved prior to submitting any schedule for approval.

  - COMPUTER PRODUCED SCHEDULES

    - The contractor shall provide monthly, to the Department of Veterans Affairs (VA), all computer-produced time/cost schedules and reports generated from monthly project updates. This monthly computer service will include: three copies of up to five different reports (inclusive of all pages) available within the user defined reports of the scheduling software approved by the Contracting Officer; a hard copy listing of all project schedule changes, and associated data, made at the update and an electronic file of this data; and the resulting monthly updated schedule in PDM format. These must be submitted with and substantively support the contractor’s monthly payment request and the signed look ahead report. The COR shall identify the five different report formats that the contractor shall provide.

    - The contractor shall be responsible for the correctness and timeliness of the computer-produced reports. The Contractor shall also responsible for the accurate and timely submittal of the updated project schedule and all CPM data necessary to produce the computer reports and payment request that is specified.

    - The VA will report errors in computer-produced reports to the Contractor’s representative within ten calendar days from receipt of reports. The Contractor shall reprocess the computer-produced reports and associated diskette(s), when requested by the Contracting Officer’s representative, to correct errors which affect the payment and schedule for the project.

  - THE COMPLETE PROJECT SCHEDULE SUBMITTAL

    - Within 45 calendar days after receipt of Notice to Proceed, the Contractor shall submit for the Contracting Officer's review; three blue line copies of the interim schedule on sheets of paper 765 x 1070 mm (30 x 42 inches) and an electronic file in the previously approved

CPM schedule program. The submittal shall also include three copies of a computer-produced activity/event ID schedule showing project duration; phase completion dates; and other data, including event cost. Each activity/event on the computer-produced schedule shall contain as a minimum, but not limited to, activity/event ID, activity/event description, duration, budget amount, early start date, early finish date, late start date, late finish date and total float. Work activity/event relationships shall be restricted to finish-to-start or start-to-start without lead or lag constraints. Activity/event date constraints, not required by the contract, will not be accepted unless submitted to and approved by the Contracting Officer. The contractor shall make a separate written detailed request to the Contracting Officer identifying these date constraints and secure the Contracting Officer’s written approval before incorporating them into the network diagram. The Contracting Officer’s separate approval of the Project Schedule shall not excuse the contractor of this requirement. Logic events (non-work) will be permitted where necessary to reflect proper logic among work events, but must have zero duration. The complete working schedule shall reflect the Contractor's approach to scheduling the complete project. The final Project Schedule in its original form shall contain no contract changes or delays which may have been incurred during the final network diagram development period and shall reflect the entire contract duration as defined in the bid documents.

These changes/delays shall be entered at the first update after the final Project Schedule has been approved. The Contractor should provide their requests for time and supporting time extension analysis for contract time as a result of contract changes/delays, after this update, and in accordance with Article, ADJUSTMENT OF CONTRACT COMPLETION.

    - Within 30 calendar days after receipt of the complete project interim Project Schedule and the complete final Project Schedule, the Contracting Officer or his representative, will do one or both of the following:

      - Notify the Contractor concerning his actions, opinions, and objections.

      - A meeting with the Contractor at or near the job site for joint review, correction or adjustment of the proposed plan will be scheduled if required. Within 14 calendar days after the joint review, the Contractor shall revise and shall submit three blue line copies of the revised Project Schedule, three copies of the revised computer-produced activity/event ID schedule and a revised electronic file as specified by the Contracting Officer. The revised submission will be reviewed by the Contracting Officer and, if found to be as previously agreed upon, will be approved.

    - The approved baseline schedule and the computer-produced schedule(s) generated there from shall constitute the approved baseline schedule until subsequently revised in accordance with the requirements of this section.

    - The Complete Project Schedule shall contain approximately work activities/events.

  - WORK ACTIVITY/EVENT COST DATA

    - The Contractor shall cost load all work activities/events except procurement activities. The cumulative amount of all cost loaded work activities/events (including alternates) shall equal the total contract price. Prorate overhead, profit and general conditions on all work activities/events for the entire project length. Activity-Based Costing (ABC) or Strategic Acquisition Guidance (SAG) methodologies may be used to justify these allocations. The contractor shall generate from this information cash flow curves indicating graphically the total percentage of work activity/event dollar value scheduled to be in place on early finish, late finish. These cash flow curves will be used by the Contracting Officer to assist him in determining approval or disapproval of the cost loading. Negative work activity/event cost data will not be acceptable, except on VA issued contract changes.

    - The Contractor shall cost load work activities/events for guarantee period services, test, balance and adjust various systems in accordance with the provisions VAAR 852.232 – Article 70 Without NAS-CPM for (PAYMENTS UNDER FIXED PRICE CONSTRUCTION).

    - The Contractor shall provide a responsibility code for all activities to identify the entity performing the work, ensuring clear accountability for project execution.

    - The Contractor shall cost load work activities/events for all BID ITEMS including ASBESTOS ABATEMENT. The sum of each BID ITEM work shall equal the value of the bid item in the Contractors' bid.

  - PROJECT SCHEDULE REQUIREMENTS

    - Show on the project schedule the sequence of work activities/events required for complete performance of all items of work. The Contractor Shall:

      - Show activities/events as:

        - Contractor's time required for submittal of shop drawings, templates, fabrication, delivery and similar pre-construction work.

        - Contracting Officer's and Architect-Engineer's review and approval of shop drawings, equipment schedules, samples, template, or similar items.

        - Interruption of VA Facilities utilities, delivery of Government furnished equipment, and rough-in drawings, project phasing and any other specification requirements.

        - Test, balance and adjust various systems and pieces of equipment, maintenance and operation manuals, instructions and preventive maintenance tasks.

        - VA inspection and acceptance activity/event with a minimum duration of five work days at the end of each phase and immediately preceding any VA move activity/event required by the contract phasing for that phase.

      - Show not only the activities/events for actual construction work for each trade category of the project, but also trade relationships to indicate the movement of trades from one area, floor, or building, to another area, floor, or building, for at least five trades who are performing major work under this contract.

      - Break up the work into activities/events of a duration no longer than 20 work days each or one reporting period, except as to

non-construction activities/events (i.e., procurement of materials, delivery of equipment, concrete and asphalt curing) and any other activities/events for which the COR may approve the showing of a

longer duration. The duration for VA approval of any required submittal, shop drawing, or other submittals will not be less than

20 work days.

      - Describe work activities/events clearly, so the work is readily identifiable for assessment of completion. Activities/events labeled "start," "continue," or "completion," are not specific and will not be allowed. Lead and lag time activities will not be acceptable.

      - The schedule shall be generally numbered in such a way to reflect either discipline, phase or location of the work.

    - The Contractor shall submit the following supporting data in addition to the project schedule:

      - The appropriate project calendar including working days and holidays.

      - The planned number of shifts per day.

      - The number of hours per shift.

Failure of the Contractor to include this data shall delay the review of the submittal until the Contracting Officer is in receipt of the missing data.

    - To the extent that the Project Schedule or any revised Project Schedule shows anything not jointly agreed upon, it shall not be deemed to have been approved by the COR. Failure to include any element of work required for the performance of this contract shall not excuse the Contractor from completing all work required within any applicable completion date of each phase regardless of the COR’s approval of the Project Schedule.

    - Compact Disk Requirements and CPM Activity/Event Record Specifications: Submit to the VA an electronic file(s) containing one file of the data required to produce a schedule, reflecting all the activities/events of the complete project schedule being submitted.

  - PAYMENT TO THE CONTRACTOR:

    - Monthly, the contractor shall submit an application and certificate for payment using the AIA application and certificate for payment documents G702 & G703 reflecting updated schedule activities and cost data in accordance with the provisions of the following Article, PAYMENT AND PROGRESS REPORTING, as the basis upon which progress payments will be made pursuant to Article, FAR 52.232 – 5 (PAYMENT UNDER FIXED-PRICE

CONSTRUCTION CONTRACTS) and VAAR 852.232 – Article 70 Without NAS-CPM

for (PAYMENTS UNDER FIXED PRICE CONSTRUCTION). The Contractor shall be entitled to a monthly progress payment upon approval of estimates as determined from the currently approved updated project schedule.

Monthly payment requests shall include: a listing of all agreed upon project schedule changes and associated data; and an electronic file

(s) of the resulting monthly updated schedule.

    - Approval of the Contractor’s monthly Application for Payment shall be contingent, among other factors, on the submittal of a satisfactory monthly update of the project schedule.

  - PAYMENT AND PROGRESS REPORTING

    - Monthly schedule update meetings will be held on dates mutually agreed to by the COR and the Contractor. Contractor and their CPM consultant (if applicable) shall attend all monthly schedule update meetings. The Contractor shall accurately update the Project Schedule and all other data required and provide this information to the COR three work days in advance of the schedule update meeting. Job progress will be reviewed to verify:

      - Actual start and/or finish dates for updated/completed activities/events.

      - Remaining duration for each activity/event started, or scheduled to start, but not completed.

      - Logic, time and cost data for change orders, and supplemental agreements that are to be incorporated into the Project Schedule.

      - Changes in activity/event sequence and/or duration which have been made, pursuant to the provisions of following Article, ADJUSTMENT OF CONTRACT COMPLETION.

      - Completion percentage for all completed and partially completed activities/events.

      - Logic and duration revisions required by this section of the specifications.

      - Activity/event duration and percent complete shall be updated independently.

    - After completion of the joint review, the contractor shall generate an updated computer-produced calendar-dated schedule and supply the

Contracting Officer’s representative with reports in accordance with the Article, COMPUTER PRODUCED SCHEDULES, specified.

    - After completing the monthly schedule update, the contractor’s representative or scheduling consultant shall rerun all current period contract change(s) against the prior approved monthly project schedule. The analysis shall only include original workday durations and schedule logic agreed upon by the contractor and COR for the contract change(s). When there is a disagreement on logic and/or durations, the Contractor shall use the schedule logic and/or durations provided and approved by the COR. After each rerun update, the resulting electronic project schedule data file shall be appropriately identified and submitted to the VA in accordance to the requirements listed in articles 1.4 and

1.7. This electronic submission is separate from the regular monthly project schedule update requirements and shall be submitted to the COR within fourteen (14) calendar days of completing the regular schedule update. Before inserting the contract changes durations, care must be taken to ensure that only the original durations will be used for the analysis, not the reported durations after progress. In addition, once the final network diagram is approved, the contractor must recreate all manual progress payment updates on this approved network diagram and associated reruns for contract changes in each of these update periods as outlined above for regular update periods. This will require detailed record keeping for each of the manual progress payment updates.

    - Following approval of the CPM schedule, the VA, the General Contractor, its approved CPM Consultant, RE office representatives, and all subcontractors needed, as determined by the SRE, shall meet to discuss the monthly updated schedule. The main emphasis shall be to address work activities to avoid slippage of project schedule and to identify any necessary actions required to maintain project schedule during the reporting period. The Government representatives and the Contractor should conclude the meeting with a clear understanding of those work and administrative actions necessary to maintain project schedule status during the reporting period. This schedule coordination meeting will occur after each monthly project schedule update meeting utilizing the resulting schedule reports from that schedule update. If the

project is behind schedule, discussions should include ways to prevent further slippage as well as ways to improve the project schedule status, when appropriate.

  - RESPONSIBILITY FOR COMPLETION

    - If it becomes apparent from the current revised monthly progress schedule that phasing or contract completion dates will not be met, the Contractor shall execute some or all of the following remedial actions:

      - Increase construction manpower in such quantities and crafts as necessary to eliminate the backlog of work.

      - Increase the number of working hours per shift, shifts per working day, working days per week, the amount of construction equipment, or any combination of the foregoing to eliminate the backlog of work.

      - Reschedule the work in conformance with the specification requirements.

    - Prior to proceeding with any of the above actions, the Contractor shall notify and obtain approval from the COR for the proposed schedule changes. If such actions are approved, the representative schedule revisions shall be incorporated by the Contractor into the Project Schedule before the next update, at no additional cost to the Government.

  - CHANGES TO THE SCHEDULE

    - Within 30 calendar days after VA acceptance and approval of any updated project schedule, the Contractor shall submit a revised electronic file

(s) and a list of any activity/event changes including predecessors and successors for any of the following reasons:

- Delay in completion of any activity/event or group of activities/events, which may be involved with contract changes, strikes, unusual weather, and other delays will not relieve the Contractor from the requirements specified unless the conditions are shown on the CPM as the direct cause for delaying the project beyond the acceptable limits.

- Delays in submittals, or deliveries, or work stoppage are encountered which make rescheduling of the work necessary.

- The schedule does not represent the actual prosecution and progress of the project.

- When there is, or has been, a substantial revision to the activity/event costs regardless of the cause for these revisions.

    - CPM revisions made under this paragraph which affect the previously approved computer-produced schedules for Government furnished equipment, vacating of areas by the VA Facility, contract phase(s) and sub phase(s), utilities furnished by the Government to the Contractor, or any other previously contracted item, shall be furnished in writing to the Contracting Officer for approval.

    - Contracting Officer's approval for the revised project schedule and all relevant data is contingent upon compliance with all other paragraphs of this section and any other previous agreements by the Contracting Officer or the VA representative.

    - The cost of revisions to the project schedule resulting from contract changes will be included in the proposal for changes in work as specified in FAR 52.243 – 4 (Changes, and will be based on the complexity of the revision or contract change, man hours expended in analyzing the change, and the total cost of the change.

    - The cost of revisions to the Project Schedule not resulting from contract changes is the responsibility of the Contractor.

  - ADJUSTMENT OF CONTRACT COMPLETION

    - The contract completion time will be adjusted only for causes specified in this contract. Request for an extension of the contract completion date by the Contractor shall be supported with a justification, CPM data and supporting evidence as the COR may deem necessary for determination as to whether or not the Contractor is entitled to an extension of time under the provisions of the contract. Submission of proof based on revised activity/event logic, durations (in work days) and costs is obligatory to any approvals. The schedule must clearly display that the Contractor has used, in full, all the float time available for the work involved in this request. The Contracting Officer's determination as to the total number of days of contract extension will be based upon the current computer-produced

calendar-dated schedule for the time period in question and all other relevant information.

    - Actual delays in activities/events which, according to the computer- produced calendar-dated schedule, do not affect the extended

and predicted contract completion dates shown by the critical path in the network, will not be the basis for a change to the contract completion date. The Contracting Officer will within a reasonable time after receipt of such justification and supporting evidence, review the facts and advise the Contractor in writing of the Contracting Officer's decision.

    - The Contractor shall submit each request for a change in the contract completion date to the Contracting Officer in accordance with the provisions specified under FAR 52.243 – 4 (Changes). The Contractor shall include, as a part of each change order proposal, a sketch showing all CPM logic revisions, duration (in work days) changes, and cost changes, for work in question and its relationship to other activities on the approved network diagram.

    - All delays due to non-work activities/events such as RFI’s, WEATHER, STRIKES, and similar non-work activities/events shall be analyzed on a month by month basis.

- - - E N D - - -

SECTION 01 33 23

SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES

PART 1 – GENERAL

  - DESCRIPTION

    - This specification defines the general requirements and procedures for submittals. A submittal is information submitted for VA review to establish compliance with the contract documents.

    - Detailed submittal requirements are found in the technical sections of the contract specifications. The Contracting Officer may request submittals in addition to those specified when deemed necessary to adequately describe the work covered in the respective technical specifications at no additional cost to the government.

    - VA approval of a submittal does not relieve the Contractor of the responsibility for any error which may exist. The Contractor is responsible for fully complying with all contract requirements and the satisfactory construction of all work, including the need to check, confirm, and coordinate the work of all subcontractors for the project. Non-compliant material incorporated in the work will be removed and replaced at the Contractor’s expense.

  - DEFINITIONS

    - Preconstruction Submittals: Submittals which are required prior to issuing contract notice to proceed or starting construction. For example, Certificates of insurance; Surety bonds; Site-specific safety plan; Construction progress schedule; Schedule of values; Submittal register; List of proposed subcontractors.

    - Shop Drawings: Drawings, diagrams, and schedules specifically prepared to illustrate some portion of the work. Drawings prepared by or for the Contractor to show how multiple systems and interdisciplinary work will be integrated and coordinated.

    - Product Data: Catalog cuts, illustrations, schedules, diagrams, performance charts, instructions, and brochures, which describe and illustrate size, physical appearance, and other characteristics of materials, systems, or equipment for some portion of the work. Samples of warranty language when the contract requires extended product warranties.

    - Samples: Physical examples of materials, equipment, or workmanship that illustrate functional and aesthetic characteristics of a material or product and establish standards by which the work can be judged. Color samples from the manufacturer's standard line (or custom color samples if specified) to be used in selecting or approving colors for the project. Field samples and mock-ups constructed to establish standards by which the ensuing work can be judged.

    - Design Data: Calculations, mix designs, analyses, or other data pertaining to a part of work.

    - Test Reports: Report which includes findings of a test required to be performed by the Contractor on an actual portion of the work. Report which includes finding of a test made at the job site or on sample taken from the job site, on portion of work during or after installation.

    - Certificates: Document required of Contractor, or of a manufacturer, supplier, installer, or subcontractor through Contractor. The purpose is to document procedures, acceptability of methods, or personnel qualifications for a portion of the work.

    - Manufacturer's Instructions: Pre-printed material describing installation of a product, system, or material, including special notices and MSDS concerning impedances, hazards, and safety precautions.

    - Manufacturer's Field Reports: Documentation of the testing and verification actions taken by manufacturer's representative at the job site on a portion of the work, during or after installation, to confirm compliance with manufacturer's standards or instructions. The documentation must indicate whether the material, product, or system has passed or failed the test.

    - Operation and Maintenance Data: Manufacturer data that is required to operate, maintain, troubleshoot, and repair equipment, including manufacturer's help, parts list, and product line documentation. This data shall be incorporated in an operations and maintenance manual.

    - Closeout Submittals: Documentation necessary to properly close out a construction contract. For example, Record Drawings and as-built drawings. Also, submittal requirements necessary to properly close out a phase of construction on a multi-phase contract.

  - SUBMITTAL REGISTER

    - The submittal register will list items of equipment and materials for which he contract documents but which have been omitted from the submittal register.

    - The submittal register will serve as a scheduling document for submittals and will be used to control submittal actions throughout the contract period.

    - The VA will provide a blank submittal register in electronic format. Thereafter, the Contractor shall fill in the blank register with the required submittals as documented in the project spec. The Contractor shall track all submittals by maintaining a complete list, including completion of all data columns, including dates on which submittals are received and returned by the VA.

    - Blank digital register provided for Contractor use below

ENG_FORM_4288-R.

pdf

D. The Contractor shall update the submittal register as submittal actions occur and maintain the submittal register at the project site until final acceptance of all work by Contracting Officer.

E. The Contractor shall submit formal monthly updates to the submittal register in electronic format. Each monthly update shall document actual submission and approval dates for each submittal.

  - SUBMITTAL SCHEDULING

    - Submittals are to be scheduled, submitted, reviewed, and approved prior to the acquisition of the material or equipment.

    - Coordinate scheduling, sequencing, preparing, and processing of submittals with performance of work so that work will not be delayed by submittal processing. Allow time for potential resubmittal.

    - No delay costs or time extensions will be allowed for time lost in late submittals or resubmittals.

    - All submittals are required to be approved prior to the start of the specified work activity.

  - SUBMITTAL PREPARATION

    - Each submittal is to be complete and in sufficient detail to allow ready determination of compliance with contract requirements.

    - Collect required data for each specific material, product, unit of work, or system into a single submittal. Prominently mark choices, options, and portions applicable to the submittal. Partial submittals will not be accepted for expedition of construction effort. Submittal will be returned without review if incomplete.

    - If available product data is incomplete, provide Contractor-prepared documentation to supplement product data and satisfy submittal requirements.

    - All irrelevant or unnecessary data shall be removed from the submittal to facilitate accuracy and timely processing. Submittals that contain the excessive amount of irrelevant or unnecessary data will be returned without review.

    - Provide a transmittal form for each submittal with the following information:

      - Project title, location and number.

      - Construction contract number.

      - Date of the drawings and revisions.

      - Name, address, and telephone number of subcontractor, supplier, manufacturer, and any other subcontractor associated with the submittal.

      - List paragraph number of the specification section and sheet number of the contract drawings by which the submittal is required.

      - When a resubmission, add alphabetic suffix on submittal description. For example, submittal 18 would become 18A, to indicate resubmission.

      - Product identification and location in project.

    - The Contractor is responsible for reviewing and certifying that all submittals are in compliance with contract requirements before submitting for VA review. Proposed deviations from the contract requirements are to be clearly identified. All deviations submitted must include a side by side comparison of item being proposed against item specified. Failure to point out deviations will result in the VA requiring removal and replacement of such work at the Contractor's expense.

    - Stamp, sign, and date each submittal transmittal form indicating action taken.

    - Stamp used by the Contractor on the submittal transmittal form to certify that the submittal meets contract requirements is to be similar to the following:

|	CONTRACTOR	|

|	|

|	(Firm Name)	|

|	|

|	|

|	|

|	Approved	|

|	|

|	|

|	Approved with corrections as noted on submittal data and/or	|

| attached sheets(s)	|

|	|

|	|

|	|

| SIGNATURE: 	|

|	|

| TITLE: 	|

|	|

| DATE: 	|

|	|

|	|

  - SUBMITTAL FORMAT AND TRANSMISSION

    - Provide submittals in electronic format, with the exception of material samples. Use PDF as the electronic format, unless otherwise specified or directed by the Contracting Officer.

    - Compile the electronic submittal file as a single, complete document. Name the electronic submittal file specifically according to its contents.

    - Electronic files must be of sufficient quality that all information is legible. Generate PDF files from original documents so that the text included in the PDF file is both searchable and can be copied. If documents are scanned, Optical Character Resolution (OCR) routines are required.

    - E-mail electronic submittal documents smaller than 5MB in size to e-mail addresses as directed by the Contracting Officer.

    - Provide electronic documents over 5MB through an electronic FTP file sharing system. Confirm that the electronic FTP file sharing system can be accessed from the VA computer network. The Contractor is responsible for setting up, providing, and maintaining the electronic FTP file sharing system for the construction contract period of performance.

    - Provide hard copies of submittals when requested by the Contracting Officer. Up to 3 additional hard copies of any submittal may be requested at the discretion of the Contracting Officer, at no additional cost to the VA.

  - SAMPLES

    - Submit two sets of physical samples showing range of variation, for each required item.

    - Where samples are specified for selection of color, finish, pattern, or texture, submit the full set of available choices for the material or product specified.

    - When color, texture, or pattern is specified by naming a particular manufacturer and style, include one sample of that manufacturer and style, for comparison.

    - Before submitting samples, the Contractor is to ensure that the materials or equipment will be available in quantities required in the project. No change or substitution will be permitted after a sample has been approved.

    - The VA reserves the right to disapprove any material or equipment which previously has proven unsatisfactory in service.

    - Physical samples supplied maybe requested back for use in the project after reviewed and approved.

  - OPERATION AND MAINTENANCE DATA

    - Submit data specified for a given item within 30 calendar days after the item is delivered to the contract site.

    - In the event the Contractor fails to deliver O&M Data within the time limits specified, the Contracting Officer may withhold from progress payments 50 percent of the price of the item with which such O&M Data are applicable.

  - TEST REPORTS

COR may require specific test after work has been installed or completed which could require contractor to repair test area at no additional cost to contract.

  - VA REVIEW OF SUBMITTALS AND RFIS

    - The VA will review all submittals for compliance with the technical requirements of the contract documents. The Architect-Engineer for this project will assist the VA in reviewing all submittals and determining contractual compliance. Review will be only for conformance with the applicable codes, standards and contract requirements.

    - Period of review for submittals begins when the VA COR receives submittal from the Contractor.

    - Period of review for each resubmittal is the same as for initial submittal.

    - VA review period is 15 business days for submittals.

    - VA review period is 10 business days for RFIs.

    - The VA will return submittals to the Contractor with the following notations:

      - "Approved": authorizes the Contractor to proceed with the work covered.

      - "Approved as noted": authorizes the Contractor to proceed with the work covered provided the Contractor incorporates the noted comments and makes the noted corrections.

      - "Disapproved, revise and resubmit": indicates noncompliance with the contract requirements or that submittal is incomplete. Resubmit with appropriate changes and corrections. No work shall proceed for this item until resubmittal is approved.

      - "Not reviewed": indicates submittal does not have evidence of being reviewed and approved by Contractor or is not complete. A submittal marked "not reviewed" will be returned with an explanation of the reason it is not reviewed. Resubmit submittals after taking appropriate action.

  - APPROVED SUBMITTALS

    - The VA approval of submittals is not to be construed as a complete check, and indicates only that the general method of construction, materials, detailing, and other information are satisfactory.

    - VA approval of a submittal does not relieve the Contractor of the responsibility for any error which may exist. The Contractor is responsible for fully complying with all contract requirements and the satisfactory construction of all work, including the need to check, confirm, and coordinate the work of all subcontractors for the project. Non-compliant material incorporated in the work will be removed and replaced at the Contractor’s expense.

    - After submittals have been approved, no resubmittal for the purpose of substituting materials or equipment will be considered unless accompanied by an explanation of why a substitution is necessary.

    - Retain a copy of all approved submittals at project site, including approved samples.

  - WITHHOLDING OF PAYMENT

Payment for materials incorporated in the work will not be made if required approvals have not been obtained.

- - - E N D - - -

SECTION 01 35 26

|  | SAFETY | REQUIREMENTS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | TABLE | OF CONTENTS |  |  |  |  |  |
| 1.1 APPLICABLE PUBLICATIONS: |  |  |  | 4 |  |  |  |
| 1.2 DEFINITIONS: |  |  |  | 5 |  |  |  |
| 1.3 SUBMITTAL REQUIRMENTS: |  |  |  | 10 |  |  |  |
| 1.4 REGULATORY REQUIREMENTS: |  |  |  | 11 |  |  |  |
| 1.5 ACCIDENT PREVENTION PLAN | (APP): |  |  | 11 |  |  |  |
| 1.6 ACTIVITY HAZARD ANALYSES | (AHAs): |  |  | 17 |  |  |  |
| 1.7 PRECONSTRUCTION SAFETY CONFERENCE: |  |  |  |  |  |  | 18 |
| 1.8 SAFETY MEETINGS: |  |  |  |  |  |  | 19 |
| 1.9 “SITE SAFETY AND HEALTH OFFICER” (SSHO) |  |  | and | “COMPETENT | PERSON” | (CP): | 19 |
| 1.10 TRAINING: |  |  |  |  |  |  | 21 |
| 1.11 INSPECTIONS: |  |  |  |  |  |  | 22 |
| 1.12 MISHAPS, OSHA 300 LOGS, AND MAN-HOURS: |  |  |  |  |  |  | 23 |
| 1.13 PERSONAL PROTECTIVE EQUIPMENT (PPE): |  |  |  |  |  |  | 25 |
| 1.14 PRE-CONSTRUCTION RISK ASSESSMENT |  |  |  |  |  |  | 27 |
| 1.15 DUST CONTROL |  |  |  |  |  |  | 29 |
| 1.16 TUBERCULOSIS SCREENING |  |  |  |  |  |  | 29 |
| 1.17 FIRE SAFETY |  |  |  |  |  |  | 30 |
| 1.18 ELECTRICAL |  |  |  |  |  |  | 34 |
| 1.19 FALL PROTECTION |  |  |  |  |  |  | 36 |
| 1.20 SCAFFOLDS AND OTHER WORK PLATFORMS |  |  |  |  |  |  | 37 |
| 1.21 EXCAVATION AND TRENCHES |  |  |  |  |  |  | 37 |

  - CRANES	40

  - CONTROL OF HAZARDOUS ENERGY (LOCKOUT/TAGOUT)	41

  - CONFINED SPACE ENTRY	42

  - WELDING AND CUTTING	42

  - LADDERS	42

  - FLOOR & WALL OPENINGS	43

SECTION 01 35 26 SAFETY REQUIREMENTS

  - APPLICABLE PUBLICATIONS:

    - Latest publications listed below form part of this Article to extent referenced. Publications are referenced in text by basic designations only.

    - American Society of Safety Professionals (ASSP):

A10.1-2011 ..........Pre-Project & Pre-Task Safety and Health

Planning

A10.34-2012 .........Protection of the Public on or Adjacent to

Construction Sites

A10.38-2013 .........Basic Elements of an Employer’s Program to

Provide a Safe and Healthful Work Environment American National Standard Construction and Demolition Operations

Z359.0-2012 .........Definitions and Nomenclature Used for Fall

Protection and Fall Arrest Z359.1-2016 .........The Fall Protection Code

    - American Society for Testing and Materials (ASTM):

E84-2013 ............Surface Burning Characteristics of Building

Materials

    - The Facilities Guidelines Institute (FGI):

FGI Guidelines-2010Guidelines for Design and Construction of

Healthcare Facilities

    - National Fire Protection Association (NFPA):

10-2018 .............Standard for Portable Fire Extinguishers 30-2018 .............Flammable and Combustible Liquids Code

51B-2019 ............Standard for Fire Prevention During Welding,

Cutting and Other Hot Work 70-2020 .............National Electrical Code

70B-2019 ............Recommended Practice for Electrical Equipment

Maintenance

70E-2018 ...........Standard for Electrical Safety in the Workplace 241-2019 ............Standard for Safeguarding Construction,

Alteration, and Demolition Operations

703-2024 ............Standard for Fire Retardant–Treated Wood and

Fire-Retardant Coatings for Building Materials

    - The Joint Commission (TJC)

TJC Manual .........Comprehensive Accreditation and Certification

Manual

    - U.S. Nuclear Regulatory Commission

10 CFR 20 ..........Standards for Protection Against Radiation

    - U.S. Occupational Safety and Health Administration (OSHA):

29 CFR 1904 ........Reporting and Recording Injuries & Illnesses

29 CFR 1910 ........Safety and Health Regulations for General

Industry

29 CFR 1926 ........Safety and Health Regulations for Construction

Industry

CPL 2-0.124 .........Multi-Employer Citation Policy

    - US Army Corps of Engineers Safety and Occupational Health (SOH) Requirements Publication No. EM 385-1-1, 2024 edition

  - DEFINITIONS:

    - Critical Lift. A lift with the hoisted load exceeding 75% of the crane’s maximum capacity; lifts made out of the view of the operator

(blind picks); lifts involving two or more cranes; personnel being hoisted; and special hazards such as lifts over occupied facilities, loads lifted close to power-lines, and lifts in high winds or where other adverse environmental conditions exist; and any lift which the crane operator believes is critical.

    - OSHA “Competent Person” (CP). One who is capable of identifying existing and predictable hazards in the surroundings and working conditions which are unsanitary, hazardous or dangerous to employees, and who has the authorization to take prompt corrective measures to eliminate them (see 29 CFR 1926.32(f)).

    - Competent Person, Confined Space

The CP, Confined Space, is a person meeting the competent person requirements as defined EM 385-1-1 Appendix Q, with thorough knowledge of OSHA’s Confined Space Standard, 29 CFR 1910.146, and designated in writing to be responsible for the immediate supervision, implementation and monitoring of the confined space program, who through training, knowledge and experience in confined space entry is capable of identifying, evaluating and addressing existing and potential confined space hazards and, who has the authority to take prompt corrective measures with regard to such hazards.

    - Competent Person, Cranes and Rigging.

The CP, Cranes and Rigging, as defined in EM 385-1-1 Appendix Q, is a person meeting the competent person, who has been designated in writing to be responsible for the immediate supervision, implementation and monitoring of the Crane and Rigging Program, who through training, knowledge and experience in crane and rigging is capable of identifying, evaluating and addressing existing and potential hazards and, who has the authority to take prompt corrective measures regarding such hazards.

    - Competent Person, Excavation/Trenching.

A CP, Excavation/Trenching, is a person meeting the competent person requirements as defined in EM 385-1-1 Appendix Q and 29 CFR 1926,

who has been designated in writing to be responsible for the immediate supervision, implementation and monitoring of the excavation/trenching program, who through training, knowledge and experience in excavation/trenching is capable of identifying, evaluating and addressing existing and potential hazards and, who has the authority to take prompt corrective measures with regard to such hazards.

    - Competent Person, Fall Protection

The CP, Fall Protection, is a person meeting the competent person requirements as defined in EM 385-1-1 Appendix Q and in accordance with ASSE/SAFE Z359.0, who has been designated in writing by the employer to be responsible for immediate supervising, implementing and monitoring of the fall protection program, who through training, knowledge and experience in fall protection and rescue systems and equipment, is capable of identifying, evaluating and addressing existing and potential fall hazards and, who has the authority to take prompt corrective measures with regard to such hazards.

    - Competent Person, Scaffolding

The CP, Scaffolding is a person meeting the competent person requirements in EM 385-1-1 Appendix Q and designated in writing by the employer to be responsible for immediate supervising, implementing and monitoring of the scaffolding program. The CP for Scaffolding has enough training, knowledge and experience in scaffolding to correctly identify, evaluate and address existing and potential hazards and has the authority to take prompt corrective measures with regard to these hazards. CP qualifications must be documented and include experience on the specific scaffolding systems/types being used, assessment of the base material that the scaffold will be erected upon, load calculations for materials and personnel, and erection and dismantling. The CP for scaffolding must have a documented, minimum of 8-hours of scaffold training to include training on the specific type of scaffold being used (e.g. mast-climbing, adjustable, tubular frame), in accordance with EM

385-1-1 Section 22.B.02.

    - Competent Person (CP) Trainer

A competent person trainer as defined in EM 385-1-1 Appendix Q, who is qualified in the material presented, and who possesses a working knowledge of applicable technical regulations, standards, equipment and systems related to the subject matter on which they are training Competent Persons. A competent person trainer must be familiar with the typical hazards and the equipment used in the industry they are instructing. The training provided by the competent person trainer must be appropriate to that specific industry. The competent person trainer must evaluate the knowledge and skills of the competent persons as part of the training process.

    - High Risk Activities

High Risk Activities are activities that involve work at heights, crane and rigging, excavations and trenching, scaffolding, electrical work, and confined space entry.

    - "Qualified Person" means one who, by possession of a recognized degree, certificate, or professional standing, or who by extensive knowledge, training and experience, has successfully demonstrated his ability to solve or resolve problems relating to the subject matter, the work, or the project.

    - Qualified Person, Fall Protection (QP for FP)

A QP for FP is a person meeting the requirements of EM 385-1-1 Appendix Q, and ASSE/SAFE Z359.0, with a recognized degree or professional certificate and with extensive knowledge, training and experience in the fall protection and rescue field who is capable of designing, analyzing, and evaluating and specifying fall protection and rescue systems.

    - USACE Property and Equipment

Interpret "USACE" property and equipment specified in USACE EM 385- 1-1 as Government property and equipment.

    - High Visibility Accident. Any mishap which may generate publicity or high visibility.

    - Mishap: Mishap in this specification is defined according to the EM 385-1-1. A mishap is any unplanned, undesired event that occurs during the course of work being performed. This includes accidents, incidents, and near misses.

    - Mishap Criticality Categories

## No impact/Near-Miss – near miss incidents that shall be investigated and reported to the VA within 24 hours.

## Minor incident/impact – incidents that require first aid or result in minor equipment damage (less than

## $5000). These incidents must be investigated and reported to the VA within 24 hours.

## Moderate incident/impact – Any work-related injury or illness that results in any of the following. These incidents must be investigated and are required to be reported to the VA within 2 hours.

## Days away from work (any time lost after day of injury/illness onset);

## Restricted work;

## Transfer to another job;

## Medical treatment beyond first aid;

## Loss of consciousness;

## A significant injury or illness diagnosed by a physician or other licensed health care professional, even if it did not result in (1) through (5) above or,

## any incident that leads to major equipment damage (greater than $5000).

## Major incident/impact – Any mishap that leads to fatalities, hospitalizations, amputations, and losses of an eye as a result of contractors’ activities. Or any incident which leads to major property damage (greater than $20,000) and/or may generate publicity or high visibility. These incidents must be investigated and are required to be reported to the VA as soon as practical, but not later than 2 hours after the incident.

    - Load Handling Equipment (LHE)

LHE is a term used to describe cranes, hoists and all other hoisting equipment (hoisting equipment means equipment, including crane, derricks, hoists and power operated equipment used with rigging to raise, lower or horizontally move a load).

    - Medical Treatment. Treatment administered by a physician or by registered professional personnel under the standing orders of a physician. Medical treatment does not include first aid treatment even through provided by physician or registered personnel.

  - SUBMITTAL REQUIRMENTS:

    - Government approval or concurrence is required for submittals with a "G" designation; submittals not having a "G" designation are submitted for information only.

    - Preconstruction Submittals

## Accident Prevention Plan (APP); G

    - Reports

## Monthly Contractor Health Safety and Environmental (HS&E) Performance Report; G

## Notifications and Reports;

## Mishap Reports;

## Near-Miss Reports;

## LHE Inspection Reports

## Monthly Exposure Hour Reports;

    - Work Plans

## Standard Lift Plan; G

## Critical Lift Plan; G

## Activity Hazard Analysis (AHA); G

## Confined Space Entry Permit

## Hot Work Permit

## Radiography Operation Planning Work Sheet; G

## Portable Gauge Operations Planning Worksheet; G

    - Certificates

## Contractor Safety Self-Evaluation Checklist

## Crane Operators/Riggers Certifications; G

## Certificate of Compliance

## Mobile Cranes Inspection Certificate

## License Certificates

## Machinery & Mechanized Equipment Certification Form

  - REGULATORY REQUIREMENTS:

    - In addition to the detailed requirements included in the provisions of this contract, comply with the most recent edition of USACE EM 385-1-1, comply with 29 CFR 1926, comply with 29 CFR 1910 as incorporated by reference within 29 CFR 1926, comply with ASSP A10.34, and all applicable federal, state, and local laws, ordinances, criteria, rules and regulations. Submit matters of interpretation of standards for resolution before starting work. Where the requirements of this specification, applicable laws, criteria, ordinances, regulations, and referenced documents vary, the most stringent requirements govern except with specific approval and acceptance by the Resident Engineer// Regional Safety Engineer or Contracting Officer Representative or Government Designated Authority.

  - ACCIDENT PREVENTION PLAN (APP):

    - The APP (aka Construction Safety & Health Plan) shall interface with the Contractor's overall safety and health program. Include any portions of the Contractor's overall safety and health program referenced in the APP in the applicable APP element and ensure it is site-specific. The Government considers the Prime Contractor to be the "controlling authority" for all worksite safety and health of each subcontractor(s). Contractors are responsible for informing their subcontractors of the safety provisions under the terms of the contract and the penalties for noncompliance, coordinating the work to prevent one craft from interfering with or creating hazardous working conditions for other crafts, and inspecting subcontractor operations to ensure that Mishap prevention responsibilities are being carried out.

## The APP shall be prepared as follows:

      - Written in English by a qualified person who is employed by the Prime Contractor articulating the specific work and hazards pertaining to the contract. Specifically articulating the safety requirements found within these VA contract safety specifications

and the latest version of the United States Army Corps of Engineers – Safety and Occupational Health (SOH) Requirements - EM 385-1-1 Manual. Model language and format can be found in Appendix A of the EM 385-1-1 Manual

      - Address both the Prime Contractors and the subcontractors work operations.

      - State measures to be taken to control hazards associated with materials, services, or equipment provided by suppliers.

      - Address all the elements/sub-elements and in order as follows:

- SIGNATURE SHEET. Title, signature, and phone number of the following:

  - Plan preparer (Qualified Person such as corporate safety staff person or contracted Certified Safety Professional with construction safety experience);

  - Plan approver (company/corporate officers authorized to obligate the company);

  - Plan concurrence (e.g., Chief of Operations, Corporate Chief of Safety, Corporate Industrial Hygienist, project manager or superintendent, project safety professional). Provide concurrence of other applicable corporate and project personnel (Contractor).

- BACKGROUND INFORMATION. List the following:

  - Contractor;

  - Contract number;

  - Project name;

  - Brief project description, description of work to be performed, and location; phases of work anticipated (these will require an AHA).

- STATEMENT OF SAFETY AND HEALTH POLICY. Provide a copy of current corporate/company Safety and Health Policy Statement, detailing commitment to providing a safe and healthful workplace for all employees. The Contractor’s written safety program goals, objectives, and accident experience goals for this contract should be provided. The Statement of Safety and Health Policy must be signed by a company executive.

- RESPONSIBILITIES AND LINES OF AUTHORITIES. Provide the following:

  - A statement of the employer’s ultimate responsibility for the implementation of his SOH program;

  - Identification and accountability of personnel responsible for safety at both corporate and project level. Contracts specifically requiring safety or industrial hygiene personnel shall include a copy of their resumes.

  - The names of Competent and/or Qualified Person(s) and proof of competency/qualification to meet specific OSHA or EM 385-1-1 Competent/Qualified Person(s) requirements must be attached.;

  - Requirements that no work shall be performed unless a designated competent person is present on the job site;

  - Requirements for pre-task Activity Hazard Analysis (AHAs);

  - Lines of authority;

  - Policies and procedures regarding noncompliance with safety requirements (to include disciplinary actions for violation of safety requirements) should be identified;

- SUBCONTRACTORS AND SUPPLIERS. If applicable, provide procedures for coordinating SOH activities with other employers on the job site:

  - Identification of subcontractors and suppliers (if known);

  - Safety responsibilities of subcontractors and suppliers.

- TRAINING.

  - Site-specific SOH orientation training at the time of initial hire or assignment to the project for every employee before working on the project site is required.

  - Mandatory training and certifications that are applicable to this project (e.g., explosive actuated tools, crane operator, rigger, crane signal person, fall protection, electrical lockout/NFPA 70E, machine/equipment lockout, confined space, etc.…) and any requirements for periodic retraining/recertification are required.

  - Procedures for ongoing safety and health training for supervisors and employees shall be established to address changes in site hazards/conditions.

  - OSHA 10-hour Construction Outreach training within the past five years is required for all workers on site and the OSHA 30-hour Construction Outreach training within the past five years is required for Trade Competent Persons (CPs)

- SAFETY AND HEALTH INSPECTIONS.

  - Specific assignment of responsibilities for a minimum daily job site safety and health inspection during periods of work activity: Who will conduct (e.g., “Site Safety and Health CP”), proof of inspector’s training/qualifications, when inspections will be conducted, procedures for documentation, deficiency tracking system, and follow-up procedures.

  - Any external inspections/certifications that may be required (e.g., contracted CSP or CSHT)

- MISHAP INVESTIGATION & REPORTING.

  - The APP shall include identify person(s) responsible to provide the following to the Resident Engineer // Contracting Officer Representative // Government Designated Authority :

## Monthly HS&E Performance Report (Exposure Hours Data);

## Mishap investigation reports;

## Project site injury and illness logs;

## Near-Miss reports;

- PLANS (PROGRAMS, PROCEDURES) REQUIRED. Based on a risk assessment of contracted activities and on mandatory OSHA and/or EM 385-1-1 compliance programs, the Contractor shall address all applicable occupational, patient, and public safety risks in site-specific compliance and accident prevention plans. These Plans shall include but are not limited to procedures for addressing the risks associated with the following:

  - Emergency response;

  - Contingency for severe weather;

  - Fire Prevention;

  - Medical Support;

  - Posting of emergency telephone numbers;

  - Prevention of alcohol and drug abuse;

  - Site sanitation (housekeeping, drinking water, toilets);

  - Night operations and lighting;

  - Hazard communication program;

  - Welding/Cutting “Hot” work;

  - Electrical Safe Work Practices (Electrical LOTO/NFPA 70E);

  - General Electrical Safety;

  - Hazardous energy control (LOTO);

  - Site-Specific Fall Protection & Prevention;

  - Excavation/trenching;

  - Asbestos abatement;

  - Lead abatement;

  - Crane Critical lift;

  - Respiratory protection;

  - Health hazard control program;

  - Radiation Safety Program;

  - Abrasive blasting;

  - Heat/Cold Stress Monitoring;

  - Crystalline Silica Monitoring (Assessment);

  - Demolition plan (to include engineering survey);

  - Formwork and shoring erection and removal;

  - Pre-Cast Concrete;

  - Public (Mandatory compliance with ANSI/ASSP A10.34-2012);

  - Sub-contractor or cross-trade coordination;

    - Submit the APP to the Contracting Officer Representative Government Designated Authority for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES 15 calendar days prior to the date of the preconstruction safety conference for acceptance. Work cannot proceed without an accepted APP.

    - Once accepted by the Contracting Officer Representative, the APP and attachments will be enforced as part of the contract. Disregarding the provisions of this contract or the accepted APP will be cause for stopping of work, at the discretion of the Contracting Officer in

accordance with FAR Clause 52.236-13, Accident Prevention, until the matter has been rectified.

    - Once work begins, changes to the accepted APP shall be made with the knowledge and concurrence of the Resident Engineer, Contracting Officer Representative or Government Designated Authority. Should any severe hazard exposure, i.e. imminent danger, become evident, stop work in the area, secure the area, and develop a plan to remove the exposure and control the hazard. Notify the Resident Engineering Office and Contracting Officer within 2 hours of discovery. Eliminate/remove the hazard. In the interim, take all necessary action to restore and maintain safe working conditions to safeguard onsite personnel, visitors, the public and the environment.

  - ACTIVITY HAZARD ANALYSES (AHAS):

    - AHAs are also known as Job Hazard Analyses, Job Safety Analyses, and Activity Safety Analyses. Before beginning each work activity involving a type of work presenting hazards not experienced in previous project operations or where a new work crew or sub-contractor is to perform the work, the Contractor(s) performing that work activity shall prepare an AHA (Example electronic AHA forms can be found on the US Army Corps of Engineers web site)

    - AHAs shall define the activities being performed and identify the work sequences, the specific anticipated hazards, site conditions, equipment, materials, and the control measures to be implemented to eliminate or reduce each hazard to an acceptable level of risk.

    - Work shall not begin until the AHA for the work activity has been accepted by the Resident Engineer, Contracting Officer Representative or Government Designated Authority and discussed with all engaged in the activity, including the Contractor, subcontractor(s), and Government on-site representatives at preparatory and initial control phase meetings.

      - The names of the Competent/Qualified Person(s) required for a particular activity (for example, excavations, scaffolding, fall

protection, other activities as specified by OSHA, EM 385-1-1, or other State and Local agencies) shall be identified and included in the AHA. Certification of their competency/qualification shall be submitted to the Government Designated Authority (GDA) for acceptance prior to the start of that work activity.

      - The AHA shall be reviewed and modified as necessary to address changing site conditions, operations, or change of competent/qualified person(s).

- If more than one Competent/Qualified Person is used on the AHA activity, a list of names shall be submitted as an attachment to the AHA. Those listed must be Competent/Qualified for the type of work involved in the AHA and familiar with current site safety issues.

- If a new Competent/Qualified Person (not on the original list) is added, the list shall be updated (an administrative action not requiring an updated AHA). The new person shall acknowledge in writing that he or she has reviewed the AHA and is familiar with current site safety issues.

      - Submit AHAs to the , Contracting Officer Representative Government Designated Authority for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES for review at least 15 calendar days prior to the start of each phase. Subsequent AHAs as shall be formatted as amendments to the APP. The analysis should be used during daily inspections to ensure the implementation and effectiveness of the activity's safety and health controls.

      - The AHA list will be reviewed periodically (at least weekly) at the Contractor supervisory safety meeting and updated as necessary when procedures, scheduling, or hazards change.

      - Develop the activity hazard analyses using the project schedule as the basis for the activities performed. All activities listed on the project schedule will require an AHA. The AHAs will be developed by

the contractor, supplier, or subcontractor and provided to the prime contractor for review and approval and then submitted to the Contracting Officer Representative or Government Designated Authority for review for compliance.

  - PRECONSTRUCTION SAFETY CONFERENCE:

    - Contractor representatives who have a responsibility or significant role in implementation of the accident prevention program, as required by 29 CFR 1926.20(b)(1), on the project shall attend the pre- construction safety conference to gain a mutual understanding of its implementation. This includes the project superintendent, subcontractor superintendents, and any other assigned safety and health professionals.

    - Discuss the details of the submitted APP to include incorporated plans, programs, procedures and a listing of anticipated AHAs that will be developed and implemented during the performance of the contract. This list of proposed AHAs will be reviewed at the conference and an agreement will be reached between the Contractor and the Contracting Officer's representative as to which phases will require an analysis. In addition, establish a schedule for the preparation, submittal, review, and acceptance of AHAs to preclude project delays.

  - SAFETY MEETINGS:

Conduct safety meetings to review past activities, plan for new or changed operations, review pertinent aspects of appropriate AHA (by trade), establish safe working procedures for anticipated hazards, and provide pertinent Safety and Occupational Health (SOH) training and motivation. Conduct meetings at least once a month for all supervisors on the project location. The SSHO, supervisors, foremen, or CDSOs must conduct meetings at least once a week for the trade workers. Document meeting minutes to include the date, persons in attendance, subjects discussed, and names of individual(s) who conducted the meeting.

Maintain documentation on-site and furnish copies to the Contracting

Officer on request. Notify the Contracting Officer of all scheduled meetings 7 calendar days in advance.

  - “SITE SAFETY AND HEALTH OFFICER” (SSHO) AND “COMPETENT PERSON” (CP):

    - The Prime Contractor shall provide a Safety oversight team that includes a minimum of one (1) person at each project site, for each shift, to function as the Site Safety and Health Officer (SSHO). The Prime Contractor shall provide a minimum of one “Full-Time” SSHO at each project site, for each shift (with no other duties) that holds as current, a professional safety certification with at least 3 years of dedicated construction safety related experience. The SSHO shall ensure that the requirements of the VA and of 29 CFR 1926.16 are met for the project. The SSHO must be at the work site at all times, during construction activities, to implement and administer the Contractor's safety program and government-accepted Accident Prevention Plan. If the SSHO is off-site for a period longer than 8 hours, or one shift, and not exceeding 40 hours, or 5 shifts, a pre-approved Alternate Safety Officer shall be provided and shall fulfill the same roles and responsibilities as the primary SSHO. The Alternate Safety Officer shall have the required training, experience, and qualifications in accordance with EM 385-1-1 Section 01.A.17, and all associated sub- paragraphs. When the SSHO is temporarily (not to exceed 8 hours) off- site, a Designated Representative (DR) from the Prime Contractors’ staff, as identified in the AHA may be used in lieu of an Alternate Safety Officer and shall be on the project site, at all times, when work is being performed. Note that the DR is a collateral duty safety position, with safety duties in addition to their full-time occupation. Each subcontractor shall designate a minimum of one CP in compliance with 29 CFR 1926.20 (b)(2) that will be identified as a CP to administer their individual safety programs.

    - Further, all specialized Competent Persons for the work crews will be supplied by the respective contractor as required by 29 CFR 1926 (i.e. Asbestos, Electrical, Cranes, & Derricks, Demolition, Fall Protection,

Fire Safety/Life Safety, Ladder, Rigging, Scaffolds, and Trenches/Excavations).

    - These Competent Persons can have collateral duties as the subcontractor’s superintendent and/or work crew lead persons as well as fill more than one specialized CP role (i.e. Asbestos, Electrical, Cranes, & Derricks, Demolition, Fall Protection, Fire Safety/Life Safety, Ladder, Rigging, Scaffolds, and Trenches/Excavations).

However, the SSHO has be a separate qualified individual from the Prime Contractor’s Superintendent and/or Quality Control Manager with duties only as the SSHO

    - The SSHO or an equally qualified Designated Representative/alternate will maintain a presence on the site during construction operations in accordance with FAR Clause 52.236-6: Superintendence by the Contractor. CPs will maintain presence during their construction activities in accordance with above mentioned clause. A listing of the designated SSHO and all known CPs shall be submitted prior to the start of work as part of the APP with the training documentation and/or AHA as listed in Section 1.8 below.

    - The repeated presence of uncontrolled hazards during a contractor’s work operations will result in the designated CP as being deemed incompetent and result in the required removal of the employee in accordance with FAR Clause 52.236-5: Material and Workmanship, Paragraph (c).

  - TRAINING:

    - The designated Prime Contractor SSHO must meet the requirements of all applicable OSHA standards and be capable (through training, experience, and qualifications) of ensuring that the requirements of 29 CFR 1926.16 and other appropriate Federal, State and local requirements are met for the project.

## As a minimum the SSHO must have completed the OSHA 30-hour Construction Safety Outreach class within the past five (5) years and:

## Seven (7) years of construction industry safety related experience.

## OR have a safety and health degree from an accredited university or college and five (5) years of construction industry safety related experience

## OR hold as current, a Certified Safety Professional (CSP) or a Construction Health and Safety Technician (CHST) certification and five (3) years of construction industry safety related experience.

    - The Alternate Safety Officer shall meet, at a minimum, the requirements of EM 385-1-1 Section 1 and have five (5) years of construction industry safety experience If the SSHO does not have a current certification, certification must be obtained within 90 days, maximum, of contract award.

    - All designated CPs shall have completed the OSHA 30-hour Construction Safety course and/or EM 385-1-1 40-hour training within the past 5 years. In addition, all CPs with high hazard work operations (such as operations involving asbestos, electrical, cranes, demolition, work at heights/fall protection, fire safety/life safety, ladder, rigging, scaffolds, and trenches/excavations) shall have a specialized formal course in the hazard recognition and control associated with those high hazard work operations. Documented “repeat” deficiencies in the execution of safety requirements will require retaking the requisite formal course.

    - All other construction workers shall have the OSHA 10-hour Construction Safety Outreach course within the past 5 years and any necessary safety training to be able to identify hazards within their work environment.

    - Submit training records associated with the above training requirements to Contracting Officer Representative for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP

DRAWINGS, PRODUCT DATA AND SAMPLES 15 calendar days prior to the date of the preconstruction safety conference for acceptance.

    - Prior to any worker for the contractor or subcontractors beginning work, they shall undergo a safety briefing provided by the SSHO or his/her designated representative. As a minimum, this briefing shall include information on the site-specific hazards, construction limits, VAMC safety guidelines, means of egress, break areas, work hours, locations of restrooms, use of VAMC equipment, emergency procedures, accident reporting etc... Documentation shall be provided to the COR that individuals have undergone contractor’s safety briefing.

    - Ongoing safety training will be accomplished in the form of weekly documented safety meeting.

  - INSPECTIONS:

    - The SSHO shall conduct frequent and regular safety inspections (daily) of the site and each of the subcontractors CPs shall conduct frequent and regular safety inspections (daily) of their work operations as required by 29 CFR 1926.20(b)(2). Each week, the SSHO shall conduct a formal documented inspection with a written report of the entire construction areas with the subcontractors’ “Trade Safety and Health CPs” present in their work areas. Coordinate with, and report findings and corrective actions weekly to Contracting Officer Representative.

    - A Certified Safety Professional (CSP) with specialized knowledge in construction safety or a certified Construction Safety and Health Technician (CSHT) shall randomly conduct a monthly site safety inspection. The CSP or CSHT shall be one that is not a part of the immediate site project team. The individual can be a corporate safety professional or independently contracted who is not an immediate member of the construction project site team. The CSP or CSHT will provide their certificate number on the required report for verification as necessary.

      - Results of the inspection will be documented with tracking of the identified hazards to abatement.

      - The Contracting Officer Representative will be notified immediately prior to start of the inspection and invited to accompany the inspection.

      - Identified hazard and controls will be discussed to come to a mutual understanding to ensure abatement and prevent future reoccurrence.

      - A report of the inspection findings with status of abatement will be provided to the Contracting Officer Representative within one week of the onsite inspection.

  - MISHAPS, OSHA 300 LOGS, AND EXPOSURE-HOURS:

    - The prime contractor shall establish and maintain a Near-Miss and Mishap reporting, recordkeeping, and analysis system to track and analyze all injuries and illnesses, high visibility incidents, and accidental property damage (both government and contractor) that occur on site. Notify and provide an initial report to the Contracting Officer Representative as soon as practical, but no more than two hours after any Moderate or Major Mishap, High Visibility Incidents, or any weight handling and hoisting equipment mishap. No Impact/Near-Miss and Minor Mishaps shall be reported within 24 hours or as soon as practical. Within the notification the sender shall include contractor name; contract title; type of contract; name of activity, installation or location where mishap occurred; date and time of accident; names of personnel injured; extent of property damage, if any; extent of injury, if known, and brief description of mishap (to include type of construction equipment used, PPE used, etc.). Preserve the conditions and evidence on the Mishap site until the Contracting Officer Representative determines whether a government investigation will be conducted.

    - Conduct a mishap investigation for all Mishaps including mishaps resulting in at least $20,000 in damages without injury, to establish the root cause(s) of the mishap. The Mishap investigation shall include images, 5 whys, the injured person’s firsthand account, any witness accounts, methods of procedures, related AHA to the task, and corrective action plan signed by the president, vice president, or

appropriate corporate-level leadership identified in the company’s org chart for the project. Additionally, complete the VA Form 2162 (or equivalent) and provide the report to the Contracting Officer Representative within 7 calendar days of the accident. The Contracting Officer Representative will provide copies of any required or special forms.

    - A summation of all exposure-hours worked by the contractor and associated sub-contractors for each month will be reported Contracting Officer Representative no later than the 10th day of the following month.

    - A summation of all Minor, Moderate, and Major incidents experienced on site by the contractor and associated sub-contractors for each month will be provided to the Contracting Officer Representative monthly. The contractor and associated sub-contractors’ OSHA 300 logs will be made available to the Contracting Officer Representative upon request.

  - PERSONAL PROTECTIVE EQUIPMENT (PPE):

    - PPE is governed in all areas by the nature of the work the employee is performing. For example, specific PPE required for performing work on electrical equipment is identified in NFPA 70E, Standard for Electrical Safety in the Workplace.

    - Any PPE above and beyond the Mandatory PPE identified below and determined by the Contracting Officer or their Representative to be necessary in the performance of the Governments duties relative to this contract, shall be provided to the Government upon written notification by the Contracting Officer and at no additional expense to the Government. All PPE provided to the Government shall also be accompanied by any relevant or required training necessary to ensure its proper use.

    - Mandatory Minimum PPE includes:

      - Hard Hats – unless written authorization is given by the or Contracting Officer Representative in circumstances of work

operations that have limited potential for falling object hazards such as during finishing work or minor remodeling. With authorization to relax the requirement of hard hats, if a worker becomes exposed to an overhead falling object hazard, then hard hats would be required in accordance with the OSHA and/or EM 385-1-1 regulations.

      - Safety glasses - unless written authorization is given by the Contracting Officer Representative in circumstances of no eye hazards, appropriate safety glasses meeting the ANSI Z.87.1 standard must be worn by each person on site.

      - Appropriate Safety Shoes – based on the hazards present, safety shoes meeting the requirements of ASTM F2413-11 shall be worn by each person on site unless written authorization is given by Contracting Officer Representative in circumstances of no foot hazards.

      - Hearing protection - Use personal hearing protection at all times in designated noise hazardous areas or when performing noise hazardous tasks.

      - High-visibility Safety Apparel – appropriate brightly colored clothing that feature some type of reflective material on them, such as safety vests, shall be worn by personnel or visitors on construction sites.

  - PRE-CONSTRUCTION RISK ASSESSMENT

    - Control of all construction-associated hazards that affect VA medical facilities, their occupants, services and mission-essential functions and capabilities is critical in all medical center facilities. VHA Pre-Construction Risk Assessments (PCRAs) for construction, renovation and maintenance projects are included with this contract solicitation

with required mitigations of identified hazards. VHA-PCRAs will be re- validated and updated as needed based on but not limited to changes from original designs, affected individuals, areas/locations, scope,

contractor means and methods, safety requirements, phasing, contractor competencies and capabilities.

    - Infection Prevention and Control is critical in all medical center facilities. Interior construction activities causing disturbance of existing dust, or creating new dust, must be conducted within ventilation-controlled areas that minimize the flow of airborne particles into patient areas. A detailed analysis of potential risks for infectious disease transmission affecting the care, treatment or services of patients or residents has been conducted. VHA Infection Control Risk Assessments (ICRAs) are included with this contract solicitation with required mitigation actions/activities. VHA-ICRAs will be re-validated and updated as needed based on changes in original designs, affected individuals, area(s) or location(s), scope, contractor means and methods, infection prevention and control requirements, differing site conditions, phasing, contractor competencies and capabilities, and infectious disease outbreaks.

    - For work occurring at a VA medical facility, coordinate with the facility Safety Manager/Officer, as several aspects of this section directly relate to infection control risk assessments required in or adjacent to construction affecting occupied buildings accredited by The Joint Commission.

    - Products and Materials:

      - Sheet Plastic: Fire retardant polyethylene, 6-mil thickness meeting local fire codes

      - Barrier Doors: Self Closing, One-hour solid core wood in steel frame, painted

      - one-hour drywall

      - High Efficiency Particulate Air-Equipped filtration machine rated at 95% capture of 0.3 microns including pollen, mold spores and dust particles. HEPA filters should have ASHRAE 85 or other prefilter to extend the useful life of the HEPA. Provide both primary and secondary filtrations units. Maintenance of equipment and

replacement of the HEPA filters and other filters will be in accordance with manufacturer’s instructions.

      - Exhaust Hoses: Heavy duty, flexible steel reinforced; Ventilation Blower Hose

      - Adhesive Walk-off Mats: Provide minimum size mats of 24 inches x 36 inches

      - Disinfectant: EPA-registered, Hospital-approved disinfectant or equivalent product

      - Portable Ceiling Access Module as indicated on drawings.

      - PPE: in areas designated on drawings.

  - DUST CONTROL

## Contractor shall verify that dust will not be introduced into the facility through intake vents or building openings. HEPA filtration on intake vents is required where dust may be introduced.

## Dust created from disturbance of soil such as from vehicle movement will be wetted with use of a water truck as necessary.

    - All cutting, drilling, grinding, sanding, or disturbance of materials shall be accomplished with tools equipped with either local exhaust ventilation (i.e. vacuum systems) or wet suppression controls.

  - TUBERCULOSIS SCREENING

    - Contractor shall provide written certification that all contract employees assigned to the work site have had a pre-placement tuberculin screening within 90 days prior to assignment to the worksite and been found have negative TB screening reactions. Contractors shall be required to show documentation of negative TB screening reactions for

any additional workers who are added after the 90-day requirement before they will be allowed to work on the work site. NOTE: This can be the Center for Disease Control (CDC) and Prevention and two-step skin testing or a Food and Drug Administration (FDA)-approved blood test.

      - Contract employees manifesting positive screening reactions to the tuberculin shall be examined according to current CDC guidelines prior to working on VHA property.

      - Subsequently, if the employee is found without evidence of active (infectious) pulmonary TB, a statement documenting examination by a physician shall be on file with the employer (construction contractor), noting that the employee with a positive tuberculin screening test is without evidence of active (infectious) pulmonary TB.

      - If the employee is found with evidence of active (infectious) pulmonary TB, the employee shall require treatment with a subsequent statement to the fact on file with the employer before being allowed to return to work on VHA property.

  - FIRE SAFETY

    - Fire Safety Plan: Establish and maintain a site-specific fire protection program in accordance with 29 CFR 1926. Prior to start of work, prepare a plan detailing project-specific fire safety measures, including periodic status reports, and submit to Contracting Officer Representative for review for compliance with contract requirements in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES. This plan may be an element of the Accident Prevention Plan.

    - Site and Building Access: Maintain free and unobstructed access to facility emergency services and for fire, police and other emergency response forces in accordance with NFPA 241.

    - For work occurring at a VA medical facility, coordinate with the facility Safety Manager/Officer, as several aspects of this section

directly relate to interim life safety measures required in or adjacent to construction affecting occupied buildings accredited by The Joint Commission.

    - Separate temporary facilities, such as trailers, storage sheds, and dumpsters, from existing buildings and new construction by distances in accordance with NFPA 241. For small facilities with less than 6 m (20 feet) exposing overall length, separate by 3m (10 feet).

    - Temporary Construction Partitions:

## Install and maintain temporary construction partitions to provide smoke-tight separations between construction areas and adjoining areas. Construct partitions of gypsum board or fire-retardant treated plywood (fire-retardant treated in accordance with NFPA 703) on both sides of fire-retardant treated wood framing or metal steel studs. Extend the partitions through suspended ceilings to floor slab deck or roof. Seal joints and penetrations. At door openings, install Class C, ¾ hour fire/smoke rated doors with self-closing devices.

## Install one-hour temporary construction partitions as shown on drawings to maintain integrity of existing exit stair enclosures, exit passageways, fire-rated enclosures of hazardous areas, horizontal exits, smoke barriers, vertical shafts and openings enclosures.

## Close openings in smoke barriers and fire-rated construction to maintain fire ratings. Seal penetrations with listed through-penetration firestop materials in accordance with Section 07 84 00, FIRESTOPPING.

    - Temporary Heating and Electrical: Install, use and maintain installations in accordance with 29 CFR 1926, NFPA 241 and NFPA 70.

    - Means of Egress: Do not block exiting for occupied buildings, including paths from exits to roads. Minimize disruptions and coordinate with // Resident Engineer Contracting Officer Representative.

    - Egress Routes for Construction Workers: Maintain free and unobstructed egress. Inspect daily. Report findings and corrective actions weekly to Contracting Officer Representative.

    - Fire Extinguishers: Provide and maintain extinguishers in construction areas and temporary storage areas in accordance with 29 CFR 1926, NFPA

241 and NFPA 10.

    - Flammable and Combustible Liquids: Store, dispense and use liquids in accordance with 29 CFR 1926, NFPA 241 and NFPA 30.

    - “MISSING INFORMATION and Letter L”

- Existing Fire Protection: Do not impair automatic sprinklers, smoke and heat detection, and fire alarm systems, except for portions immediately under construction, and temporarily for connections. Provide fire watch for impairments more than 4 hours in a 24-hour period. Request interruptions in accordance with Article, OPERATIONS AND STORAGE AREAS, and coordinate with Safety Personnel. Contracting Officer Representative shall be informed of existing or temporary fire protection systems (fire alarms, sprinklers) located in construction areas shall be tested as coordinated with the medical center. Parameters for the testing and results of any tests performed shall be recorded by the medical center and copies provided to the Resident Engineer.

- Smoke Detectors: Prevent accidental operation. Remove temporary covers at end of work operations each day. Coordinate with // Resident Engineer Contracting Officer Representative.

- Hot Work: Perform and safeguard hot work operations in accordance with NFPA 241 and NFPA 51B. Coordinate with Officer at least 48 hours in

advance. Designate contractor's responsible project-site fire prevention program manager to permit hot work.

- Fire Hazard Prevention and Safety Inspections: Inspect entire construction areas weekly. Coordinate with, and report findings and corrective actions weekly to Contracting Officer Representative .

- Smoking: Smoking is prohibited in and adjacent to construction areas inside existing buildings and additions under construction. In separate and detached buildings under construction, smoking is prohibited except in designated smoking rest areas.

- Dispose of waste and debris in accordance with NFPA 241. Remove from buildings daily.

- If required, submit documentation to the COR that personnel have been trained in the fire safety aspects of working in areas with impaired structural or compartmentalization features.

  - ELECTRICAL

    - All electrical work shall comply with NFPA 70 (NEC), NFPA 70B, NFPA 70E, 29 CFR Part 1910 Subpart J – General Environmental Controls, 29 CFR Part 1910 Subpart S – Electrical, and 29 CFR 1926 Subpart K in addition to other references required by contract.

    - All qualified persons performing electrical work under this contract shall be licensed journeyman or master electricians. All apprentice electricians performing under this contract shall be deemed unqualified persons unless they are working under the immediate supervision of a licensed electrician or master electrician.

    - All electrical work will be accomplished de-energized and in the Electrically Safe Work Condition (refer to NFPA 70E for Work Involving Electrical Hazards, including Exemptions to Work Permit). Any Contractor, subcontractor or temporary worker who fails to fully comply with this requirement is subject to immediate termination in accordance with FAR clause 52.236-5(c). Only in rare circumstances when achieving an electrically safe work condition prior to beginning work would

increase or cause additional hazards or is infeasible due to equipment design or operational limitations is energized work permitted. The Contracting Officer Representative with approval of the Medical Center Director will make the determination if the circumstances would meet the exception outlined above. An AHA and permit specific to energized work activities will be developed, reviewed, and accepted by the VA prior to the start of that activity.

- Development of a Hazardous Electrical Energy Control Procedure is required prior to de-energization. A single Simple Lockout/Tagout Procedure for multiple work operations can only be used for work involving qualified person(s) de-energizing one set of conductors or circuit part source. Task specific Complex Lockout/Tagout Procedures are required at all other times.

- Verification of the absence of voltage after de-energization and lockout/tagout is considered “energized electrical work” (live work) under NFPA 70E, and shall only be performed by qualified persons wearing appropriate shock protective (voltage rated) gloves and arc rate personal protective clothing and equipment, using Underwriters Laboratories (UL) tested and appropriately rated contact electrical testing instruments or equipment appropriate for the environment in which they will be used.

- Personal Protective Equipment (PPE) and electrical testing instruments will be readily available for inspection by the Contracting Officer Representative.

    - Before beginning any electrical work, an Activity Hazard Analysis (AHA) will be conducted to include Shock Hazard and Arc Flash Hazard analyses (NFPA Tables can be used only as a last alterative and it is strongly suggested a full Arc Flash Hazard Analyses be conducted). Work shall not begin until the AHA for the work activity and permit for energized work has been reviewed and accepted by Contracting Officer Representative and discussed with all engaged in the activity, including the Contractor, subcontractor(s), and Government on-site representatives at preparatory and initial control phase meetings.

    - Ground-fault circuit interrupters. GFCI protection shall be provided where an employee is operating or using cord- and plug-connected tools related to construction activity supplied by 125-volt, 15-, 20-, or 30- ampere circuits. Where employees operate or use equipment supplied by greater than 125-volt, 15-, 20-, or 30- ampere circuits, GFCI protection or an assured equipment grounding conductor program shall be implemented in accordance with NFPA 70E - 2015, Chapter 1, Article 110.4(C)(2).

  - FALL PROTECTION

    - The fall protection (FP) threshold height requirement is 4ft for ALL WORK in government occupied sites, unless the OSHA 29 CFR 1926 or EM 385-1-1 requirements are more stringent, to include steel erection activities, systems-engineered activities (prefabricated) metal buildings, residential (wood) construction and scaffolding work. For work occurring at new “greenfield” sites or sites with 24/7 Contractor controlled 100% restricted access, the fall protection (FP) threshold height may be increased to 6ft unless the OSHA 29 CFR 1926 or EM 385-1-

- requirements are more stringent.

- The use of a Safety Monitoring System (SMS) as a fall protection method is prohibited.

- The use of Controlled Access Zone (CAZ) as a fall protection method is prohibited.

- A Warning Line System (WLS) may ONLY be used on floors or flat or low-sloped roofs (between 0 - 18.4 degrees or 4:12 slope) and shall be erected around all sides of the work area (See 29 CFR 1926.502(f) for construction of WLS requirements). Working within the WLS does not require FP. No worker shall be allowed in the area between the roof or floor edge and the WLS without FP. FP is required when working outside the WLS.

- Fall protection while using a ladder will be governed by the more stringent of OSHA and EM 385-1-1 requirements.

  - SCAFFOLDS AND OTHER WORK PLATFORMS

    - All scaffolds and other work platforms construction activities shall comply with 29 CFR 1926 Subpart L.

    - The fall protection (FP) threshold height requirement is 4 ft as stated in Section 1.16.

    - The following hierarchy and prohibitions shall be followed in selecting appropriate work platforms.

      - Scaffolds, platforms, or temporary floors shall be provided for all work except that can be performed safely from the ground or similar footing.

      - Ladders less than 20 feet may be used as work platforms only when use of small hand tools or handling of light material is involved.

      - Ladder jacks, lean-to, and prop-scaffolds are prohibited.

      - Emergency descent devices shall not be used as working platforms.

    - Contractors shall use a scaffold tagging system in which all scaffolds are tagged by the Competent Person. Tags shall be color-coded: green indicates the scaffold has been inspected and is safe to use; red indicates the scaffold is unsafe to use. Tags shall be readily visible, made of materials that will withstand the environment in which they are used, be legible and shall include:

      - The Competent Person’s name and signature;

      - Dates of initial and last inspections.

    - Mast Climbing work platforms: When access ladders, including masts designed as ladders, exceed 20 ft (6 m) in height, positive fall protection shall be used.

  - EXCAVATION AND TRENCHES

    - All excavation and trenching work shall comply with 29 CFR 1926 Subpart

P. Excavations less than 5 feet in depth require evaluation by the contractor’s “Competent Person” (CP) for determination of the necessity

of an excavation protective system where kneeing, laying in, or stooping within the excavation is required.

    - All excavations and trenches 24 inches in depth or greater shall require a written trenching and excavation permit (NOTE – some States and other local jurisdictions require separate state/jurisdiction- issued excavation permits). The permit shall have two sections, one section will be completed prior to digging or drilling and the other will be completed prior to personnel entering the excavations greater than 5 feet in depth. Each section of the permit shall be provided to the Contracting Officer Representative and/or other Government Designated Authority //	prior to proceeding with digging or drilling and prior to proceeding with entering the excavation. After completion of the work and prior to opening a new section of an excavation, the permit shall be closed out and provided to the Contracting Officer Representative. The permit shall be maintained onsite, and the first section of the permit shall include the following:

      - Estimated start time & stop time

      - Specific location and nature of the work.

      - Indication of the contractor’s “Competent Person” (CP) in excavation safety with qualifications and signature. Formal course in excavation safety is required by the contractor’s CP.

      - Indication of whether soil or concrete removal to an offsite location is necessary.

      - Indication of whether soil samples are required to determine soil contamination.

      - Indication of coordination with local authority (i.e. “One Call”) or contractor’s effort to determine utility location with search and survey equipment.

      - Indication of review of site drawings for proximity of utilities to digging/drilling.

    - The second section of the permit for excavations greater than five feet in depth shall include the following:

      - Determination of OSHA classification of soil. Soil samples will be from freshly dug soil with samples taken from different soil type layers as necessary and placed at a safe distance from the excavation by the excavating equipment. A pocket penetrometer will be utilized in determination of the unconfined compression strength of the soil for comparison against OSHA table (Less than 0.5 Tons/FT2 – Type C, 0.5 Tons/FT2 to 1.5 Tons/FT2 – Type B, greater than 1.5 Tons/FT2 – Type A without condition to reduce to Type B).

      - Indication of selected protective system (sloping/benching, shoring, shielding). When soil classification is identified as “Type A” or “Solid Rock”, only shoring or shielding or Professional Engineer designed systems can be used for protection. A Sloping/Benching system may only be used when classifying the soil as Type B or Type

C. Refer to Appendix B of 29 CFR 1926, Subpart P for further information on protective systems designs.

      - Indication of the spoil pile being stored at least 2 feet from the edge of the excavation and safe access being provided within 25 feet of the workers.

      - Indication of assessment for a potential toxic, explosive, or oxygen deficient atmosphere where oxygen deficiency (atmospheres containing less than 19.5 percent oxygen) or a hazardous atmosphere exists or could reasonably be expected to exist. Internal combustion engine equipment is not allowed in an excavation without providing force air ventilation to lower the concentration to below OSHA PELs, providing sufficient oxygen levels, and atmospheric testing as necessary to ensure safe levels are maintained.

C. As required by OSHA 29 CFR 1926.651(b)(1), the estimated location of utility installations, such as sewer, telephone, fuel, electric, water lines, or any other underground installations that reasonably may be expected to be encountered during excavation work, shall be determined prior to opening an excavation.

- The planned dig site will be outlined/marked in white prior to locating the utilities.

- Used of the American Public Works Association Uniform Color Code is required for the marking of the proposed excavation and located utilities.

- 811 will be called two business days before digging on all local or State lands and public Right-of Ways.

- Digging will not commence until all known utilities are marked.

- Utility markings will be maintained

D. Excavations will be hand dug or excavated by other similar safe and acceptable means as excavation operations approach within 3 to 5 feet of identified underground utilities. Exploratory bar or other detection equipment will be utilized as necessary to further identify the location of underground utilities.

E. Excavations greater than 20 feet in depth require a Professional Engineer designed excavation protective system.

# CRANES

    - All crane work shall comply with 29 CFR 1926 Subpart CC and EM 385-1-1.

    - Prior to operating a crane, the operator must be licensed, qualified or certified to operate the crane. Thus, all the provisions contained with Subpart CC are effective and there is no “Phase In” date.

    - A detailed lift plan for all lifts shall be submitted to the Resident Engineer, COR and/or other Government Designated Authority 14 days prior to the scheduled lift complete with route for truck carrying load, crane load analysis, siting of crane and path of swing and all other elements of a critical lift plan where the lift meets the definition of a critical lift. Critical lifts require a more comprehensive lift plan to minimize the potential of crane failure and/or catastrophic loss. The plan must be reviewed and accepted by the General Contractor before being submitted to the VA for review. The

lift will not be allowed to proceed without prior acceptance of this document by the Contracting Officer Representative .

    - Crane operators shall not carry loads

      - over the general public or VAMC personnel

      - over any occupied building unless

- The top two or more floors are vacated under the lift affected area AND a Contractor provided engineering analysis, performed by a Professional Engineer, demonstrates that overhead protection provided by the roof and vacated floors is sufficient to protect against the potential loss of a load being lifted or a minimum of

300 psf of protection is provided, whichever is greater

## OR Overhead protection is designed by a Professional Engineer and installed over the roof by the Contractor to protect the occupants below. The installed system shall be sufficient to protect against the potential loss of a load being lifted or a minimum of 300 psf of protection is provided, whichever is greater.

- OR A formal request may be submitted to the Contracting Officer for documentation, if available, indicating the roof of the building has been previously designed and constructed using a reinforced concrete roof slab or other means to provide overhead protection from construction activities specifically associated with the vertical or horizontal expansion of the same

building AND a Contractor provided engineering analysis, performed by a Professional Engineer, demonstrates that overhead protection provided by the roof is sufficient to protect against the potential loss of a load being lifted or a minimum of 300 psf of protection is provided, whichever is greater.

# CONTROL OF HAZARDOUS ENERGY (LOCKOUT/TAGOUT)

    - All installation, maintenance, and servicing of equipment or machinery shall comply with 29 CFR 1910.147 except for specifically referenced operations in 29 CFR 1926 such as concrete & masonry equipment [1926.702(j)], heavy machinery & equipment [1926.600(a)(3)(i)], and process safety management of highly hazardous chemicals (1926.64). Control of hazardous electrical energy during the installation, maintenance, or servicing of electrical equipment shall comply with Section 1.15 to include NFPA 70E and other VA specific requirements discussed in the section.

# CONFINED SPACE ENTRY

    - All confined space entry shall comply with 29 CFR 1926, Subpart AA except for specifically referenced operations in 29 CFR 1926 such as excavations/trenches [1926.651(g)].

    - A site-specific Confined Space Entry Plan (including permitting process) shall be developed and submitted to the Contracting Officer Representative.

# LADDERS

- All Ladder use shall comply with 29 CFR 1926 Subpart X and EM 385-1-1.

- All portable ladders shall be of sufficient length and shall be placed so that workers will not stretch or assume a hazardous position.

- Manufacturer safety labels shall be in place on ladders

- Step Ladders shall not be used in the closed position

- Top steps or cap of step ladders shall not be used as a step

- Portable ladders, used as temporary access, shall extend at least 3 ft (0.9 m) above the upper landing surface.

  - When a 3 ft (0.9-m) extension is not possible, a grasping device (such as a grab rail) shall be provided to assist workers in mounting and dismounting the ladder.

  - In no case shall the length of the ladder be such that ladder deflection under a load would, by itself, cause the ladder to slip from its support.

- Ladders shall be inspected for visible defects on a daily basis and after any occurrence that could affect their safe use. Broken or damaged ladders shall be immediately tagged "DO NOT USE," or with similar wording, and withdrawn from service until restored to a condition meeting their original design.

# FLOOR & WALL OPENINGS

    - All floor and wall openings shall comply with 29 CFR 1926 Subpart M and EM 385-1-1.

    - Floor and roof holes/openings are any that measure over 2 in (51 mm) in any direction of a walking/working surface which persons may trip or fall into or where objects may fall to the level below. Skylights located in floors or roofs are considered floor or roof hole/openings.

    - All floor, roof openings or hole into which a person can accidentally walk or fall through shall be guarded either by a railing system with toe boards along all exposed sides or a load-bearing cover. When the cover is not in place, the opening or hole shall be protected by a removable guardrail system or shall be attended when the guarding system has been removed, or other fall protection system.

      - Covers shall be capable of supporting, without failure, at least twice the weight of the worker, equipment and material combined.

      - Covers shall be secured when installed, clearly marked with the word “HOLE”, “COVER” or “Danger, Roof Opening-Do Not Remove” or color- coded or equivalent methods (e.g., red or orange “X”). Workers must be made aware of the meaning for color coding and equivalent methods.

      - Roofing material, such as roofing membrane, insulation or felts, covering or partly covering openings or holes, shall be immediately cut out. No hole or opening shall be left unattended unless covered.

      - Non-load-bearing skylights shall be guarded by a load-bearing skylight screen, cover, or railing system along all exposed sides.

      - Workers are prohibited from standing/walking on skylights.

- - - E N D - - -

SECTION 01 42 19 REFERENCE STANDARDS

PART 1 - GENERAL

  - DESCRIPTION

This section specifies the availability and source of references and standards specified in the project manual under paragraphs APPLICABLE PUBLICATIONS and/or shown on the drawings.

  - AVAILABILITY OF SPECIFICATIONS LISTED IN THE GSA INDEX OF FEDERAL SPECIFICATIONS, STANDARDS AND COMMERCIAL ITEM DESCRIPTIONS FPMR PART 101-29 (FAR 52.211-1) (AUG 1998)

    - The GSA Index of Federal Specifications, Standards and Commercial Item Descriptions, FPMR Part 101-29 and copies of specifications, standards, and commercial item descriptions cited in the solicitation may be obtained for a fee by submitting a request to – GSA Federal Supply Service, Specifications Section, Suite 8100, 470 East L’Enfant Plaza, SW, Washington, DC 20407, Telephone (202) 619-8925, Facsimile (202)

619-8978.

    - If the General Services Administration, Department of Agriculture, or Department of Veterans Affairs issued this solicitation, a single copy of specifications, standards, and commercial item descriptions cited in this solicitation may be obtained free of charge by submitting a request to the addressee in paragraph (a) of this provision. Additional copies will be issued for a fee.

  - AVAILABILITY FOR EXAMINATION OF SPECIFICATIONS NOT LISTED IN THE GSA INDEX OF FEDERAL SPECIFICATIONS, STANDARDS AND COMMERCIAL ITEM DESCRIPTIONS (FAR 52.211-4) (JUN 1988)

The specifications and standards cited in this solicitation can be examined at the following location:

DEPARMENT OF VETERANS AFFAIRS

Office of Construction & Facilities Management Facilities Quality Service (00CFM1A)

425 Eye Street N.W, (sixth floor) Washington, DC 20001

Telephone Numbers: (202) 632-5249 or (202) 632-5178

Between 9:00 AM - 3:00 PM

  - AVAILABILITY OF SPECIFICATIONS NOT LISTED IN THE GSA INDEX OF FEDERAL SPECIFICATIONS, STANDARDS AND COMMERCIAL ITEM DESCRIPTIONS (FAR 52.211-3) (JUN 1988)

The specifications cited in this solicitation may be obtained from the associations or organizations listed below.

AA	Aluminum Association Inc. http://www.aluminum.org

AABC	Associated Air Balance Council https://www.aabc.com

AAMA	American Architectural Manufacturer's Association http://www.aamanet.org

AASHTO	American Association of State Highway and Transportation Officials

http://www.aashto.org

AATCC	American Association of Textile Chemists and Colorists http://www.aatcc.org

ACGIH	American Conference of Governmental Industrial Hygienists http://www.acgih.org

ACI	American Concrete Institute http://www.aci-int.net

ACPA	American Concrete Pipe Association http://www.concrete-pipe.org

ACPPA	American Concrete Pressure Pipe Association http://www.acppa.org

ADC	Air Diffusion Council http://flexibleduct.org

AGA	American Gas Association http://www.aga.org

AGC	Associated General Contractors of America http://www.agc.org

AGMA	American Gear Manufacturers Association, Inc. http://www.agma.org

AH	American Hort https://www.americanhort.org

AHAM	Association of Home Appliance Manufacturers http://www.aham.org

AIA	American Institute of Architects http://www.aia.org

AISC	American Institute of Steel Construction http://www.aisc.org

AISI	American Iron and Steel Institute http://www.steel.org

AITC	American Institute of Timber Construction https://aitc-glulam.org

AMCA	Air Movement and Control Association, Inc. http://www.amca.org

ANSI	American National Standards Institute, Inc. http://www.ansi.org

APA	The Engineered Wood Association http://www.apawood.org

ARI	Air-Conditioning and Refrigeration Institute http://www.ari.org

ARPM	Association for Rubber Product Manufacturers https://arpm.com

ASABE	American Society of Agricultural and Biological Engineers https://www.asabe.org

ASCE	American Society of Civil Engineers http://www.asce.org

ASHRAE	American Society of Heating, Refrigerating, and Air-Conditioning Engineers http://www.ashrae.org

ASME	American Society of Mechanical Engineers http://www.asme.org

ASSE	American Society of Sanitary Engineering International http://www.asse-plumbing.org

ASTM	American Society for Testing and Materials International http://www.astm.org

AWI	Architectural Woodwork Institute https://www.awinet.org

AWS	American Welding Society https://www.aws.org

AWWA	American Water Works Association https://www.awwa.org

BHMA	Builders Hardware Manufacturers Association https://www.buildershardware.com

BIA	The Brick Industry Association http://www.gobrick.com

CAGI	Compressed Air and Gas Institute https://www.cagi.org

CGA	Compressed Gas Association, Inc. https://www.cganet.com

CI	The Chlorine Institute, Inc. https://www.chlorineinstitute.org

CISCA	Ceilings and Interior Systems Construction Association https://www.cisca.org

CISPI	Cast Iron Soil Pipe Institute https://www.cispi.org

CLFMI	Chain Link Fence Manufacturers Institute https://www.chainlinkinfo.org

CPA	Composite Panel Association https://www.compositepanel.org

CPMB	Concrete Plant Manufacturers Bureau https://www.cpmb.org

CRA	California Redwood Association http://www.calredwood.org

CRSI	Concrete Reinforcing Steel Institute https://www.crsi.org

CTI	Cooling Technology Institute https://www.cti.org

DHA	Decorative Hardwoods Association https://www.decorativehardwoods.org

DHI	Door and Hardware Institute https://www.dhi.org

EGSA	Electrical Generating Systems Association http://www.egsa.org

EEI	Edison Electric Institute https://www.eei.org

EPA	United States Environmental Protection Agency https://www.epa.gov

ETL	ETL Testing Services http://www.intertek.com

FAA	Federal Aviation Administration https://www.faa.gov

FCC	Federal Communications Commission https://www.fcc.gov

FPS	Forest Products Society http://www.forestprod.org

GANA	Glass Association of North America http://www.glasswebsite.com

FM	Factory Mutual Global Insurance https://www.fmglobal.com

GA	Gypsum Association https://gypsum.org

GSA	General Services Administration https://www.gsa.gov

HI	Hydraulic Institute http://www.pumps.org

ICC	International Code Council https://shop.iccsafe.org

ICEA	Insulated Cable Engineers Association https://www.icea.net

ICAC	Institute of Clean Air Companies http://www.icac.com

IEEE	Institute of Electrical and Electronics Engineers https://www.ieee.org\

IGMA	Insulating Glass Manufacturers Alliance https://www.igmaonline.org

IMSA	International Municipal Signal Association http://www.imsasafety.org

MBMA	Metal Building Manufacturers Association https://www.mbma.com

MSS	Manufacturers Standardization Society of the Valve and Fittings Industry

http://msshq.org

NAAMM	National Association of Architectural Metal Manufacturers https://www.naamm.org

PHCC	Plumbing-Heating-Cooling Contractors Association https://www.phccweb.org

NBS	National Bureau of Standards See - NIST

NBBI	The National Board of Boiler and Pressure Vessel Inspectors https://www.nationalboard.org

NEC	National Electric Code

See - NFPA National Fire Protection Association

NEMA	National Electrical Manufacturers Association https://www.nema.org

NFPA	National Fire Protection Association https://www.nfpa.org

NHLA	National Hardwood Lumber Association https://www.nhla.com

NIH	National Institute of Health https://www.nih.gov

NIST	National Institute of Standards and Technology https://www.nist.gov

NELMA	Northeastern Lumber Manufacturers Association, Inc. http://www.nelma.org

NPA	National Particleboard Association (See CPA, Composite Panel Association)

NSF	National Sanitation Foundation http://www.nsf.org

OSHA	Occupational Safety and Health Administration Department of Labor

https://www.osha.gov

PCA	Portland Cement Association https://www.cement.org

PCI	Precast Prestressed Concrete Institute https://www.pci.org

PPI	Plastics Pipe Institute https://www.plasticpipe.org

PEI	Porcelain Enamel Institute http://www.porcelainenamel.com

PTI	Post-Tensioning Institute http://www.post-tensioning.org

RFCI	Resilient Floor Covering Institute https://www.rfci.com

RIS	Redwood Inspection Service

(See Western Wood Products Association) https://www.wwpa.org

SCMA	Southern Cypress Manufacturers Association http://www.cypressinfo.org

SDI	Steel Door Institute http://www.steeldoor.org

SJI	Steel Joist Institute https://www.steeljoist.org

SMACNA	Sheet Metal & Air-Conditioning Contractors’

National Association https://www.smacna.org

SSPC	The Society for Protective Coatings https://www.sspc.org

STI	Steel Tank Institute https://www.steeltank.com

SWI	Steel Window Institute https://www.steelwindows.com

TCNA	Tile Council of North America https://www.tcnatile.com

TEMA	Tubular Exchanger Manufacturers Association http://www.tema.org

TPI	Truss Plate Institute https://www.tpinst.org

UBC	The Uniform Building Code (See ICC)

UL	Underwriters' Laboratories Incorporated https://www.ul.com

ULC	Underwriters' Laboratories of Canada https://www.ulc.ca

WCLB	West Coast Lumber Inspection Bureau http://www.wclib.org

WDMA	Window and Door Manufacturers Association https://www.wdma.com

WRCLA	Western Red Cedar Lumber Association https://www.realcedar.com

WWPA	Western Wood Products Association http://www.wwpa.org

- - - E N D - - -

SECTION 01 45 00 QUALITY CONTROL

PART 1 - GENERAL

  - DESCRIPTION

This section specifies requirements for Contractor Quality Control (CQC) for Design-Bid-Build (DBB) or Design-Build (DB) construction projects. This section can be used for both project types.

  - APPLICABLE PUBLICATIONS

    - The publication listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

    - ASTM International (ASTM)

      - D3740 - (2012a) Minimum Requirements for Agencies Engaged in the Testing and/or Inspection of Soil and Rock as Used in Engineering Design and Construction

      - E329 - (2014a) Standard Specification for Agencies Engaged in the Testing and/or Inspection of Materials Used in Construction

  - SUBMITTALS

Government approval is required for all submittals. CQC inspection reports shall be submitted under this Specification section and follow the naming convention.

- Preconstruction Submittals

  - Interim CQC Plan

  - CQC Plan

  - Additional Requirements for Design Quality Control (DQC) Plan

- Design Data

  - Discipline-Specific Checklists

  - Design Quality Control

- Test Reports

  - Verification Statement

PART 2 PRODUCTS – NOT USED PART 3 - EXECUTION

  - GENERAL REQUIREMENTS

Establish and maintain an effective quality control (QC) system. that complies with the FAR Clause 52.246.12 titled “Inspection of Construction”. QC consists of plans, procedures, and organization necessary to produce an end product which complies with the Contract requirements. The QC system covers all design and construction operations, both onsite and offsite, and be keyed to the proposed design and construction sequence. The project superintendent will be held responsible for the quality of work and is subject to removal by the Contracting Office or Authorized designee for non-compliance with the quality requirements specified in the Contract. In this context the highest level manager responsible for the overall construction activities at the site, including quality and production is the project superintendent. The project superintendent maintains a physical presence at the site at all times and is responsible for all construction and related activities at the site, except as otherwise acceptable to the Contracting Officer.

  - CQC PLAN:

    - Submit the CQC Plan no later than CO or Designee to determine during Constructability review – 30days after receipt of Notice to Proceed (NTP) proposed to implement the requirements of the FAR Clause 52.246.12 titled “Inspection of Construction”. The Government will consider an Interim CQC Plan for the first to match timeline established immediately above 30 days of operation, which must be accepted within 20 business days of NTP. Design and/or construction will be permitted to begin only after acceptance of the CQC Plan or acceptance of an Interim plan applicable to the particular feature of work to be started. Work outside of the accepted Interim CQC Plan will not be permitted to begin until acceptance of a CQC Plan or another Interim CQC Plan containing the additional work scope is accepted.

    - Content of the CQC Plan: Include, as a minimum, the following to cover all design and construction operations, both onsite and offsite,

including work by subcontractors, designers of record consultants, architects/engineers (A/E), fabricators, suppliers, and purchasing agents:

      - A description of the QC organization, including a chart showing lines of authority and acknowledgement that the CQC staff will implement the three phase control system for all aspects of the work specified. Include a CQC System Manager that reports to the project superintendent.

      - The name, qualifications (in resume format) duties, responsibilities, and authorities of each person assigned a CQC function.

      - A copy of the letter to the CQC System Manager signed by an authorized official of the firm which describes the responsibilities and delegates sufficient authorities to adequately perform the functions of the CQC System Manager, including authority to stop work which is not in compliance with the Contract. Letters of direction to all other various quality control representatives outlining duties, authorities, and responsibilities will be issued by the CQC System Manager. Furnish copies of these letters to the Contracting Officer or Authorized designee.

      - Procedures for scheduling, reviewing, certifying, and managing submittals including those of subcontractors, designers of record, consultants, A/E’s offsite fabricators, suppliers and purchasing agents. These procedures must be in accordance with Section 01 33 23 Shop Drawings, Product Data, and Samples.

      - Control, verification, and acceptance of testing procedures for each specific test to include the test name, specification paragraph requiring test, feature of work to be tested, test frequency, and person responsible for each test. (Laboratory facilities approved by the Contracting Officer or Authorized designee are required to be used)

      - Procedures for tracking Preparatory, Initial, and Follow-Up control phases and control, verification, and acceptance tests including documentation.

      - Procedures for tracking design and construction deficiencies from identification through acceptable corrective action. Establish verification procedures that identified deficiencies have been corrected.

      - Reporting procedures, including proposed reporting formats.

      - A list of the definable features of work. A definable feature of work is a task which is separate and distinct from other tasks has separate control requirements, and is identified by different trades or disciplines, or it is work by the same trade in a different environment. Although each section of specifications can generally be considered as a definable feature of work, there are frequently more than one definable feature under a particular section. This list will be agreed upon during the Coordination meeting.

      - Coordinate schedule work with Special Inspections required by Section 01 45 35 Special Inspections, the Statement of Special Inspections and Schedule of Special Inspections. Where the applicable Code issue by the International Code Council (ICC) calls for inspections by the Building Official, the Contractor must include the inspections in the CQC Plan and must perform the inspections required by the applicable ICC. The Contractor must perform these inspections using independent qualified inspectors. Include the Special Inspection Plan requirements in the CQC Plan.

    - Additional Requirements for Design Quality Control (DQC) Plan: The following additional requirements apply to the DQC Plan for DB projects only and not DBB projects:

      - Submit and maintain a DQC Plan as an effective QC program which assures that all services required by this contract are performed and provided in a manner that meets professional architectural and engineering quality standards. As a minimum, all documents must be technically reviewed by competent, independent reviewers identified in the DQC Plan. The same element that produced the product may not perform the independent technical review (ITR). Correct errors and deficiencies in the design documents prior to submitting them to the Government.

      - Include the design schedule in the master project schedule, showing the sequence of events involved in carrying out the project design tasks within the specific Contract period. This should be at a detailed level of scheduling sufficient to identify all major design tasks, including those that control the flow of work. Include review and correction periods associated with each item. This should be a forward planning as well as a project monitoring tool. The schedule reflects calendar days and not dates for each activity. If the schedule is changed, submit a revised schedule reflecting the change within 7 calendar days. Include in the DQC Plan the discipline- specific checklists to be used during the design and quality control of each submittal. Submit at each design phase as part of the project documentation these completed discipline-specific checklists.

      - Implement the DQC Plan by a DQC Manager who has the responsibility of being cognizant of and assuring that all documents on the project have been coordinated. This individual must be a person who has verifiable engineering or architectural design experience and is a Professional Engineer or Registered Architect within the state of Construction location. Notify the Contracting Officer or Authorized designee, in writing, of the name of the individual, and the name of an alternate person assigned to the position.

    - Acceptance of Plan: Acceptance of the Contractor’s plan is required prior to the start of design and construction. Acceptance is conditional and will be predicated on satisfactory performance during the design and construction. The Government reserves the right to require the Contractor to make changes in the CQC Plan and operations including removal of personnel as necessary, to obtain the quality specified.

    - Notification of Changes: After acceptance of the CQC Plan, notify the Contracting Officer or Authorized designee in writing of any proposed change. Proposed changes are subject to acceptance by the Government prior to implementation by the Contractor.

  - COORDINATION MEETING:

After the Preconstruction Conference Post-award Conference before start of design or construction, and prior to acceptance by the Government of the CQC Plan, meet with the Contracting Officer or Authorized designee to discuss the Contractor’s quality control system. Submit the CQC Plan a minimum of 5 business days prior to the Coordination Meeting. During the meeting, a mutual understanding of the system details must be developed, including the forms for recording the CC operations, design activities (if applicable), control activities, testing, administration of the system for both onsite and offsite work, and the interrelationship of Contractor’s Management and control with the Government’s Quality Assurance. Minutes of the meeting will be prepared by the Government, signed by both the Contractor and Contracting Officer or Authorized designee and will become a part of the contract file. There can be occasions when subsequent conferences will be called by either party to reconfirm mutual understandings or address deficiencies in the CQC system or procedures which can require corrective action by the Contractor.

  - QUALITY CONTROL ORGANIZATION:

    - Personnel Requirements: The requirements for the CQC organization are a Safety and Health Manager, CQC System Manager, a Design Quality Manager (if applicable), and sufficient number of additional qualified personnel to ensure safety and Contract compliance. The Safety and Health Manager shall satisfy the requirements of Specification 01 35 26 Safety Requirements and reports directly to a senior project (or corporate) official independent from the CQC System Manager. The Safety and Health Manager will also serve as a member of the CQC Staff. Personnel identified in the technical provisions as requiring specialized skills to assure the required work is being performed properly will also be included as part of the CQC organization. The Contractor’s CQC staff maintains a presence at the site at all times during progress of the work and have complete authority and responsibility to take any action necessary to ensure Contract compliance. The CQC staff will be subject to acceptance by the Contracting Officer or Authorized designee. Provide adequate office

space, filing systems, and other resources as necessary to maintain an effective and fully functional CQC organization. Promptly complete and furnish all letters, material submittals, shop drawings submittals, schedules and all other project documentation to the CQC organization. The CQC organization is responsible to maintain these documents and records at the site at all times, except as otherwise acceptable to the Government.

    - CQC System Manager: Identify as CQC System Manager an individual within the onsite work organization that is responsible for overall management of CQC and has the authority to act in all CQC matters for the Contractor. The CQC system Manager is required to be construction person with a minimum of PM or SRE to determine qualifications based on project complexity at construction review (5) fiveyears in related work. The CQC System Manger is assigned as CQC System Manager but has duties as project superintendent in addition to quality control. Identify in the plan an alternate to serve in the event of the CDQC System Manager’s absence. The requirements for the alternate are the same as the CQC System Manager.

    - CQC Personnel: In addition to CQC personnel specified elsewhere in the contract, provide as part of the CQC organization specialized personnel to assist in the CQC System Manager for the following areas, as applicable: electrical, environmental, materials technician submittals clerk, and low voltage systems. These individuals or specified technical companies are employees of the prime or subcontractor; be responsible to the CQC System Manager; be physically present at the construction site during work on the specialized personnel’s areas of responsibility; have the necessary education or experience in accordance with the Experience Matrix listed herein. These individuals can perform other duties but need to be allowed sufficient time to perform the specialized personnel’s assigned quality controls duties as described in the CQC Plan. A single person can cover more than one area provided that the single person is qualified to perform QC activities in each designated and that workload allows.

EXPERIENCE MATRIX

| Area | Qualifications |
| --- | --- |
| Electrical | Graduate Electrical Engineer with 2 years related experience or construction professional with 5 years of experience supervising electrical features of work in the field with a construction company. |
| Environmental | Graduate Environmental Engineer with 3 years experience. |
| Submittals | Submittal Clerk with 1 year experience. |
| Concrete, Pavement, and Soils | Materials Technician with 2 years experience for the appropriate area. |

    - Additional Requirements: In addition to the above experience and education requirements, the CQC System Manager and Alternate CQC System Manager are required to have completed the Construction Quality Management (CQM) for Construction course. If the CQC System Manager does not have a current specification, obtain the CQM for Contractors

course identification within 90 days of award. This course is periodically offered by the Naval Facilities Engineering Command and the Army Corps of Engineers. Contact the Contracting Officer or Authorized designee for information on the next scheduled class.

    - Organizational Changes: Maintain the CQC staff at full strength at all times. When it is necessary to make changes to the CQC staff, revise the CQC Plan to reflect the changes and submit the changes to the Contracting Officer or Authorized designee for acceptance.

  - SUBMITTALS AND DELIVERABLES: Submittals have to comply with the requirements in Section 01 33 23 Shop Drawings, Product Data, and Samples. The CQC organization is responsible for certifying that all submittals and deliverables are in compliance with the contract requirements. When Section 01 91 00 General Commissioning Requirements is included in the contract, the submittals required by the section have to be coordinated with the Section 01 33 23 Shop Drawings, Product Data, and Samples to ensure adequate time is allowed for each type of submittal required.

  - CONTROL:

    - CQC is the means by which the Contractor ensures that the construction, to include that of subcontractors and suppliers, complies with the requirements of the contract. At least three phases of control are required to be conducted by the CQC System Manager for each definable feature of the construction work as follows:

      - Preparatory Phase: This phase is performed prior to beginning work on each definable feature of work after all required plans/documents/materials are approved/accepted, and after copies are at the work site. This phase includes:

        - A review of each paragraph of applicable specifications, references codes, and standards. Make available during the preparatory inspection a copy of those sections of referenced codes and standards applicable to that portion of the work to be accomplished in the field. Maintain and make available in the field for use by Government personnel until final acceptance of the work.

        - Review of the Contract drawings.

        - Check to assure that all materials and equipment have been tested, submitted, and approved.

        - Review of provisions that have been made to provide required control inspection and testing.

        - Review Special Inspections required by Section 01 45 35 Special Inspections, that Statement of Special Inspections and the Schedule of Specials Inspections.

        - Examination of the work area to assure that all required preliminary work has been completed and is in compliance with the Contract.

        - Examination of required materials, equipment, and sample work to assure that they are on hand conform to approved shop drawings or submitted data, and are properly stored.

        - Review of the appropriate Activity Hazard Analysis (AHA) to assure safety requirements are met.

        - Discussion of procedures for controlling quality of the work including repetitive deficiencies. Document construction tolerances and workmanship standards – contract defined or industry standard if not contract defined - for that feature of work.

        - Check to ensure that the portion of the plan for the work to be performed has been accepted by the Contracting Officer.

        - Discussion of the initial control phase.

        - The Government needs to be notified at least 48 hours or 2 business days in advance of beginning the Preparatory control phase. Include a meeting conducted by the CQC System Manager and attended by the superintendent, other CQC personnel (as applicable), and the foreman responsible for the definable feature. Document the results of the Preparatory phase actions by separate minutes prepared by the CQC System Manager and attach to the daily CQC report. Instruct applicable workers as to the acceptable level of workmanship required in order to meet contract specifications.

    - Initial Phase: This phase is accomplished at the beginning of a definable feature of work. Accomplish the following:

      - Check work to ensure that it is in full compliance with contract requirements. Review minutes of the Preparatory meeting.

      - Verify adequacy of controls to ensure full contract compliance. Verify the required control inspection and testing is in compliance with the contract.

      - Establish level of workmanship and verify that it meets minimum acceptable workmanship standards. Compare with required sample panels as appropriate.

      - Resolve all differences.

      - Check safety to include compliance with an upgrading of the safety plan and activity hazard analysis. Review the activity analysis with each worker.

      - The Government needs to be notified at least 48 hours or 2 business days in advance of beginning the initial phase for definable features of work. Prepare separate minutes of this phase by the CQC System Manager and attach to the daily CQC report. Indicate the exact location of initial phase for definable feature of work for future reference and comparison with Follow-Up phases.

      - The initial phase for each definable feature of work is repeated for each new crew to work onsite, or any time acceptable specified quality standards are not being met.

      - Coordinate scheduled work with Special Inspections required by Section 01 45 35 Special Inspections, the Statement of Special Inspections, and the Schedule of Special Inspections.

    - Follow-Up Phase: Perform daily checks to assure control activities, including control testing, are providing continued compliance with contract requirements until the completion of the particular feature of work. Record the checks in the CQC documentation. Conduct final Follow- Up checks and correct all deficiencies prior to the start of additional features of work which may be affected by the deficient work. Do not build upon nor conceal non-conforming work. Coordinate scheduled work with Special Inspections required by Section 01 45 35 Special Inspections, the Statement of Special Inspections, and the Schedule of Special Inspections

    - Additional Preparatory and Initial Phases on the same definable features of work if: the quality ongoing work is unacceptable; if there are changes in the applicable CQC staff, onsite production supervision or work crew; if work on a definable feature is resumed after a substantial period of inactivity, or if other problems develop.

  - TESTS

    - Testing Procedure: Perform specified or required tests to verify that control measures are adequate to provide a product which conforms to contract requirements. Upon request, furnish to the Government duplicate samples of test specimens for possible testing by the Government. Testing includes operation and acceptance test when specified. Procure the services of a Department of Veteran Affairs approved testing laboratory or establish an approved testing laboratory at the project site. Perform the following activities and record and provide the following data:

      - Verify that testing procedures comply with contract requirements.

      - Verify that facilities and testing equipment are available and comply with testing standards.

      - Check test instrument calibration data against certified standards.

      - Verify that recording forms and test identification control number system, including all of the test documentation requirements, have been prepared.

      - Record results of all tests taken, both passing and failing on the CQC report for the date taken. Specification paragraph reference, location where tests were taken, and the unique sequential control number identifying the test. If approved by the Contracting Officer or Authorized designee, actual test reports are submitted later with a reference to the test number and date taken. Provide an information copy of tests performed by an offsite or commercial test facility directly to the Contracting Officer or Authorized designee. Failure to submit timely test reports as stated results in nonpayment for related work performed and disapproval of the test facility for this Contract.

    - Testing Laboratories: All testing laboratories must be validated through the procedures contained in Specification section 01 45 29 Testing Laboratory Services.

      - Capability Check: The Government reserves the right to check laboratory equipment in the proposed laboratory for compliance with the standards set forth in the contract specifications and to check the laboratory technician’s testing procedures and techniques. Laboratories utilized for testing soils, concrete, asphalt and steel is required to meet criteria detailed in ASTM D3740 and ASTM E329.

      - Capability Recheck: If the selected laboratory fails the capability check, the Contractor will be assessed a charge equal to value of recheck to reimburse the Government for each succeeding recheck of the laboratory or the checking of a subsequently selected laboratory. Such costs will be deducted from the Contract amount due the Contractor.

    - Onsite Laboratory: The Government reserves the right to utilize the Contractor’s control testing laboratory and equipment to make assurance tests, and to check the Contractor’s testing procedures, techniques, and test results at no additional cost to the Government.

  - COMPLETION INSPECTION

    - Punch-Out Inspection: Conduct an inspection of the work by the CQC system Manager near the end of the work, or any increment of the work established by the specifications. Prepare and include in the CQC documentation a punch list of items which do not conform to the approved drawings and specifications. Include within the list of deficiencies the estimated date by which the deficiencies will be corrected. Make a second inspection the CQC System Manager or staff to ascertain that all deficiencies have been corrected. Once this is accomplished, notify the Government that the facility is ready for the Government Pre-Final Inspection.

    - Pre-Final Inspection: The Government will perform the Pre-Final Inspection to verify that the facility is complete and ready to be occupied. A Government Pre-Final Punch List may be developed as a result of this inspection. Ensure that all items on this list have been corrected before notifying the Government, so that a Final Acceptance

Inspection with the customer can be scheduled. Correct any items noted on the Pre-Final Inspection in a timely manner. These inspections and any deficiency corrections required by this paragraph need to be accomplished within the time slated for completion of the entire work or any particular increment of the work if the project is divided into increments by separate construction completion dates.

    - Final Acceptance Inspection: The Contractor’s QC Inspection personnel, plus the superintendent or other primary management person, and the Contracting Officer’s Authorized designee is required to be in attendance at the Final Acceptance Inspection. Additional Government personnel can also be in attendance. The Final Acceptance Inspection

will be formally scheduled by the Contracting Officer’s or Authorized designee based upon results of the Pre-Final Inspection. Notify the Contracting Officer through the Resident Engineer office at least 14 days prior to the Final Acceptance Inspection and include the Contractor’s assurance that all specific items previously identified to the Contractor as being unacceptable, along with all remaining work performed under the contract, will be complete and acceptable by the date schedule for the Final Acceptance Inspection. Failure of the Contractor to have all contract work acceptably complete for this inspection will be cause for the Contracting Officer to bill the Contractor for the Government’s additional inspection cost in accordance with FAR Clause 52.246-12 titled “Inspection of Construction”.

  - DOCUMENTATION

    - Quality Control Activities: Maintain current records providing factual evidence that required QC activities and tests have been performed. Include in these records the work of subcontractors and suppliers on an acceptable form that includes, as a minimum, the following information:

      - The name and area of responsibility of the Contractor/Subcontractor

      - Operating plant/equipment with hours worked, idle, or down for repair.

      - Work performed each day, giving location, description, and by whom. When Network Analysis (NAS) is used, identify each phase of work performed each day by NAS activity number.

      - Test and control activities performed with results and references to specification/drawing requirements. Identify the Control Phase (Preparatory, Initial, and/or Follow-Up). List deficiencies noted, along with corrective action.

      - Quantity of materials received at the site with statement as to acceptability, storage, and reference to specification/drawing requirements.

      - Submittals and deliverables reviewed, with Contract reference, by whom, and action taken.

      - Offsite surveillance activities, including actions taken.

      - Job safety evaluations stating what was checked, results, and instructions or corrective actions.

      - Instructions given/received and conflicts in plans and specifications.

      - Provide documentation of design quality control activities. For independent design reviews, provide, as a minimum, identification of the Independent Technical Reviewer (ITR) team, the ITR review comments, responses, and the record of resolution of the comments.

    - Verification Statement: Indicate a description of trades working on the project; the number of personnel working; weather conditions encountered; and any delays encountered. Cover both conforming and deficient features and include a statement that equipment and materials incorporated in the work and workmanship comply with the Contract. Furnish the original and one copy of these records in report form to the Government daily with 1 week after the date covered by the report, except that reports need not be submitted for days on which no work is performed. As a minimum, prepare and submit on report for every 7 days of no work and on the last day of a no work period. All calendar days need to be accounted for throughout the life of the contract. The first report following a day of no work will be for that day only. Reports need to be signed and dated by the CQC System Manager. Include copies of test reports and copies of reports prepared by all subordinate QC personnel within the CQC System Manager Report.

  - SAMPLE FORMS

Templates of various quality control reports can be found on the Whole Building Design Guide website at https://www.wbdg.org/FFC/NAVGRAPH/ 01%2045%2000.00%2020_quality_control_reports.pdf

  - NOTIFICATION OF NONCOMPLIANCE: The Contracting Officer or Authorized designee will notify the Contractor of any detected noncompliance with the foregoing requirements. The Contractor should take immediate corrective action after receipt of such notice. Such notice, when delivered to the Contractor at the work site will be deemed sufficient for the purpose of notification. If the Contractor fails or refuses to comply promptly, the Contracting Officer can issue an order stopping all or part of the work until satisfactory corrective action has been taken. No part of the time lost due to such stop orders will be made the subject of claim for extension of time or for excess costs or damages by the Contractor.

--- End of Section ---

SECTION 01 45 29 TESTING LABORATORY SERVICES

PART 1 - GENERAL

  - DESCRIPTION:

This section specifies materials testing activities and inspection services required during project construction to be provided by a Testing Laboratory retained by the General Contractor.

  - APPLICABLE PUBLICATIONS:

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to in the text by the basic designation only.

    - American Association of State Highway and Transportation Officials (AASHTO):

T27-11 .................Standard Method of Test for Sieve Analysis of

Fine and Coarse Aggregates

T96-02 (R2006) .........Standard Method of Test for Resistance to

Degradation of Small-Size Coarse Aggregate by Abrasion and Impact in the Los Angeles Machine

T99-10 .................Standard Method of Test for Moisture-Density

Relations of Soils Using a 2.5 Kg (5.5 lb.) Rammer and a 305 mm (12 in.) Drop

T104-99 (R2007) ........Standard Method of Test for Soundness of

Aggregate by Use of Sodium Sulfate or Magnesium Sulfate

T180-10 ................Standard Method of Test for Moisture-Density

Relations of Soils using a 4.54 kg (10 lb.) Rammer and a 457 mm (18 in.) Drop

T191-02(R2006) .........Standard Method of Test for Density of Soil In-

Place by the Sand-Cone Method

T310-13 ................Standard Method of Test for In-place Density

and Moisture Content of Soil and Soil-aggregate by Nuclear Methods (Shallow Depth)

    - American Concrete Institute (ACI):

506.4R-94 (R2004) ......Guide for the Evaluation of Shotcrete

    - American Society for Testing and Materials (ASTM):

A370-12 ................Standard Test Methods and Definitions for

Mechanical Testing of Steel Products A416/A416M-10 ..........Standard Specification for Steel Strand,

Uncoated Seven-Wire for Prestressed Concrete C31/C31M-10 ............Standard Practice for Making and Curing

Concrete Test Specimens in the Field

C33/C33M-11a ...........Standard Specification for Concrete Aggregates C39/C39M-12 ............Standard Test Method for Compressive Strength

of Cylindrical Concrete Specimens

C109/C109M-11b .........Standard Test Method for Compressive Strength

of Hydraulic Cement Mortars

C136-06 ................Standard Test Method for Sieve Analysis of Fine

and Coarse Aggregates

C138/C138M-10b .........Standard Test Method for Density (Unit Weight),

Yield, and Air Content (Gravimetric) of Concrete

C140-12 ................Standard Test Methods for Sampling and Testing

Concrete Masonry Units and Related Units C143/C143M-10a .........Standard Test Method for Slump of Hydraulic

Cement Concrete

C172/C172M-10 ..........Standard Practice for Sampling Freshly Mixed

Concrete

C173/C173M-10b .........Standard Test Method for Air Content of freshly

Mixed Concrete by the Volumetric Method C330/C330M-09 ..........Standard Specification for Lightweight

Aggregates for Structural Concrete C567/C567M-11 ..........Standard Test Method for Density Structural

Lightweight Concrete

C780-11 ................Standard Test Method for Pre-construction and

Construction Evaluation of Mortars for Plain and Reinforced Unit Masonry

C1019-11 ...............Standard Test Method for Sampling and Testing

Grout

C1064/C1064M-11 ........Standard Test Method for Temperature of Freshly

Mixed Portland Cement Concrete

C1077-11c ..............Standard Practice for Agencies Testing Concrete

and Concrete Aggregates for Use in Construction and Criteria for Testing Agency Evaluation

C1314-11a ..............Standard Test Method for Compressive Strength

of Masonry Prisms

D422-63(2007) ..........Standard Test Method for Particle-Size Analysis

of Soils

D698-07e1 ..............Standard Test Methods for Laboratory Compaction

Characteristics of Soil Using Standard Effort D1140-00(2006) .........Standard Test Methods for Amount of Material in

Soils Finer than No. 200 Sieve D1143/D1143M-07e1 ......Standard Test Methods for Deep Foundations

Under Static Axial Compressive Load

D1188-07e1 .............Standard Test Method for Bulk Specific Gravity

and Density of Compacted Bituminous Mixtures Using Coated Samples

D1556-07 ...............Standard Test Method for Density and Unit

Weight of Soil in Place by the Sand-Cone Method D1557-09 ...............Standard Test Methods for Laboratory Compaction

Characteristics of Soil Using Modified Effort (56,000ft lbf/ft3 (2,700 KNm/m3))

D2166-06 ...............Standard Test Method for Unconfined Compressive

Strength of Cohesive Soil

D2167-08) ..............Standard Test Method for Density and Unit

Weight of Soil in Place by the Rubber Balloon Method

D2216-10 ...............Standard Test Methods for Laboratory

Determination of Water (Moisture) Content of Soil and Rock by Mass

D2974-07a ..............Standard Test Methods for Moisture, Ash, and

Organic Matter of Peat and Other Organic Soils D3666-11 ...............Standard Specification for Minimum Requirements

for Agencies Testing and Inspecting Road and Paving Materials

D3740-11 ...............Standard Practice for Minimum Requirements for

Agencies Engaged in Testing and/or Inspection

of Soil and Rock as used in Engineering Design and Construction

D6938-10 ...............Standard Test Method for In-Place Density and

Water Content of Soil and Soil-Aggregate by Nuclear Methods (Shallow Depth)

E94-04(2010) ...........Standard Guide for Radiographic Examination E164-08 ................Standard Practice for Contact Ultrasonic

Testing of Weldments

E329-11c ...............Standard Specification for Agencies Engaged in

Construction Inspection, Testing, or Special Inspection

E543-09 ................Standard Specification for Agencies Performing Non-Destructive Testing

E605-93(R2011) .........Standard Test Methods for Thickness and Density

of Sprayed Fire Resistive Material (SFRM) Applied to Structural Members

E709-08 ................Standard Guide for Magnetic Particle Examination

E1155-96(R2008) ........Determining FF Floor Flatness and FL Floor Levelness Numbers

F3125/F3125M-15 ........Standard Specification for High Strength

Structural Bolts, Steel and Alloy Steel, Heat Treated, 120 ksi (830 MPa) and 150 ksi (1040 MPa) Minimum Tensile Strength, Inch and Metric Dimensions

    - American Welding Society (AWS):

D1.D1.1M-10 ............Structural Welding Code-Steel

  - REQUIREMENTS:

    - Accreditation Requirements: Construction materials testing laboratories must be accredited by a laboratory accreditation authority and will be required to submit a copy of the Certificate of Accreditation and Scope of Accreditation. The laboratory’s scope of accreditation must include the appropriate ASTM standards (i.e.; E329, C1077, D3666, D3740, A880, E543) listed in the technical sections of the specifications. Laboratories engaged in Hazardous Materials Testing shall meet the requirements of OSHA and EPA. The policy applies to the specific

laboratory performing the actual testing, not just the “Corporate Office.”

    - Inspection and Testing: Testing laboratory shall inspect materials and workmanship and perform tests described herein and additional tests requested by Resident Engineer. When it appears materials furnished, or work performed by Contractor fail to meet construction contract requirements, Testing Laboratory shall direct attention of Resident Engineer to such failure.

    - Written Reports: Testing laboratory shall submit test reports to Resident Engineer, Contractor, unless other arrangements are agreed to in writing by the Resident Engineer. Submit reports of tests that fail to meet construction contract requirements on colored paper.

    - Verbal Reports: Give verbal notification to Resident Engineer immediately of any irregularity.

PART 2 - PRODUCTS (NOT USED)

PART 3 - EXECUTION

3.1 EARTHWORK:

- General: The Testing Laboratory shall provide qualified personnel, materials, equipment, and transportation as required to perform the services identified/required herein, within the agreed to schedule and/or time frame. The work to be performed shall be as identified herein and shall include but not be limited to the following:

  - Observe fill and subgrades during proof-rolling to evaluate suitability of surface material to receive fill or base course. Provide recommendations to the Resident Engineer regarding suitability or unsuitability of areas where proof-rolling was observed. Where unsuitable results are observed, witness excavation of unsuitable material and recommend to Resident Engineer extent of removal and replacement of unsuitable materials and observe proof- rolling of replaced areas until satisfactory results are obtained.

  - Provide full time observation of fill placement and compaction and field density testing in building areas and provide full time observation of fill placement and compaction and field density testing in pavement areas to verify that earthwork compaction obtained is in accordance with contract documents.

  - Provide supervised geotechnical technician to inspect excavation, subsurface preparation, and backfill for structural fill.

- Testing Compaction:

  - Determine maximum density and optimum moisture content for each type of fill, backfill and subgrade material used, in compliance with AASHTO T99/T180 Method A , ASTM D698 or ASTM D1557 Method A, or ASTM D698 and/or ASTM D1557.

  - Make field density tests in accordance with the primary testing method following ASTM D6938 or AASHTO T310 wherever possible. Field density tests utilizing ASTM D1556, AASHTO T191 , or // ASTM D2167 shall be utilized on a case by case basis only if there are problems with the validity of the results from the primary method due to specific site field conditions. Should the testing laboratory propose these alternative methods, they should provide satisfactory explanation to the Resident Engineer before the tests are conducted.

    - Pavement Subgrade: One test for each 335 m2 (400 square yards), but in no case fewer than two tests.

    - Curb, Gutter, and Sidewalk: One test for each 90 m (300 feet), but in no case fewer than two tests.

    - Trenches: One test at maximum 30 m (100 foot) intervals per 1200 mm (4 foot) of vertical lift and at changes in required density, but in no case fewer than two tests.

- Fill and Backfill Material Gradation: One test per 400 square yards stockpiled or in-place source material. Gradation of fill and backfill material shall be determined in accordance with ASTM C136,ASTM D422, or ASTM D1140.

E. Testing Materials: Test suitability of on-site and off-site borrow as directed by Resident Engineer.

  - LANDSCAPING:

    - Test topsoil for organic materials, pH, phosphate, potash content, and gradation of particles.

      - Test for organic material by using ASTM D2974.

      - Determine percent of silt, sand, clay, and foreign materials such as rock, roots, and vegetation.

    - Submit laboratory test report of topsoil to Resident Engineer.

  - ASPHALT CONCRETE PAVING:

    - Aggregate Base Course:

      - Determine maximum density and optimum moisture content for aggregate base material in accordance with AASHTO T180, Method D

      - Make a minimum of three field density tests on each day's final compaction on each aggregate course in accordance with AASHTO T191 .

      - Sample and test aggregate as necessary to insure compliance with specification requirements for gradation, wear, and soundness as specified in the applicable state highway standards and specifications.

    - Asphalt Concrete:

      - Aggregate: Sample and test aggregates in stock pile and hot-bins as necessary to insure compliance with specification requirements for gradation (AASHTO T27), wear (AASHTO T96), and soundness (AASHTO T104).

      - Temperature: Check temperature of each load of asphalt concrete at mixing plant and at site of paving operation.

      - Density: Make a minimum of two field density tests in accordance with ASTM D1188 of asphalt base and surface course for each day's paving operation.

  - SITE WORK CONCRETE:

Test site work concrete including materials for concrete as required in Article CONCRETE of this section.

3.17 SPRAYED-ON FIREPROOFING:

- Provide field inspection and testing services to certify sprayed-on fireproofing has been applied in accordance with contract documents.

- Obtain a copy of approved submittals from Resident Engineer.

- Use approved installation in test areas as criteria for inspection of work.

- Test sprayed-on fireproofing for thickness and density in accordance with ASTM E605.

  - Thickness gauge specified in ASTM E605 may be modified for pole extension so that overhead sprayed material can be reached from floor.

- Location of test areas for field tests as follows:

  - Thickness: Select one bay per floor, or one bay for each 930 m2 (10,000 square feet) of floor area, whichever provides for greater number of tests. Take thickness determinations from each of following locations: Metal deck, beam, and column.

  - Density: Take density determinations from each floor, or one test from each 930 m2 (10,000 square feet) of floor area, whichever provides for greater number of tests, from each of the following areas: Underside of metal deck, beam flanges, and beam web.

- Submit inspection reports, certification, and instances of noncompliance to Resident Engineer.

3.19 TYPE OF TEST:

Approximate Number of Tests Required

- Aggregate Base:

Laboratory Compaction, (AASHTO T180), ASTM D1557)

Field Density,(AASHTO T191),(ASTM D1556)

Aggregate, Base Course Gradation (AASHTO T27)		 Wear (AASHTO T96)

Soundness (AASHTO T104)

- Asphalt Concrete:

Field Density, (AASHTO T230, ASTM D1188

Aggregate, Asphalt Concrete Gradation (AASHTO T27) Wear (AASHTO T96)

Soundness (AASHTO T104)

- Sprayed-On Fireproofing:

Thickness and Density Tests (ASTM E605)

as identified in cutting and patching notes on drawings.

- - - E N D - - -

SECTION 01 57 19 TEMPORARY ENVIRONMENTAL CONTROLS

PART 1 - GENERAL

  - DESCRIPTION

    - This section specifies the control of environmental pollution and damage that the Contractor must consider for air, water, and land resources. It includes management of visual aesthetics, noise, solid waste, radiant energy, and radioactive materials, as well as other pollutants and resources encountered or generated by the Contractor. The Contractor is obligated to consider specified control measures with the costs included within the various contract items of work.

    - Environmental pollution and damage is defined as the presence of chemical, physical, or biological elements or agents which:

      - Adversely effect human health or welfare,

      - Unfavorably alter ecological balances of importance to human life,

      - Effect other species of importance to humankind, or;

      - Degrade the utility of the environment for aesthetic, cultural, and historical purposes.

    - Definitions of Pollutants:

      - Chemical Waste: Petroleum products, bituminous materials, salts, acids, alkalis, herbicides, pesticides, organic chemicals, and inorganic wastes.

      - Debris: Combustible and noncombustible wastes, such as leaves, tree trimmings, ashes, and waste materials resulting from construction or maintenance and repair work.

      - Sediment: Soil and other debris that has been eroded and transported by runoff water.

      - Solid Waste: Rubbish, debris, garbage, and other discarded solid materials resulting from industrial, commercial, and agricultural operations and from community activities.

      - Surface Discharge: The term "Surface Discharge" implies that the water is discharged with possible sheeting action and subsequent soil erosion may occur. Waters that are surface discharged may terminate in drainage ditches, storm sewers, creeks, and/or "water

of the United States" and would require a permit to discharge water from the governing agency.

      - Rubbish: Combustible and noncombustible wastes such as paper, boxes, glass and crockery, metal and lumber scrap, tin cans, and bones.

      - Sanitary Wastes:

        - Sewage: Domestic sanitary sewage and human and animal waste.

        - Garbage: Refuse and scraps resulting from preparation, cooking, dispensing, and consumption of food.

  - QUALITY CONTROL

    - Establish and maintain quality control for the environmental protection of all items set forth herein.

    - Record on daily reports any problems in complying with laws, regulations, and ordinances. Note any corrective action taken.

  - REFERENCES

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to in the text by basic designation only.

    - U.S. National Archives and Records Administration (NARA):

33 CFR 328	Definitions

  - SUBMITTALS

    - In accordance with Section, 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES, furnish the following:

      - Environmental Protection Plan: After the contract is awarded and prior to the commencement of the work, the Contractor shall meet with the Contracting Officer’s Representative (COR) to discuss the proposed Environmental Protection Plan and to develop mutual understanding relative to details of environmental protection. Not more than 20 days after the meeting, the Contractor shall prepare and submit to the Contracting Officer for approval, a written and/or graphic Environmental Protection Plan including, but not limited to, the following:

        - Name(s) of person(s) within the Contractor's organization who is (are) responsible for ensuring adherence to the Environmental Protection Plan.

        - Name(s) and qualifications of person(s) responsible for manifesting hazardous waste to be removed from the site.

        - Name(s) and qualifications of person(s) responsible for training the Contractor's environmental protection personnel.

        - Description of the Contractor's environmental protection personnel training program.

        - A list of Federal, State, and local laws, regulations, and permits concerning environmental protection, pollution control, noise control and abatement that are applicable to the Contractor's proposed operations and the requirements imposed by those laws, regulations, and permits.

        - Methods for protection of features to be preserved within authorized work areas including trees, shrubs, vines, grasses, ground cover, landscape features, air and water quality, fish and wildlife, soil, historical, and archeological and cultural resources.

        - Procedures to provide the environmental protection that comply with the applicable laws and regulations. Describe the procedures to correct pollution of the environment due to accident, natural causes, or failure to follow the procedures as described in the Environmental Protection Plan.

        - Permits, licenses, and the location of the solid waste disposal area.

        - Drawings showing locations of any proposed temporary excavations or embankments for haul roads, material storage areas, structures, sanitary facilities, and stockpiles of excess or spoil materials. Include as part of an Erosion Control Plan approved by the District Office of the U.S. Soil Conservation Service and the Department of Veterans Affairs.

        - Environmental Monitoring Plans for the job site including land, water, air, and noise.

        - Work Area Plan showing the proposed activity in each portion of the area and identifying the areas of limited use or nonuse. Plan should include measures for marking the limits of use areas. This plan may be incorporated within the Erosion Control Plan.

        - Inclusion of “best management practices” and methodologies.

    - Approval of the Contractor's Environmental Protection Plan will not relieve the Contractor of responsibility for adequate and continued control of pollutants and other environmental protection measures.

  - PROTECTION OF ENVIRONMENTAL RESOURCES

    - Protect environmental resources within the project boundaries and those affected outside the limits of permanent work during the entire period of this contract. Confine activities to areas defined by the specifications and drawings.

    - Protection of Land Resources: Prior to construction, identify all land resources to be preserved within the work area. Do not remove, cut, deface, injure, or destroy land resources including trees, shrubs, vines, grasses, topsoil, and landforms without permission from the COR. Do not fasten or attach ropes, cables, or guys to trees for anchorage unless specifically authorized, or where special emergency use is permitted. Provide erosion control plans, in phases where required.

      - Work Area Limits: Prior to any construction, mark the areas that require work to be performed under this contract. Mark or fence isolated areas within the general work area that are to be saved and protected. Protect monuments, works of art, and markers before construction operations begin. Convey to all personnel the purpose of marking and protecting all necessary objects.

      - Protection of Landscape: Protect trees, shrubs, vines, grasses, land forms, and other landscape features shown on the drawings to be preserved by marking, fencing, or using any other approved techniques.

        - Box and protect from damage existing trees and shrubs to remain on the construction site.

        - Immediately repair all damage to existing trees and shrubs by trimming, cleaning, and painting with antiseptic tree paint.

        - Do not store building materials or perform construction activities closer to existing trees or shrubs than the farthest extension of their limbs.

      - Reduction of Exposure of Unprotected Erodible Soils: Plan and conduct earthwork to minimize the duration of exposure of unprotected soils. Clear areas in reasonably sized increments only as needed to use. Form earthwork to final grade as shown.

Immediately protect side slopes and back slopes upon completion of rough grading.

      - Temporary Protection of Disturbed Areas: Construct diversion ditches, benches, and berms to retard and divert runoff from the construction site to protected drainage areas approved under paragraph 208 of the Clean Water Act.

        - Sediment Basins: Trap sediment from construction areas in temporary or permanent sediment basins that accommodate the runoff of a local 50 (design year) storm. After each storm, pump the basins dry and remove the accumulated sediment. Control overflow/drainage with paved weirs or by vertical overflow pipes, draining from the surface.

        - Reuse or conserve the collected topsoil sediment as directed by the COR. Topsoil use and requirements are specified in Section 31

20 00, EARTH MOVING.

        - Institute effluent quality monitoring programs as required by Federal, State, and local environmental agencies.

      - Erosion and Sedimentation Control Devices: The erosion and sediment controls selected and maintained by the Contractor shall be such that water quality standards are not violated as a result of the Contractor's activities. Construct or install all temporary and permanent erosion and sedimentation control features // shown. // on the Environmental Protection Plan. // Maintain temporary erosion and sediment control measures such as berms, dikes, drains, sedimentation basins, grassing, and mulching, until permanent drainage and erosion control facilities are completed and operative.

      - Manage borrow areas on Government property to minimize erosion and to prevent sediment from entering nearby water courses or lakes.

      - Manage and control spoil areas on Government property to limit spoil to areas and prevent erosion of soil or sediment from entering nearby water courses or lakes.

      - Protect adjacent areas from despoilment by temporary excavations and embankments.

      - Handle and dispose of solid wastes in such a manner that will prevent contamination of the environment. Place solid wastes (excluding clearing debris) in containers that are emptied on a

regular schedule. Transport all solid waste off Government property and dispose of waste in compliance with Federal, State, and local requirements.

      - Store chemical waste away from the work areas in corrosion resistant containers and dispose of waste in accordance with Federal, State, and local regulations.

      - Handle discarded materials other than those included in the solid waste category as directed by the COR.

    - Protection of Water Resources: Keep construction activities under surveillance, management, and control to avoid pollution of surface and ground waters and sewer systems. Implement management techniques to control water pollution by the listed construction activities that are included in this contract.

      - Washing and Curing Water: Do not allow wastewater directly derived from construction activities to enter water areas. Collect and place wastewater in retention ponds allowing the suspended material to settle, the pollutants to separate, or the water to evaporate.

      - Control movement of materials and equipment at stream crossings during construction to prevent violation of water pollution control standards of the Federal, State, or local government.

    - Protection of Fish and Wildlife Resources: Keep construction activities under surveillance, management, and control to minimize interference with, disturbance of, or damage to fish and wildlife. Prior to beginning construction operations, list species that require specific attention along with measures for their protection.

    - Protection of Air Resources: Keep construction activities under surveillance, management, and control to minimize pollution of air resources. Burning is not permitted on the job site. Keep activities, equipment, processes, and work operated or performed, in strict accordance with the State of Virginia Air Pollution Statue, Rule, or Regulation and Federal emission and performance laws and standards. Maintain ambient air quality standards set by the Environmental Protection Agency, for those construction operations and activities specified.

      - Particulates: Control dust particles, aerosols, and gaseous by- products from all construction activities, processing, and

preparation of materials (such as from asphaltic batch plants) at all times, including weekends, holidays, and hours when work is not in progress.

      - Particulates Control: Maintain all excavations, stockpiles, haul roads, permanent and temporary access roads, plant sites, spoil areas, borrow areas, and all other work areas within or outside the project boundaries free from particulates which would cause a hazard or a nuisance. Sprinklering, chemical treatment of an approved type, light bituminous treatment, baghouse, scrubbers, electrostatic precipitators, or other methods are permitted to control particulates in the work area.

      - Hydrocarbons and Carbon Monoxide: Control monoxide emissions from equipment to Federal and State allowable limits.

      - Odors: Control odors of construction activities and prevent obnoxious odors from occurring.

    - Reduction of Noise: Minimize noise using every action possible. Perform noise-producing work in less sensitive hours of the day or week as directed by the COR. Maintain noise-produced work at or below the decibel levels and within the time periods specified.

      - Perform construction activities involving repetitive, high-level impact noise only between 8:00a.m. and 6:00p.m unless otherwise permitted by local ordinance or the COR. Repetitive impact noise on the property shall not exceed the following dB limitations:

Time Duration of Impact Noise	Sound Level in dB More than 12 minutes in any hour		70

Less than 30 seconds of any hour	85

Less than three minutes of any hour	80

Less than 12 minutes of any hour	75

      - Provide sound-deadening devices on equipment and take noise abatement measures that are necessary to comply with the requirements of this contract, consisting of, but not limited to, the following:

a. Maintain maximum permissible construction equipment noise levels at 15 meter (50 feet) (dBA):

EARTHMOVING			MATERIALS HANDLING FRONT LOADERS	75	CONCRETE MIXERS	75

BACKHOES	75

DOZERS	75

TRACTORS	75

SCAPERS	80

GRADERS	75	JACK HAMMERS	75

TRUCKS	75

PNEUMATIC TOOLS	80

GENERATORS	75	SAWS	75

COMPRESSORS	75	VIBRATORS	75

- Use shields or other physical barriers to restrict noise transmission.

- Provide soundproof housings or enclosures for noise-producing machinery.

- Use efficient silencers on equipment air intakes.

- Use efficient intake and exhaust mufflers on internal combustion engines that are maintained so equipment performs below noise levels specified.

- Line hoppers and storage bins with sound deadening material.

- Conduct truck loading, unloading, and hauling operations so that noise is kept to a minimum.

3. Measure sound level for noise exposure due to the construction at least once every five successive working days while work is being performed above 55 dB(A) noise level. Measure noise exposure at the property line or 15 m (50 feet) from the noise source, whichever is greater. Measure the sound levels on the A weighing network of a General Purpose sound level meter at slow response. To minimize the effect of reflective sound waves at buildings, take measurements at 900 to 1800 mm (three to six feet) in front of any building face. Submit the recorded information to the COR noting any problems and the alternatives for mitigating actions.

    - Restoration of Damaged Property: If any direct or indirect damage is done to public or private property resulting from any act, omission,

neglect, or misconduct, the Contractor shall restore the damaged property to a condition equal to that existing before the damage at no additional cost to the Government. Repair, rebuild, or restore property as directed or make good such damage in an acceptable manner.

    - Final Clean-up: On completion of project and after removal of all debris, rubbish, and temporary construction, Contractor shall leave the construction area in a clean condition satisfactory to the COR. Cleaning shall include off the station disposal of all items and materials not required to be salvaged, as well as all debris and rubbish resulting from demolition and new work operations.

- - - E N D - - -

SECTION 01 58 16 TEMPORARY INTERIOR SIGNAGE

PART 1 GENERAL DESCRIPTION

This section specifies temporary interior signs.

PART 2 PRODUCTS

  - TEMPORARY SIGNS

    - Fabricate from 50 Kg (110 pound) mat finish white paper.

    - Cut to 100 mm (4-inch) wide by 300 mm (12 inch) long size tag.

    - Punch 3 mm (1/8-inch) diameter hole centered on 100 mm (4-inch) dimension of tag. Edge of Hole spaced approximately 13 mm (1/2-inch) from one end on tag.

    - Reinforce hole on both sides with gummed cloth washer or other suitable material capable of preventing tie pulling through paper edge.

    - Ties: Steel wire 0.3 mm (0.0120-inch) thick, attach to tag with twist tie, leaving 150 mm (6-inch) long free ends.

PART 3 EXECUTION

        - INSTALLATION

          - Install temporary signs attached to room door frame or room door knob, lever, or pull for doors on corridor openings.

          - Mark on signs with felt tip marker having approximately 3 mm (1/8-inch) wide stroke for clearly legible numbers or letters.

          - Identify room with numbers as designated on floor plans.

        - LOCATION

          - Install on doors that have room, corridor, and space numbers shown.

          - Doors that do not require signs are as follows:

            - Corridor barrier doors (cross-corridor) in corridor with same number.

            - Folding doors or partitions.

            - Toilet or bathroom doors within and between rooms.

            - Communicating doors in partitions between rooms with corridor entrance doors.

            - Closet doors within rooms.

          - Replace missing, damaged, or illegible signs.

- - - E N D - - -

##### SECTION 017329 - CUTTING AND PATCHING

##### PART 1 - GENERAL

##### RELATED DOCUMENTS

###### The Contract Documents, including but not limited to, the Drawings and Individual Specification Sections, apply to this Section.

##### SUMMARY

###### This Section includes procedural requirements for cutting and patching.

###### Responsibility:	Each Contractor is responsible for the cutting and patching to permit installation or performance of Work of their contract.

###### Related Sections include the following:

###### Individual Specification Sections.

##### DEFINITIONS

###### Cutting: Removal of in-place construction necessary to permit installation or performance of Work of the contract.

###### Patching:	Fitting and repair work required to restore surfaces to original conditions after installation of Work of the contract.

##### SUBMITTALS

###### Cutting and Patching Proposal: Submit a proposal describing procedures at least 10 days before the time cutting and patching will be performed, requesting approval to proceed. Include the following information:

###### Extent:	At each occurrence, describe cutting and patching, show how they will be performed, and indicate why they cannot be avoided.

###### Changes to In-Place Construction: Describe anticipated results. Include changes to structural elements and operating components as well as changes in building's appearance and other significant visual elements.

###### Products: List products to be used and firms or entities that will perform the Work.

###### Dates: Indicate when cutting and patching will be performed.

###### Utility Services and Mechanical/Electrical Systems: List services/systems that cutting and patching procedures will disturb or affect. List services/systems that will be relocated and those that will be temporarily out of service. Indicate how long services/systems will be disrupted.

###### Structural Elements: Where cutting and patching involve adding reinforcement to structural elements, submit details and engineering calculations showing integration of reinforcement with original structure.

###### Design Professional’s Approval: Obtain approval of cutting and patching proposal before cutting and patching. Approval does not waive right to later require removal and replacement of unsatisfactory work.

##### QUALITY ASSURANCE

###### Structural Elements: Do not cut and patch structural elements in a manner that could change their load-carrying capacity or load- deflection ratio.

###### Operational Elements: Do not cut and patch operating elements and related components in a manner that results in reducing their capacity to perform as intended or that result in increased maintenance or decreased operational life or safety.

###### Fire Rated Elements: Do not cut and patch fire rated elements (i.e. floors, walls, roofs, shafts, etc.) in a manner that results in reducing their capacity to perform as intended or that results in decreased fire rating.

###### Miscellaneous Elements: Do not cut and patch miscellaneous elements or related components in a manner that could change their load-carrying capacity, which results in reducing their capacity to perform as intended, or that result in increased maintenance or decreased operational life or safety.

###### Visual Requirements: Do not cut and patch construction in a manner that results in visual evidence of cutting and patching. Do not cut and patch construction exposed on the exterior or in occupied spaces in a manner that would, in Design Professional’s opinion, reduce the building's aesthetic qualities. Remove and replace construction that has been cut and patched in a visually unsatisfactory manner.

###### Cutting and Patching Conference: Before proceeding, meet at Project site with parties involved in cutting and patching, including other trades. Review areas of potential interference and conflict. Coordinate procedures and resolve potential

###### conflicts before proceeding.

##### WARRANTY

###### Existing Warranties: Remove, replace, patch, and repair materials and surfaces cut or damaged during cutting and patching operations, by methods and with materials so as not to void existing warranties.

##### PART 2 - PRODUCTS

##### MATERIALS

###### General: Comply with requirements specified in other Sections.

###### In-Place Materials: Use materials identical to in-place materials. For exposed surfaces, use materials that visually match in-place adjacent surfaces to the fullest extent possible.

###### If identical materials are unavailable or cannot be used, use materials that, when installed, will match the visual and functional performance of in-place materials, unless specified otherwise in other Sections.

###### Fire Rated Elements: Provide firestopping products/systems specified in system design listings by approved testing agencies that conform to the construction type, penetrating item, annular space requirements and fire rating involved in each separate assembly. Refer to applicable Individual Specification Sections.

##### PART 3 - EXECUTION

##### EXAMINATION

###### Examine surfaces to be cut and patched and conditions under which cutting and patching are to be performed.

###### Compatibility: Before patching, verify compatibility with and suitability of substrates, including compatibility with in- place finishes or primers.

###### Proceed with installation only after unsafe or unsatisfactory conditions have been corrected.

##### PREPARATION

###### Temporary Support: Provide temporary support of Work to be cut.

###### Protection: Protect in-place construction during cutting and patching to prevent damage. Provide protection from adverse weather conditions for portions of Project that might be exposed during cutting and patching operations.

###### Adjoining Areas: Avoid interference with use of adjoining areas or interruption of free passage to adjoining areas.

###### Existing Utility Services and Mechanical/Electrical Systems: Where existing services/systems are required to be removed, relocated, or abandoned, bypass such services/systems before cutting or patching to minimize interruption to occupied areas.

##### PERFORMANCE

###### General: Employ skilled workers to perform cutting and patching. Proceed with cutting and patching at the earliest feasible time, and complete without delay.

###### Cut in-place construction to provide for installation of other components or performance of other construction, and subsequently patch as required to restore surfaces to their original condition.

###### Cutting: Cut in-place construction by sawing, drilling, breaking, chipping, grinding, and similar operations, including excavation, using methods least likely to damage elements retained or adjoining construction.

###### In general, use hand or small power tools designed for sawing and grinding, not hammering and chopping. Cut holes and slots as small as possible, neatly to size required, and with minimum disturbance of adjacent surfaces. Temporarily cover openings when not in use.

###### Finished Surfaces: Cut or drill from the exposed or finished side into concealed surfaces.

###### Concrete or Masonry: Cut using a cutting machine, such as an

###### abrasive saw or a diamond-core drill.

###### Mechanical and Electrical Services: Cut off pipe or conduit in walls or partitions to be removed. Cap, valve, or plug and seal remaining portion of pipe or conduit to prevent entrance of moisture or other foreign matter after cutting.

###### Proceed with patching after construction operations requiring cutting are complete.

###### Patching: Patch construction by filling, repairing, refinishing, closing up, and similar operations following performance of other Work. Patch with durable seams that are as invisible as possible. Provide materials and comply with installation requirements specified in other Sections.

###### Inspection: Where feasible, test and inspect patched areas

###### after completion to demonstrate integrity of installation.

###### Exposed Finishes: Restore exposed finishes of patched areas and extend finish restoration into retained adjoining construction in a manner that will eliminate evidence of patching and refinishing.

###### Clean piping, conduit, and similar features before applying paint or other finishing materials.

###### Restore damaged pipe covering to its original condition.

###### Floors and Walls: Where walls or partitions that are removed extend one finished area into another, patch and repair floor and wall surfaces in the new space. Provide an even surface of uniform finish, color, texture, and appearance. Remove in- place floor and wall coverings and replace with new materials, if necessary, to achieve uniform color and appearance.

###### Where patching occurs in a painted surface, apply primer and intermediate paint coats over the patch and apply final paint coat over entire unbroken surface containing the patch. Provide additional coats until patch blends with adjacent surfaces.

###### Ceilings: Patch, repair, or rehang in-place ceilings as necessary to provide an even-plane surface of uniform appearance.

###### Exterior Building Enclosure: Patch components in a manner that restores enclosure to a weathertight condition.

###### Fire Rated Elements: Install firestopping systems to comply with applicable Individual Specification Sections and firestopping manufacturer’s written installation instructions and published drawings for products and applications. Refer to drawings for indications of fire rated elements.

###### Cleaning: Clean areas and spaces where cutting and patching are performed. Completely remove paint, mortar, oils, putty, and similar materials.

##### END OF SECTION 017329

SECTION 01 74 19 CONSTRUCTION WASTE MANAGEMENT

PART 1 - GENERAL

  - DESCRIPTION

    - This section specifies the requirements for the management of non- hazardous building construction and demolition waste.

    - Waste disposal in landfills shall be minimized to the greatest extent possible. Of the inevitable waste that is generated, as much of the waste material as economically feasible shall be salvaged, recycled or reused.

    - Contractor shall use all reasonable means to divert construction and demolition waste from landfills and incinerators, and facilitate their salvage and recycle not limited to the following:

    - Waste Management Plan development and implementation.

    - Techniques to minimize waste generation.

    - Sorting and separating of waste materials.

    - Salvage of existing materials and items for reuse or resale.

    - Recycling of materials that cannot be reused or sold.

    - At a minimum the following waste categories shall be diverted from landfills:

      - Soil.

      - Inerts (eg, concrete, masonry and asphalt).

      - Clean dimensional wood and palette wood.

      - Green waste (biodegradable landscaping materials).

      - Engineered wood products (plywood, particle board and I-joists, etc).

      - Metal products (eg, steel, wire, beverage containers, copper, etc).

      - Sheathings

      - Cardboard, paper and packaging.

      - Bitumen roofing materials.

      - Plastics (eg, ABS, PVC).

      - Carpet and/or pad.

      - Gypsum board.

      - Insulation.

      - Paint.

      - Fluorescent lamps.

  - RELATED WORK

    - Section 02 41 00, DEMOLITION.

    - Section 01 00 00, GENERAL REQUIREMENTS.

      - Lead Paint: Section 02 83 33.13, LEAD BASED PAINT REMOVAL AND DISPOSAL.

      - Asbestos: SECTION 02 82 13.13 GLOVEBAG ASBESTOS ABATEMENT

  - QUALITY ASSURANCE

    - Contractor shall practice efficient waste management when sizing, cutting and installing building products. Processes shall be employed to ensure the generation of as little waste as possible. Construction Demolition waste includes products of the following:

      - Excess or unusable construction materials.

      - Packaging used for construction products.

      - Poor planning and/or layout.

      - Construction error.

      - Over ordering.

      - Weather damage.

      - Contamination.

      - Mishandling.

      - Breakage.

    - Establish and maintain the management of non-hazardous building construction and demolition waste set forth herein. Conduct a site assessment to estimate the types of materials that will be generated by demolition and construction.

    - Contractor shall be responsible for implementation of any special programs involving rebates or similar incentives related to recycling. Any revenues or savings obtained from salvage or recycling shall accrue to the contractor.

    - Contractor shall provide all demolition, removal and legal disposal of materials. Contractor shall ensure that facilities used for recycling, reuse and disposal shall be permitted for the intended use to the extent required by local, state, federal regulations.

    - Contractor shall assign a specific area to facilitate separation of materials for reuse, salvage, recycling, and return. Such areas are to

be kept neat and clean and clearly marked in order to avoid contamination or mixing of materials.

    - Contractor shall provide on-site instructions and supervision of separation, handling, salvaging, recycling, reuse and return methods to be used by all parties during waste generating stages.

    - Record on daily reports any problems in complying with laws, regulations and ordinances with corrective action taken.

  - TERMINOLOGY

    - Class III Landfill: A landfill that accepts non-hazardous resources such as household, commercial and industrial waste resulting from construction, remodeling, repair and demolition operations.

    - Clean: Untreated and unpainted; uncontaminated with adhesives, oils, solvents, mastics and like products.

    - Construction and Demolition Waste: Includes all non-hazardous resources resulting from construction, remodeling, alterations, repair and demolition operations.

    - Dismantle: The process of parting out a building in such a way as to preserve the usefulness of its materials and components.

    - Disposal: Acceptance of solid wastes at a legally operating facility for the purpose of land filling (includes Class III landfills and inert fills).

    - Inert Backfill Site: A location, other than inert fill or other disposal facility, to which inert materials are taken for the purpose of filling an excavation, shoring or other soil engineering operation.

    - Inert Fill: A facility that can legally accept inert waste, such as asphalt and concrete exclusively for the purpose of disposal.

    - Inert Solids/Inert Waste: Non-liquid solid resources including, but not limited to, soil and concrete that does not contain hazardous waste or soluble pollutants at concentrations in excess of water-quality objectives established by a regional water board, and does not contain significant quantities of decomposable solid resources.

    - Mixed Debris: Loads that include commingled recyclable and non- recyclable materials generated at the construction site.

    - Mixed Debris Recycling Facility: A solid resource processing facility that accepts loads of mixed construction and demolition debris for the

purpose of recovering re-usable and recyclable materials and disposing non-recyclable materials.

    - Permitted Waste Hauler: A company that holds a valid permit to collect and transport solid wastes from individuals or businesses for the purpose of recycling or disposal.

    - Recycling: The process of sorting, cleansing, treating, and reconstituting materials for the purpose of using the altered form in the manufacture of a new product. Recycling does not include burning, incinerating or thermally destroying solid waste.

      - On-site Recycling – Materials that are sorted and processed on site for use in an altered state in the work, i.e. concrete crushed for use as a sub-base in paving.

      - Off-site Recycling – Materials hauled to a location and used in an altered form in the manufacture of new products.

    - Recycling Facility: An operation that can legally accept materials for the purpose of processing the materials into an altered form for the manufacture of new products. Depending on the types of materials accepted and operating procedures, a recycling facility may or may not be required to have a solid waste facilities permit or be regulated by the local enforcement agency.

    - Reuse: Materials that are recovered for use in the same form, on-site or off-site.

    - Return: To give back reusable items or unused products to vendors for credit.

    - Salvage: To remove waste materials from the site for resale or re-use by a third party.

    - Source-Separated Materials: Materials that are sorted by type at the site for the purpose of reuse and recycling.

    - Solid Waste: Materials that have been designated as non-recyclable and are discarded for the purposes of disposal.

    - Transfer Station: A facility that can legally accept solid waste for the purpose of temporarily storing the materials for re-loading onto other trucks and transporting them to a landfill for disposal, or recovering some materials for re-use or recycling.

  - SUBMITTALS

    - In accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, and SAMPLES, furnish the following:

    - Prepare and submit to the CORa written demolition debris management plan. The plan shall include, but not be limited to, the following information:

      - Procedures to be used for debris management.

      - Techniques to be used to minimize waste generation.

      - Analysis of the estimated job site waste to be generated:

        - List of each material and quantity to be salvaged, reused, recycled.

        - List of each material and quantity proposed to be taken to a landfill.

      - Detailed description of the Means/Methods to be used for material handling.

        - On site: Material separation, storage, protection where applicable.

        - Off site: Transportation means and destination. Include list of materials.

          - Description of materials to be site-separated and self-hauled to designated facilities.

          - Description of mixed materials to be collected by designated waste haulers and removed from the site.

            - The names and locations of mixed debris reuse and recycling facilities or sites.

            - The names and locations of trash disposal landfill facilities or sites.

            - Documentation that the facilities or sites are approved to receive the materials.

    - Designated Manager responsible for instructing personnel, supervising, documenting and administer over meetings relevant to the Waste Management Plan.

    - Monthly summary of construction and demolition debris diversion and disposal, quantifying all materials generated at the work site and disposed of or diverted from disposal through recycling.

    - Target waste diversion rate by material and an overall diversion rate.

    - Final report documenting the results of implementation of the preconstruction waste management plan.

  - APPLICABLE PUBLICATIONS

    - Publications listed below form a part of this specification to the extent referenced. Publications are referenced by the basic designation only. In the event that criteria requirements conflict, the most stringent requirements shall be met.

    - U.S. Green Building Council (USGBC): LEED Green Building Rating System for New Construction

      - Green Building Initiative (GBI): Green Globes for New Construction 2019

  - RECORDS

    - Maintain records to document the quantity of waste generated; the quantity of waste diverted through sale, reuse, or recycling; and the quantity of waste disposed by landfill or incineration.

PART 2 - PRODUCTS

2.1 MATERIALS

- List of each material and quantity to be salvaged, recycled, reused.

- List of each material and quantity proposed to be taken to a landfill.

- Material tracking data: Receiving parties, dates removed, transportation costs, weight tickets, tipping fees, manifests, invoices, net total costs or savings.

PART 3 - EXECUTION

  - COLLECTION

    - Provide all necessary containers, bins and storage areas to facilitate effective waste management.

    - Clearly identify containers, bins and storage areas so that recyclable materials are separated from trash and can be transported to respective recycling facility for processing.

    - Hazardous wastes shall be separated, stored, disposed of according to local, state, federal regulations.

  - DISPOSAL

    - Contractor shall be responsible for transporting and disposing of materials that cannot be delivered to a source-separated or mixed materials recycling facility to a transfer station or disposal facility that can accept the materials in accordance with state and federal regulations.

    - Construction or demolition materials with no practical reuse or that cannot be salvaged or recycled shall be disposed of at a landfill or incinerator.

  - REPORT

    - With each application for progress payment, submit a summary of construction and demolition debris diversion and disposal including beginning and ending dates of period covered.

    - Quantify all materials diverted from landfill disposal through salvage or recycling during the period with the receiving parties, dates removed, transportation costs, weight tickets, manifests, invoices. Include the net total costs or savings for each salvaged or recycled material.

    - Quantify all materials disposed of during the period with the receiving parties, dates removed, transportation costs, weight tickets, tipping fees, manifests, invoices. Include the net total costs for each disposal.

- - - E N D - - -

SECTION 01 91 00

GENERAL COMMISSIONING REQUIREMENTS

PART 1 - GENERAL

  - COMMISSIONING DESCRIPTION

    - This Section 01 91 00 GENERAL COMMISSIONING REQUIREMENTS shall form the basis of the construction phase commissioning process and procedures. The Commissioning Agent shall add, modify, and refine the commissioning procedures, as approved by the Department of Veterans Affairs (VA), to suit field conditions and actual manufacturer's equipment, incorporate test data and procedure results, and provide detailed scheduling for all commissioning tasks.

    - Various sections of the project specifications require equipment startup, testing, and adjusting services. Requirements for startup, testing, and adjusting services specified in the Division 7, Division 27, Division 28, and Division 31 series sections of these specifications are intended to be provided in coordination with the commissioning services and are not intended to duplicate services. The Contractor shall coordinate the work required by individual specification sections with the commissioning services requirements specified herein.

    - Where individual testing, adjusting, or related services are required in the project specifications and not specifically required by this commissioning requirements specification, the specified services shall be provided and copies of documentation, as required by those specifications shall be submitted to the VA and the Commissioning Agent to be indexed for future reference.

    - Where training or educational services for VA are required and specified in other sections of the specifications, including but not limited to Division 7, Division 27, Division 28, and Division 31 series sections of the specification, these services are intended to be provided in addition to the training and educational services specified herein.

    - Commissioning is a systematic process of verifying that the building systems perform interactively according to the construction documents and the VA’s operational needs. The commissioning process shall encompass and coordinate the system documentation, equipment startup, control system calibration, testing and balancing, performance testing

and training. Commissioning during the construction and post-occupancy phases is intended to achieve the following specific objectives according to the contract documents:

      - Verify that the applicable equipment and systems are installed in accordance with the contact documents and according to the manufacturer's recommendations.

      - Verify and document proper integrated performance of equipment and systems.

      - Verify that Operations & Maintenance documentation is complete.

      - Verify that all components requiring servicing can be accessed, serviced and removed without disturbing nearby components including ducts, piping, cabling or wiring.

      - Verify that the VA’s operating personnel are adequately trained to enable them to operate, monitor, adjust, maintain, and repair building systems in an effective and energy-efficient manner.

      - Document the successful achievement of the commissioning objectives listed above.

    - The commissioning process does not take away from or reduce the responsibility of the Contractor to provide a finished and fully functioning product.

  - CONTRACTUAL RELATIONSHIPS

    - For this construction project, the Department of Veterans Affairs contracts with a Contractor to provide construction services. The contracts are administered by the VA Contracting Officer and the Resident Engineer as the designated representative of the Contracting Officer. On this project, the authority to modify the contract in any way is strictly limited to the authority of the Contracting Officer.

    - In this project, only two contract parties are recognized and communications on contractual issues are strictly limited to VA Resident Engineer and the Contractor. It is the practice of the VA to require that communications between other parties to the contracts (Subcontractors and Vendors) be conducted through the Resident Engineer and Contractor. It is also the practice of the VA that communications between other parties of the project (Commissioning Agent / Architect/Engineer) be conducted through the Resident Engineer.

- With these fundamental practices in mind, the commissioning process described herein has been developed to recognize that, in the execution

of the Commissioning Process, the Commissioning Agent must develop effective methods to communicate with every member of the construction team involved in delivering commissioned systems while simultaneously respecting the exclusive contract authority of the Contracting Officer and Resident Engineer.	Thus, the procedures outlined in this specification must be executed within the following limitations:

  - No communications (verbal or written) from the Commissioning Agent shall be deemed to constitute direction that modifies the terms of any contract between the Department of Veterans Affairs and the Contractor.

  - Commissioning Issues identified by the Commissioning Agent will be delivered to the Resident Engineer and copied to the designated Commissioning Representatives for the Contractor and subcontractors on the Commissioning Team for information only in order to expedite the communication process. These issues must be understood as the professional opinion of the Commissioning Agent and as suggestions for resolution.

  - In the event that any Commissioning Issues and suggested resolutions are deemed by the Resident Engineer to require either an official interpretation of the construction documents or require a modification of the contract documents, the Contracting Officer or Resident Engineer will issue an official directive to this effect.

  - All parties to the Commissioning Process shall be individually responsible for alerting the Resident Engineer of any issues that they deem to constitute a potential contract change prior to acting on these issues.

  - Authority for resolution or modification of design and construction issues rests solely with the Contracting Officer or Resident Engineer, with appropriate technical guidance from the Architect/Engineer and/or Commissioning Agent.

  - RELATED WORK

    - Section 01 00 00 GENERAL REQUIREMENTS.

    - Section 01 32 16.01 ARCHITECTURAL AND ENGINEERING CPM SCHEDULES

    - Section 01 32.16.15 PROJECT SCHEDULES (SMALL PROJECTS – DESIGN/BID/BUILD)

    - Section 27 08 00 COMMISSIONING OF COMMUNICATIONS SYSTEMS.

    - Section 28 08 00 COMMISSIONING OF ELECTRONIC SAFETY AND SECURITY SYSTEMS.

  - SUMMARY

    - This Section includes general requirements that apply to implementation of commissioning without regard to systems, subsystems, and equipment being commissioned.

    - The commissioning activities have been developed to support the VA requirements to meet guidelines for Federal Leadership in Environmental, Energy, and Economic Performance.

    - 1.5 ACRONYMS

| List of Acronyms |  |
| --- | --- |
| Acronym | Meaning |
| A/E | Architect / Engineer Design Team |
| AHJ | Authority Having Jurisdiction |
| ASHRAE | Association Society for Heating Air Condition and Refrigeration Engineers |
| BOD | Basis of Design |
| BSC | Building Systems Commissioning |
| CCTV | Closed Circuit Television |
| CD | Construction Documents |
| CMMS | Computerized Maintenance Management System |
| CO | Contracting Officer (VA) |
| COR | Contracting Officer’s Representative (see also VA-RE) |
| COBie | Construction Operations Building Information Exchange |
| CPC | Construction Phase Commissioning |
| Cx | Commissioning |
| CxA | Commissioning Agent |
| CxM | Commissioning Manager |
| CxR | Commissioning Representative |
| DPC | Design Phase Commissioning |
| FPT | Functional Performance Test |
| GBI-GG | Green Building Initiative - Green Globes |
| HVAC | Heating, Ventilation, and Air Conditioning |
| LEED | Leadership in Energy and Environmental Design |
| NC | Department of Veterans Affairs National Cemetery |

| List of Acronyms |  |
| --- | --- |
| Acronym | Meaning |
| NCA | Department of Veterans Affairs National Cemetery Administration |
| NEBB | National Environmental Balancing Bureau |
| O&M | Operations & Maintenance |
| OPR | Owner’s Project Requirements |
| PFC | Pre-Functional Checklist |
| PFT | Pre-Functional Test |
| SD | Schematic Design |
| SO | Site Observation |
| TAB | Test Adjust and Balance |
| VA | Department of Veterans Affairs |
| VAMC | VA Medical Center |
| VA CFM | VA Office of Construction and Facilities Management |
| VACO | VA Central Office |
| VA PM | VA Project Manager |
| VA-RE | VA Resident Engineer |
| USGBC | United States Green Building Council |

  - DEFINITIONS

Acceptance Phase Commissioning: Commissioning tasks executed after most construction has been completed, most Site Observations and Static Tests have been completed and Pre-Functional Testing has been completed and accepted. The main commissioning activities performed during this phase are verification that the installed systems are functional by conducting Systems Functional Performance tests and Owner Training.

Accuracy: The capability of an instrument to indicate the true value of a measured quantity.

Back Check: A back check is a verification that an agreed upon solution to a design comment has been adequately addressed in a subsequent design review

Basis of Design (BOD): The Engineer’s Basis of Design is comprised of two components: the Design Criteria and the Design Narrative, these documents record the concepts, calculations, decisions, and product selections used to meet the Owner’s Project Requirements (OPR) and to satisfy applicable regulatory requirements, standards, and guidelines.

Benchmarks: Benchmarks are the comparison of a building’s energy usage to other similar buildings and to the building itself.. For example, ENERGY STAR Portfolio Manager is a frequently used and nationally recognized building energy benchmarking tool.

Building Information Modeling (BIM):	Building Information Modeling is a parametric database which allows a building to be designed and constructed virtually in 3D, and provides reports both in 2D views and as schedules. This electronic information can be extracted and reused for pre-populating facility management CMMS systems. Building Systems Commissioning (BSC): NEBB acronym used to designate its commissioning program.

Calibrate: The act of comparing an instrument of unknown accuracy with a standard of known accuracy to detect, correlate, report, or eliminate by adjustment any variation in the accuracy of the tested instrument.

CCTV: Closed circuit Television. Normally used for security surveillance and alarm detections as part of a special electrical security system.

COBie: Construction Operations Building Information Exchange (COBie) is an electronic industry data format used to transfer information developed during design, construction, and commissioning into the Computer Maintenance Management Systems (CMMS) used to operate facilities. See the Whole Building Design Guide website for further information (http://www.wbdg.org/resources/cobie.php) Commissionability: Defines a design component or construction process that has the necessary elements that will allow a system or component to be effectively measured, tested, operated and commissioned Commissioning Agent (CxA): The qualified Commissioning Professional who administers the Cx process by managing the Cx team and overseeing the Commissioning Process. Where CxA is used in this specification it means the Commissioning Agent, members of his staff or appointed members of the commissioning team. Note that LEED uses the term Commissioning Authority in lieu of Commissioning Agent.

Commissioning Checklists: Lists of data or inspections to be verified to ensure proper system or component installation, operation, and function. Verification checklists are developed and used during all phases of the commissioning process to verify that the Owner’s Project Requirements (OPR) is being achieved.

Commissioning Design Review: The commissioning design review is a collaborative review of the design professionals design documents for items pertaining to the following: owner’s project requirements; basis of design; operability and maintainability (O&M) including documentation; functionality; training; energy efficiency, control systems’ sequence of operations including building automation system features; commissioning specifications and the ability to functionally test the systems.

Commissioning Issue: A condition identified by the Commissioning Agent or other member of the Commissioning Team that adversely affects the commissionability, operability, maintainability, or functionality of a system, equipment, or component. A condition that is in conflict with the Contract Documents and/or performance requirements of the installed systems and components. (See also – Commissioning Observation).

Commissioning Manager (CxM): A qualified individual appointed by the Contractor to manage the commissioning process on behalf of the Contractor.

Commissioning Observation: An issue identified by the Commissioning Agent or other member of the Commissioning Team that does not conform to the project OPR, contract documents or standard industry best practices. (See also Commissioning Issue)

Commissioning Plan: A document that outlines the commissioning process, commissioning scope and defines responsibilities, processes, schedules, and the documentation requirements of the Commissioning Process.

Commissioning Process: A quality focused process for enhancing the delivery of a project. The process focuses upon verifying and documenting that the facility and all of its systems, components, and assemblies are planned, designed, installed, tested, can be operated, and maintained to meet the Owner's Project Requirements.

Commissioning Report: The final commissioning document which presents the commissioning process results for the project. Cx reports include an executive summary, the commissioning plan, issue log, correspondence, and all appropriate check sheets and test forms.

Commissioning Representative (CxR): An individual appointed by a sub- contractor to manage the commissioning process on behalf of the sub- contractor.

Commissioning Specifications: The contract documents that detail the objective, scope and implementation of the commissioning process as developed in the Commissioning Plan.

Commissioning Team: Individual team members whose coordinated actions are responsible for implementing the Commissioning Process.

Construction Phase Commissioning: All commissioning efforts executed during the construction process after the design phase and prior to the Acceptance Phase Commissioning.

Contract Documents (CD): Contract documents include design and construction contracts, price agreements and procedure agreements. Contract Documents also include all final and complete drawings, specifications and all applicable contract modifications or supplements.

Construction Phase Commissioning (CPC): All commissioning efforts executed during the construction process after the design phase and prior to the Acceptance Phase Commissioning.

Coordination Drawings: Drawings showing the work of all trades that are used to illustrate that equipment can be installed in the space allocated without compromising equipment function or access for maintenance and replacement. These drawings graphically illustrate and dimension manufacturers’ recommended maintenance clearances. On mechanical projects, coordination drawings include structural steel, ductwork, major piping and electrical conduit and show the elevations and locations of the above components.

Data Logging: The monitoring and recording of temperature, flow, current, status, pressure, etc. of equipment using stand-alone data recorders.

Deferred System Test: Tests that cannot be completed at the end of the acceptance phase due to ambient conditions, schedule issues or other conditions preventing testing during the normal acceptance testing period.

Deficiency: See “Commissioning Issue”.

Design Criteria: A listing of the VA Design Criteria outlining the project design requirements, including its source. These are used during the design process to show the design elements meet the OPR. Design Intent: The overall term that includes the OPR and the BOD. It is a detailed explanation of the ideas, concepts, and criteria that are

defined by the owner to be important. The design intent documents are utilized to provide a written record of these ideas, concepts and criteria.

Design Narrative: A written description of the proposed design solutions that satisfy the requirements of the OPR.

Design Phase Commissioning (DPC): All commissioning tasks executed during the design phase of the project.

Environmental Systems: Systems that use a combination of mechanical equipment, airflow, water flow and electrical energy to provide heating, ventilating, air conditioning, humidification, and dehumidification for the purpose of human comfort or process control of temperature and humidity.

Executive Summary: A section of the Commissioning report that reviews the general outcome of the project. It also includes any unresolved issues, recommendations for the resolution of unresolved issues and all deferred testing requirements.

Functionality: This defines a design component or construction process which will allow a system or component to operate or be constructed in a manner that will produce the required outcome of the OPR. Functional Test Procedure (FTP): A written protocol that defines methods, steps, personnel, and acceptance criteria for tests conducted on components, equipment, assemblies, systems, and interfaces among systems.

Industry Accepted Best Practice: A design component or construction process that has achieved industry consensus for quality performance and functionality. Refer to the current edition of the NEBB Design Phase Commissioning Handbook for examples.

Installation Verification: Observations or inspections that confirm the system or component has been installed in accordance with the contract documents and to industry accepted best practices.

Integrated System Testing: Integrated Systems Testing procedures entail testing of multiple integrated systems performance to verify proper functional interface between systems. Typical Integrated Systems Testing includes verifying that building systems respond properly to loss of utility, transfer to emergency power sources, re-transfer from emergency power source to normal utility source; interface between HVAC controls and Fire Alarm systems for equipment shutdown, interface

between Fire Alarm system and elevator control systems for elevator recall and shutdown; interface between Fire Alarm System and Security Access Control Systems to control access to spaces during fire alarm conditions; and other similar tests as determined for each specific project.

Issues Log: A formal and ongoing record of problems or concerns – and their resolution – that have been raised by members of the Commissioning Team during the course of the Commissioning Process.

Lessons Learned Workshop: A workshop conducted to discuss and document project successes and identify opportunities for improvements for future projects.

Maintainability: A design component or construction process that will allow a system or component to be effectively maintained. This includes adequate room for access to adjust and repair the equipment.

Maintainability also includes components that have readily obtainable repair parts or service.

Manual Test: Testing using hand-held instruments, immediate control system readouts or direct observation to verify performance (contrasted to analyzing monitored data taken over time to make the ‘observation’). Owner’s Project Requirements (OPR): A written document that details the project requirements and the expectations of how the building and its systems will be used and operated. These include project goals, measurable performance criteria, cost considerations, benchmarks, success criteria, and supporting information.

Peer Review: A formal in-depth review separate from the commissioning review processes. The level of effort and intensity is much greater than a typical commissioning facilitation or extended commissioning review. The VA usually hires an independent third-party (called the IDIQ A/E) to conduct peer reviews.

Precision: The ability of an instrument to produce repeatable readings of the same quantity under the same conditions. The precision of an instrument refers to its ability to produce a tightly grouped set of values around the mean value of the measured quantity.

Pre-Design Phase Commissioning: Commissioning tasks performed prior to the commencement of design activities that includes project programming and the development of the commissioning process for the project

Pre-Functional Checklist (PFC): A form used by the contractor to verify that appropriate components are onsite, correctly installed, set up, calibrated, functional and ready for functional testing.

Pre-Functional Test (PFT): An inspection or test that is done before functional testing. PFT’s include installation verification and system and component start up tests.

Procedure or Protocol: A defined approach that outlines the execution of a sequence of work or operations. Procedures are used to produce repeatable and defined results.

Range: The upper and lower limits of an instrument’s ability to measure the value of a quantity for which the instrument is calibrated.

Resolution: This word has two meanings in the Cx Process. The first refers to the smallest change in a measured variable that an instrument can detect. The second refers to the implementation of actions that correct a tested or observed deficiency.

Site Observation Visit: On-site inspections and observations made by the Commissioning Agent for the purpose of verifying component, equipment, and system installation, to observe contractor testing, equipment start-up procedures, or other purposes.

Site Observation Reports (SO): Reports of site inspections and observations made by the Commissioning Agent. Observation reports are intended to provide early indication of an installation issue which will need correction or analysis.

Special System Inspections: Inspections required by a local code authority prior to occupancy and are not normally a part of the commissioning process.

Static Tests: Tests or inspections that validate a specified static condition such as pressure testing. Static tests may be specification or code initiated.

Start Up Tests: Tests that validate the component or system is ready for automatic operation in accordance with the manufactures requirements.

Systems Manual: A system-focused composite document that includes all information required for the owners operators to operate the systems. Test Procedure: A written protocol that defines methods, personnel, and expectations for tests conducted on components, equipment, assemblies, systems, and interfaces among systems.

Testing: The use of specialized and calibrated instruments to measure parameters such as: temperature, pressure, vapor flow, air flow, fluid flow, rotational speed, electrical characteristics, velocity, and other data in order to determine performance, operation, or function.

Testing, Adjusting, and Balancing (TAB): A systematic process or service applied to heating, ventilating and air-conditioning (HVAC) systems and other environmental systems to achieve and document air and hydronic flow rates. The standards and procedures for providing these services are referred to as “Testing, Adjusting, and Balancing” and are described in the Procedural Standards for the Testing, Adjusting and Balancing of Environmental Systems, published by NEBB or AABC.

Thermal Scans: Thermographic pictures taken with an Infrared Thermographic Camera. Thermographic pictures show the relative temperatures of objects and surfaces and are used to identify leaks, thermal bridging, thermal intrusion, electrical overload conditions, moisture containment, and insulation failure.

Training Plan: A written document that details, in outline form the expectations of the operator training. Training agendas should include instruction on how to obtain service, operate, startup, shutdown and maintain all systems and components of the project.

Trending: Monitoring over a period of time with the building automation system.

Unresolved Commissioning Issue: Any Commissioning Issue that, at the time that the Final Report or the Amended Final Report is issued that has not been either resolved by the construction team or accepted by the VA. Validation: The process by which work is verified as complete and operating correctly:

    - First party validation occurs when a firm or individual verifying the task is the same firm or individual performing the task.

    - Second party validation occurs when the firm or individual verifying the task is under the control of the firm performing the task or has other possibilities of financial conflicts of interest in the resolution (Architects, Designers, General Contractors and Third Tier Subcontractors or Vendors).

    - Third party validation occurs when the firm verifying the task is not associated with or under control of the firm performing or designing the task.

Verification: The process by which specific documents, components, equipment, assemblies, systems, and interfaces among systems are confirmed to comply with the criteria described in the Owner’s Project Requirements.

Warranty Phase Commissioning: Commissioning efforts executed after a project has been completed and accepted by the Owner. Warranty Phase Commissioning includes follow-up on verification of system performance, measurement and verification tasks and assistance in identifying warranty issues and enforcing warranty provisions of the construction contract.

Warranty Visit: A commissioning meeting and site review where all outstanding warranty issues and deferred testing is reviewed and discussed.

Whole Building Commissioning: Commissioning of building systems such as Building Envelope, HVAC, Electrical, Special Electrical (Fire Alarm, Security & Communications), Plumbing and Fire Protection as described in this specification.

  - SYSTEMS TO BE COMMISSIONED

- Commissioning of a system or systems specified for this project is part of the construction process. Documentation and testing of these systems, as well as training of the VA’s Operation and Maintenance personnel, is required in cooperation with the VA and the Commissioning Agent.

- The following systems will be commissioned by others as part of this project:

| Systems To Be Commissioned |  |
| --- | --- |
| System | Description |
| Specialties |  |
| Lightning Protection System | Witness 3rd party testing, review reports |
| Communications |  |
| Grounding & Bonding System | Witness 3rd party testing, review reports |
| Electronic Safety and Security |  |

| Systems To Be Commissioned |  |
| --- | --- |
| System | Description |
| Video Surveillance System | Witness 3rd party testing, review reports |
| Table Notes |  |

  - COMMISSIONING TEAM

- The commissioning team shall consist of, but not be limited to, representatives of Contractor, including Project Superintendent and subcontractors, installers, schedulers, suppliers, and specialists deemed appropriate by the Department of Veterans Affairs (VA) and Commissioning Agent.

- Members Appointed by Contractor:

  - Contractor’ Commissioning Manager: The designated person, company, or entity that plans, schedules and coordinates the commissioning activities for the construction team.

  - Contractor’s Commissioning Representative(s): Individual(s), each having authority to act on behalf of the entity he or she represents, explicitly organized to implement the commissioning process through coordinated actions.

- Members Appointed by VA:

  - Commissioning Agent: The designated person, company, or entity that plans, schedules, and coordinates the commissioning team to implement the commissioning process. The VA will engage the CxA under a separate contract.

  - User: Representatives of the facility user and operation and maintenance personnel.

  - A/E: Representative of the Architect and engineering design professionals.

  - VA'S COMMISSIONING RESPONSIBILITIES

- Appoint an individual, company or firm to act as the Commissioning Agent.

- Assign operation and maintenance personnel and schedule them to participate in commissioning team activities including, but not limited to, the following:

  - Coordination meetings.

  - Training in operation and maintenance of systems, subsystems, and equipment.

  - Testing meetings.

  - Witness and assist in Systems Functional Performance Testing.

  - Demonstration of operation of systems, subsystems, and equipment.

- Provide the Construction Documents, prepared by Architect and approved by VA, to the Commissioning Agent and for use in managing the commissioning process, developing the commissioning plan, systems manuals, and reviewing the operation and maintenance training plan.

  - CONTRACTOR'S COMMISSIONING RESPONSIBILITIES

- The Contractor shall assign a Commissioning Manager to manage commissioning activities of the Contractor, and subcontractors.

- The Contractor shall ensure that the commissioning responsibilities outlined in these specifications are included in all subcontracts and that subcontractors comply with the requirements of these specifications.

- The Contractor shall ensure that each installing subcontractor shall assign representatives with expertise and authority to act on behalf of the subcontractor and schedule them to participate in and perform commissioning team activities including, but not limited to, the following:

  - Participate in commissioning coordination meetings.

  - Conduct operation and maintenance training sessions in accordance with approved training plans.

  - Verify that Work is complete and systems are operational according to the Contract Documents, including calibration of instrumentation and controls.

  - Evaluate commissioning issues and commissioning observations identified in the Commissioning Issues Log, field reports, test reports or other commissioning documents. In collaboration with entity responsible for system and equipment installation, recommend corrective action.

  - Review and comment on commissioning documentation.

  - Participate in meetings to coordinate Systems Functional Performance Testing.

  - Provide schedule for operation and maintenance data submittals, equipment startup, and testing to Commissioning Agent for incorporation into the commissioning plan.

  - Provide information to the Commissioning Agent for developing commissioning plan.

  - Participate in training sessions for VA's operation and maintenance personnel.

  - Provide technicians who are familiar with the construction and operation of installed systems and who shall develop specific test procedures to conduct Systems Functional Performance Testing of installed systems.

  - COMMISSIONING AGENT’S RESPONSIBILITIES

- Organize and lead the commissioning team.

- Prepare the commissioning plan. See Paragraph 1.11-A of this specification Section for further information.

- Review and comment on selected submittals from the Contractor for general conformance with the Construction Documents. Review and comment on the ability to test and operate the system and/or equipment, including providing gages, controls and other components required to operate, maintain, and test the system. Review and comment on performance expectations of systems and equipment and interfaces between systems relating to the Construction Documents.

- At the beginning of the construction phase, conduct an initial construction phase coordination meeting for the purpose of reviewing the commissioning activities and establishing tentative schedules for operation and maintenance submittals; operation and maintenance training sessions; TAB Work; Pre-Functional Checklists, Systems Functional Performance Testing; and project completion.

- Convene commissioning team meetings for the purpose of coordination, communication, and conflict resolution; discuss status of the commissioning processes. Responsibilities include arranging for facilities, preparing agenda and attendance lists, and notifying participants. The Commissioning Agent shall prepare and distribute minutes to commissioning team members and attendees within five workdays of the commissioning meeting.

- Observe construction and report progress, observations and issues. Observe systems and equipment installation for adequate accessibility

for maintenance and component replacement or repair, and for general conformance with the Construction Documents.

- Prepare Project specific Pre-Functional Checklists and Systems Functional Performance Test procedures.

- Coordinate Systems Functional Performance Testing schedule with the Contractor.

- Witness selected systems startups.

- Verify selected Pre-Functional Checklists completed and submitted by the Contractor.

- Witness and document Systems Functional Performance Testing.

- Compile test data, inspection reports, and certificates and include them in the systems manual and commissioning report.

- Review and comment on operation and maintenance (O&M) documentation and systems manual outline for compliance with the Contract Documents. Operation and maintenance documentation requirements are specified in Paragraph 1.25, Section 01 00 00 GENERAL REQUIREMENTS.

- Review operation and maintenance training program developed by the Contractor. Verify training plans provide qualified instructors to conduct operation and maintenance training.

- Prepare commissioning Field Observation Reports.

- Prepare the Final Commissioning Report.

- Return to the site at 10 months into the 12 month warranty period and review with facility staff the current building operation and the condition of outstanding issues related to the original and seasonal Systems Functional Performance Testing. Also interview facility staff and identify problems or concerns they have operating the building as originally intended. Make suggestions for improvements and for recording these changes in the O&M manuals. Identify areas that may come under warranty or under the original construction contract. Assist facility staff in developing reports, documents and requests for services to remedy outstanding problems.

- Assemble the final commissioning documentation, including the Final Commissioning Report and Addendum to the Final Commissioning Report.

  - COMMISSIONING DOCUMENTATION

- Commissioning Plan: A document, prepared by Commissioning Agent, that outlines the schedule, allocation of resources, and documentation

requirements of the commissioning process, and shall include, but is not limited, to the following:

  - Plan for delivery and review of submittals, systems manuals, and other documents and reports. Identification of the relationship of these documents to other functions and a detailed description of submittals that are required to support the commissioning processes. Submittal dates shall include the latest date approved submittals must be received without adversely affecting commissioning plan.

  - Description of the organization, layout, and content of commissioning documentation (including systems manual) and a detailed description of documents to be provided along with identification of responsible parties.

  - Identification of systems and equipment to be commissioned.

  - Schedule of Commissioning Coordination meetings.

  - Identification of items that must be completed before the next operation can proceed.

  - Description of responsibilities of commissioning team members.

  - Description of observations to be made.

  - Description of requirements for operation and maintenance training.

  - Schedule for commissioning activities with dates coordinated with overall construction schedule.

  - Process and schedule for documenting changes on a continuous basis to appear in Project Record Documents.

  - Process and schedule for completing prestart and startup checklists for systems, subsystems, and equipment to be verified and tested.

  - Preliminary Systems Functional Performance Test procedures.

- Systems Functional Performance Test Procedures: The Commissioning Agent will develop Systems Functional Performance Test Procedures for each system to be commissioned, including subsystems, or equipment and interfaces or interlocks with other systems. Systems Functional Performance Test Procedures will include a separate entry, with space for comments, for each item to be tested. Preliminary Systems Functional Performance Test Procedures will be provided to the VA, Architect/Engineer, and Contractor for review and comment. The Systems Performance Test Procedure will include test procedures for each mode of operation and provide space to indicate whether the mode under test responded as required. Each System Functional Performance Test

procedure, regardless of system, subsystem, or equipment being tested, shall include, but not be limited to, the following:

  - Name and identification code of tested system.

  - Test number.

  - Time and date of test.

  - Indication of whether the record is for a first test or retest following correction of a problem or issue.

  - Dated signatures of the person performing test and of the witness, if applicable.

  - Individuals present for test.

  - Observations and Issues.

  - Issue number, if any, generated as the result of test.

- Pre-Functional Checklists: The Commissioning Agent will prepare Pre- Functional Checklists. Pre-Functional Checklists shall be completed and signed by the Contractor, verifying that systems, subsystems, equipment, and associated controls are ready for testing. The Commissioning Agent will spot check Pre-Functional Checklists to verify accuracy and readiness for testing. Inaccurate or incomplete Pre- Functional Checklists shall be returned to the Contractor for correction and resubmission.

- Test and Inspection Reports: The Commissioning Agent will record test data, observations, and measurements on Systems Functional Performance Test Procedure. The report will also include recommendation for system acceptance or non-acceptance. Photographs, forms, and other means appropriate for the application shall be included with data. Commissioning Agent Will compile test and inspection reports and test and inspection certificates and include them in systems manual and commissioning report.

- Corrective Action Documents: The Commissioning Agent will document corrective action taken for systems and equipment that fail tests. The documentation will include any required modifications to systems and equipment and/or revisions to test procedures, if any. The Commissioning Agent will witness and document any retesting of systems and/or equipment requiring corrective action and document retest results.

- Commissioning Issues Log: The Commissioning Agent will prepare and maintain Commissioning Issues Log that describes Commissioning Issues

and Commissioning Observations that are identified during the Commissioning process. These observations and issues include, but are not limited to, those that are at variance with the Contract Documents. The Commissioning Issues Log will identify and track issues as they are encountered, the party responsible for resolution, progress toward resolution, and document how the issue was resolved. The Master Commissioning Issues Log will also track the status of unresolved issues.

  - Creating an Commissioning Issues Log Entry:

    - Identify the issue with unique numeric or alphanumeric identifier by which the issue may be tracked.

    - Assign a descriptive title for the issue.

    - Identify date and time of the issue.

    - Identify test number of test being performed at the time of the observation, if applicable, for cross reference.

    - Identify system, subsystem, and equipment to which the issue applies.

    - Identify location of system, subsystem, and equipment.

    - Include information that may be helpful in diagnosing or evaluating the issue.

    - Note recommended corrective action.

    - Identify commissioning team member responsible for corrective action.

    - Identify expected date of correction.

    - Identify person that identified the issue.

  - Documenting Issue Resolution:

    - Log date correction is completed or the issue is resolved.

    - Describe corrective action or resolution taken. Include description of diagnostic steps taken to determine root cause of the issue, if any.

    - Identify changes to the Contract Documents that may require action.

    - State that correction was completed and system, subsystem, and equipment are ready for retest, if applicable.

    - Identify person(s) who corrected or resolved the issue.

    - Identify person(s) verifying the issue resolution.

- Final Commissioning Report: The Commissioning Agent will document results of the commissioning process, including unresolved issues, and performance of systems, subsystems, and equipment. The Commissioning Report will indicate whether systems, subsystems, and equipment have been properly installed and are performing according to the Contract Documents. This report will be used by the Department of Veterans Affairs when determining that systems will be accepted. This report will be used to evaluate systems, subsystems, and equipment and will serve as a future reference document during VA occupancy and operation. It shall describe components and performance that exceed requirements of the Contract Documents and those that do not meet requirements of the Contract Documents. The commissioning report will include, but is not limited to, the following:

  - Lists and explanations of substitutions; compromises; variances with the Contract Documents; record of conditions; and, if appropriate, recommendations for resolution. Design Narrative documentation maintained by the Commissioning Agent.

  - Commissioning plan.

  - Pre-Functional Checklists completed by the Contractor, with annotation of the Commissioning Agent review and spot check.

  - Systems Functional Performance Test Procedures, with annotation of test results and test completion.

5, Commissioning Issues Log.

6. Listing of deferred and off season test(s) not performed, including the schedule for their completion.

- Addendum to Final Commissioning Report: The Commissioning Agent will prepare an Addendum to the Final Commissioning Report near the end of the Warranty Period. The Addendum will indicate whether systems, subsystems, and equipment are complete and continue to perform according to the Contract Documents. The Addendum to the Final Commissioning Report shall include, but is not limited to, the following:

  - Documentation of deferred and off season test(s) results.

  - Completed Systems Functional Performance Test Procedures for off season test(s).

  - Documentation that unresolved system performance issues have been resolved.

  - Updated Commissioning Issues Log, including status of unresolved issues.

  - Identification of potential Warranty Claims to be corrected by the Contractor.

- Systems Manual: The Commissioning Agent will gather required information and compile the Systems Manual. The Systems Manual will include, but is not limited to, the following:

  - Design Narrative, including system narratives, schematics, single- line diagrams, flow diagrams, equipment schedules, and changes made throughout the Project.

  - Reference to Final Commissioning Plan.

  - Reference to Final Commissioning Report.

  - Approved Operation and Maintenance Data as submitted by the Contractor.

  - SUBMITTALS (BY OTHERS)

- Preliminary Commissioning Plan Submittal: The Commissioning Agent has prepared a Preliminary Commissioning Plan based on the final Construction Documents. The Preliminary Commissioning Plan is included as an Appendix to this specification section. The Preliminary Commissioning Plan is provided for information only. It contains preliminary information about the following commissioning activities:

  - The Commissioning Team: A list of commissioning team members by organization.

  - Systems to be commissioned. A detailed list of systems to be commissioned for the project. This list also provides preliminary information on systems/equipment submittals to be reviewed by the Commissioning Agent; preliminary information on Pre-Functional Checklists that are to be completed; preliminary information on Systems Performance Testing, including information on testing sample size (where authorized by the VA).

  - Commissioning Team Roles and Responsibilities: Preliminary roles and responsibilities for each Commissioning Team member.

  - Commissioning Documents: A preliminary list of commissioning-related documents, include identification of the parties responsible for preparation, review, approval, and action on each document.

  - Commissioning Activities Schedule: Identification of Commissioning Activities, including Systems Functional Testing, the expected duration and predecessors for the activity.

  - Pre-Functional Checklists: Preliminary Pre-Functional Checklists for equipment, components, subsystems, and systems to be commissioned. These Preliminary Pre-Functional Checklists provide guidance on the level of detailed information the Contractor shall include on the final submission.

  - Systems Functional Performance Test Procedures: Preliminary step- by-step System Functional Performance Test Procedures to be used during Systems Functional Performance Testing. These Preliminary Systems Functional Performance procedures provide information on the level of testing rigor, and the level of Contractor support required during performance of system’s testing.

- Final Commissioning Plan Submittal: Based on the Final Construction Documents and the Contractor’s project team, the Commissioning Agent will prepare the Final Commissioning Plan as described in this section. The Commissioning Agent will submit three hard copies and three sets of electronic files of Final Commissioning Plan. The Contractor shall review the Commissioning Plan and provide any comments to the VA. The Commissioning Agent will incorporate review comments into the Final Commissioning Plan as directed by the VA.

- Systems Functional Performance Test Procedure: The Commissioning Agent will submit preliminary Systems Functional Performance Test Procedures to the Contractor, and the VA for review and comment. The Contractor shall return review comments to the VA and the Commissioning Agent. The VA will also return review comments to the Commissioning Agent. The Commissioning Agent will incorporate review comments into the Final Systems Functional Test Procedures to be used in Systems Functional Performance Testing.

- Pre-Functional Checklists: The Commissioning Agent will submit Pre- Functional Checklists to be completed by the Contractor.

- Test and Inspection Reports: The Commissioning Agent will submit test and inspection reports to the VA with copies to the Contractor and the Architect/Engineer.

- Corrective Action Documents: The Commissioning Agent will submit corrective action documents to the VA Resident Engineer with copies to the Contractor and Architect.

- Preliminary Commissioning Report Submittal: The Commissioning Agent will submit three electronic copies of the preliminary commissioning report. One electronic copy, with review comments, will be returned to the Commissioning Agent for preparation of the final submittal.

- Final Commissioning Report Submittal: The Commissioning Agent will submit four sets of electronically formatted information of the final commissioning report to the VA. The final submittal will incorporate comments as directed by the VA.

- Data for Commissioning:

  - The Commissioning Agent will request in writing from the Contractor specific information needed about each piece of commissioned equipment or system to fulfill requirements of the Commissioning Plan.

  - The Commissioning Agent may request further documentation as is necessary for the commissioning process or to support other VA data collection requirements, including Construction Operations Building Information Exchange (COBIE), Building Information Modeling (BIM), etc.

  - COMMISSIONING PROCESS

- The Commissioning Agent will be responsible for the overall management of the commissioning process as well as coordinating scheduling of commissioning tasks with the VA and the Contractor. As directed by the VA, the Contractor shall incorporate Commissioning tasks, including, but not limited to, Systems Functional Performance Testing (including predecessors) with the Master Construction Schedule.

- Within 30 days of contract award, the Contractor shall designate a specific individual as the Commissioning Manager (CxM) to manage and lead the commissioning effort on behalf of the Contractor. The Commissioning Manager shall be the single point of contact and communications for all commissioning related services by the Contractor.

- Within 30 days of contract award, the Contractor shall ensure that each subcontractor designates specific individuals as Commissioning Representatives (CXR) to be responsible for commissioning related

tasks. The Contractor shall ensure the designated Commissioning Representatives participate in the commissioning process as team members providing commissioning testing services, equipment operation, adjustments, and corrections if necessary. The Contractor shall ensure that all Commissioning Representatives shall have sufficient authority to direct their respective staff to provide the services required, and to speak on behalf of their organizations in all commissioning related contractual matters.

  - QUALITY ASSURANCE

- Instructor Qualifications: Factory authorized service representatives shall be experienced in training, operation, and maintenance procedures for installed systems, subsystems, and equipment.

- Test Equipment Calibration: The Contractor shall comply with test equipment manufacturer's calibration procedures and intervals. Recalibrate test instruments immediately whenever instruments have been repaired following damage or dropping. Affix calibration tags to test instruments. Instruments shall have been calibrated within six months prior to use.

  - COORDINATION

- Management: The Commissioning Agent will coordinate the commissioning activities with the VA and Contractor. The Commissioning Agent will submit commissioning documents and information to the VA. All commissioning team members shall work together to fulfill their contracted responsibilities and meet the objectives of the contract documents.

- Scheduling: The Contractor shall work with the Commissioning Agent and the VA to incorporate the commissioning activities into the construction schedule. The Commissioning Agent will provide sufficient information (including, but not limited to, tasks, durations and predecessors) on commissioning activities to allow the Contractor and the VA to schedule commissioning activities. All parties shall address scheduling issues and make necessary notifications in a timely manner in order to expedite the project and the commissioning process. The Contractor shall update the Master Construction as directed by the VA.

- Initial Schedule of Commissioning Events: The Commissioning Agent will provide the initial schedule of primary commissioning events in the Commissioning Plan and at the commissioning coordination meetings. The

Commissioning Plan will provide a format for this schedule. As construction progresses, more detailed schedules will be developed by the Contractor with information from the Commissioning Agent.

- Commissioning Coordinating Meetings: The Commissioning Agent will conduct periodic Commissioning Coordination Meetings of the commissioning team to review status of commissioning activities, to discuss scheduling conflicts, and to discuss upcoming commissioning process activities.

- Pretesting Meetings: The Commissioning Agent will conduct pretest meetings of the commissioning team to review startup reports, Pre- Functional Checklist results, Systems Functional Performance Testing procedures, testing personnel and instrumentation requirements.

- Systems Functional Performance Testing Coordination: The Contractor shall coordinate testing activities to accommodate required quality assurance and control services with a minimum of delay and to avoid necessity of removing and replacing construction to accommodate testing and inspecting. The Contractor shall coordinate the schedule times for tests, inspections, obtaining samples, and similar activities.

PART 2 - PRODUCTS

    - TEST EQUIPMENT

      - The Contractor shall provide all standard and specialized testing equipment required to perform Systems Functional Performance Testing. Test equipment required for Systems Functional Performance Testing will be identified in the detailed System Functional Performance Test Procedure prepared by the Commissioning Agent.

      - Data logging equipment and software required to test equipment shall be provided by the Contractor.

      - All testing equipment shall be of sufficient quality and accuracy to test and/or measure system performance with the tolerances specified in the Specifications. If not otherwise noted, the following minimum requirements apply: Temperature sensors and digital thermometers shall have a certified calibration within the past year to an accuracy of 0.5 oC (1.0 oF) and a resolution of + or - 0.1 oC (0.2 oF). Pressure sensors shall have an accuracy of + or - 2.0% of the value range being measured (not full range of meter) and have been calibrated within the last year. All equipment shall be calibrated according to the manufacturer's

recommended intervals and following any repairs to the equipment. Calibration tags shall be affixed or certificates readily available.

PART 3 - EXECUTION

  - COMMISSIONING PROCESS ROLES AND RESPONSIBILITIES

    - The following table outlines the roles and responsibilities for the Commissioning Team members during the Construction Phase:

Spec Writer’s Notes: Edit the following tables to describe the roles and responsibilities for each commissioning team member for each of the commissioning tasks as appropriate for the project.

| Construction Phase |  | CxA = Commissioning Agent RE = Resident Engineer A/E = Design Arch/Engineer PC = Prime Contractor O&M = Gov’t Facility O&M |  |  |  |  | L = Lead P = Participate A = Approve R = Review O = Optional |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Commissioning Roles & Responsibilities |  |  |  |  |  |  |  |
| Category | Task Description | CxA | RE | A/E | PC | O&M | Notes |
| Meetings | Construction Commissioning Kick Off meeting | L | A | P | P | O |  |
|  | Commissioning Meetings | L | A | P | P | O |  |
|  | Project Progress Meetings | P | A | P | L | O |  |
|  | Controls Meeting | L | A | P | P | O |  |
| Coordination | Coordinate with [OGC's, AHJ, Vendors, etc.] to ensure that Cx interacts properly with other systems as needed to support the OPR and BOD. | L | A | P | P | N/A |  |
| Cx Plan & Spec | Final Commissioning Plan | L | A | R | R | O |  |
| Schedules | Duration Schedule for Commissioning Activities | L | A | R | R | N/A |  |

| Construction Phase |  | CxA = Commissioning Agent RE = Resident Engineer A/E = Design Arch/Engineer PC = Prime Contractor O&M = Gov’t Facility O&M |  |  |  |  | L = Lead P = Participate A = Approve R = Review O = Optional |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Commissioning Roles & Responsibilities |  |  |  |  |  |  |  |
| Category | Task Description | CxA | RE | A/E | PC | O&M | Notes |
| OPR and BOD | Maintain OPR on behalf of Owner | L | A | R | R | O |  |
|  | Maintain BOD/DID on behalf of Owner | L | A | R | R | O |  |
| Document Reviews | TAB Plan Review | L | A | R | R | O |  |
|  | Submittal and Shop Drawing Review | R | A | R | L | O |  |
|  | Review Contractor Equipment Startup Checklists | L | A | R | R | N/A |  |
|  | Review Change Orders, ASI, and RFI | L | A | R | R | N/A |  |
| Site Observations | Witness Factory Testing | P | A | P | L | O |  |
|  | Construction Observation Site Visits | L | A | R | R | O |  |
| Functional Test Protocols | Final Pre-Functional Checklists | L | A | R | R | O |  |
|  | Final Functional Performance Test Protocols | L | A | R | R | O |  |
| Technical Activities | Issues Resolution Meetings | P | A | P | L | O |  |

| Construction Phase |  | CxA = Commissioning Agent RE = Resident Engineer A/E = Design Arch/Engineer PC = Prime Contractor O&M = Gov’t Facility O&M |  |  |  |  | L = Lead P = Participate A = Approve R = Review O = Optional |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Commissioning Roles & Responsibilities |  |  |  |  |  |  |  |
| Category | Task Description | CxA | RE | A/E | PC | O&M | Notes |
| Reports and Logs | Status Reports | L | A | R | R | O |  |
|  | Maintain Commissioning Issues Log | L | A | R | R | O |  |

    - The following table outlines the roles and responsibilities for the Commissioning Team members during the Acceptance Phase:

| Acceptance Phase |  | CxA = Commissioning Agent RE = Resident Engineer A/E = Design Arch/Engineer PC = Prime Contractor O&M = Gov’t Facility O&M |  |  |  |  | L = Lead P = Participate A = Approve R = Review O = Optional |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Commissioning Roles & Responsibilities |  |  |  |  |  |  |  |
| Category | Task Description | CxA | RE | A/E | PC | O&M | Notes |
| Meetings | Commissioning Meetings | L | A | P | P | O |  |
|  | Project Progress Meetings | P | A | P | L | O |  |
|  | Pre-Test Coordination Meeting | L | A | P | P | O |  |
|  | Lessons Learned and Commissioning Report Review Meeting | L | A | P | P | O |  |

| Acceptance Phase |  | CxA = Commissioning Agent RE = Resident Engineer A/E = Design Arch/Engineer PC = Prime Contractor O&M = Gov’t Facility O&M |  |  |  |  | L = Lead P = Participate A = Approve R = Review O = Optional |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Commissioning Roles & Responsibilities |  |  |  |  |  |  |  |
| Category | Task Description | CxA | RE | A/E | PC | O&M | Notes |
| Coordination | Coordinate with [OGC's, AHJ, Vendors, etc.] to ensure that Cx interacts properly with other systems as needed to support OPR and BOD | L | P | P | P | O |  |
| Cx Plan & Spec | Maintain/Update Commissioning Plan | L | A | R | R | O |  |
| Schedules | Prepare Functional Test Schedule | L | A | R | R | O |  |
| OPR and BOD | Maintain OPR on behalf of Owner | L | A | R | R | O |  |
|  | Maintain BOD/DID on behalf of Owner | L | A | R | R | O |  |
| Document Reviews | Review Completed Pre-Functional Checklists | L | A | R | R | O |  |
|  | Pre-Functional Checklist Verification | L | A | R | R | O |  |
|  | Review Operations & Maintenance Manuals | L | A | R | R | R |  |
|  | Training Plan Review | L | A | R | R | R |  |
|  | Warranty Review | L | A | R | R | O |  |
|  | Review TAB Report | L | A | R | R | O |  |
| Site Observations | Construction Observation Site Visits | L | A | R | R | O |  |
|  | Witness Selected Equipment Startup | L | A | R | R | O |  |

| Acceptance Phase |  | CxA = Commissioning Agent RE = Resident Engineer A/E = Design Arch/Engineer PC = Prime Contractor O&M = Gov’t Facility O&M |  |  |  |  | L = Lead P = Participate A = Approve R = Review O = Optional |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Commissioning Roles & Responsibilities |  |  |  |  |  |  |  |
| Category | Task Description | CxA | RE | A/E | PC | O&M | Notes |
| Functional Test Protocols | TAB Verification | L | A | R | R | O |  |
|  | Systems Functional Performance Testing | L | A | P | P | P |  |
|  | Retesting | L | A | P | P | P |  |
| Technical Activities | Issues Resolution Meetings | P | A | P | L | O |  |
|  | Systems Training | L | S | R | P | P |  |
| Reports and Logs | Status Reports | L | A | R | R | O |  |
|  | Maintain Commissioning Issues Log | L | A | R | R | O |  |
|  | Final Commissioning Report | L | A | R | R | R |  |
|  | Prepare Systems Manuals | L | A | R | R | R |  |

    - The following table outlines the roles and responsibilities for the Commissioning Team members during the Warranty Phase:

| Warranty Phase |  | CxA = Commissioning Agent RE = Resident Engineer A/E = Design Arch/Engineer PC = Prime Contractor O&M = Gov’t Facility O&M |  |  |  |  | L = Lead P = Participate A = Approve R = Review O = Optional |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Commissioning Roles & Responsibilities |  |  |  |  |  |  |  |
| Category | Task Description | CxA | RE | A/E | PC | O&M | Notes |
| Meetings | Post-Occupancy User Review Meeting | L | A | O | P | P |  |
| Site Observations | Periodic Site Visits | L | A | O | O | P |  |
| Functional Test Protocols | Deferred and/or seasonal Testing | L | A | O | P | P |  |
| Technical Activities | Issues Resolution Meetings | L | S | O | O | P |  |
|  | Post-Occupancy Warranty Checkup and review of Significant Outstanding Issues | L | A |  | R | P |  |
| Reports and Logs | Final Commissioning Report Amendment | L | A |  | R | R |  |
|  | Status Reports | L | A |  | R | R |  |

  - STARTUP, INITIAL CHECKOUT, AND PRE-FUNCTIONAL CHECKLISTS

    - The following procedures shall apply to all equipment and systems to be commissioned, according to Part 1, Systems to Be Commissioned.

      - Pre-Functional Checklists are important to ensure that the equipment and systems are hooked up and operational. These ensure that Systems Functional Performance Testing may proceed without unnecessary delays. Each system to be commissioned shall have a full Pre- Functional Checklist completed by the Contractor prior to Systems Functional Performance Testing. No sampling strategies are used.

        - The Pre-Functional Checklist will identify the trades responsible for completing the checklist. The Contractor shall ensure the appropriate trades complete the checklists.

        - The Commissioning Agent will review completed Pre-Functional Checklists and field-verify the accuracy of the completed checklist using sampling techniques.

      - Startup and Initial Checkout Plan: The Contractor shall develop detailed startup plans for all equipment. The primary role of the Contractor in this process is to ensure that there is written documentation that each of the manufacturer recommended procedures have been completed. Parties responsible for startup shall be identified in the Startup Plan and in the checklist forms.

        - The Contractor shall develop the full startup plan by combining (or adding to) the checklists with the manufacturer's detailed startup and checkout procedures from the O&M manual data and the field checkout sheets normally used by the Contractor. The plan shall include checklists and procedures with specific boxes or lines for recording and documenting the checking and inspections of each procedure and a summary statement with a signature block at the end of the plan.

        - The full startup plan shall at a minimum consist of the following items:

          - The Pre-Functional Checklists.

          - The manufacturer's standard written startup procedures copied from the installation manuals with check boxes by each procedure and a signature block added by hand at the end.

          - The manufacturer's normally used field checkout sheets.

        - The Commissioning Agent will submit the full startup plan to the VA and Contractor for review. Final approval will be by the VA.

        - The Contractor shall review and evaluate the procedures and the format for documenting them, noting any procedures that need to be revised or added.

      - Sensor and Actuator Calibration

        - All field installed temperature, relative humidity, CO2 and pressure sensors and gages, and all actuators (dampers and valves) on all equipment shall be calibrated using the methods described in Division 21, Division 22, Division 23, Division 26,

Division 27, and Division 28 specifications.

        - All procedures used shall be fully documented on the Pre- Functional Checklists or other suitable forms, clearly referencing the procedures followed and written documentation of initial, intermediate and final results.

      - Execution of Equipment Startup

        - Four weeks prior to equipment startup, the Contractor shall schedule startup and checkout with the VA and Commissioning Agent. The performance of the startup and checkout shall be directed and executed by the Contractor.

        - The Commissioning Agent will observe the startup procedures for selected pieces of primary equipment.

        - The Contractor shall execute startup and provide the VA and Commissioning Agent with a signed and dated copy of the completed startup checklists, and contractor tests.

        - Only individuals that have direct knowledge and witnessed that a line item task on the Startup Checklist was actually performed shall initial or check that item off. It is not acceptable for witnessing supervisors to fill out these forms.

  - DEFICIENCIES, NONCONFORMANCE, AND APPROVAL IN CHECKLISTS AND STARTUP

    - The Contractor shall clearly list any outstanding items of the initial startup and Pre-Functional Checklist procedures that were not completed successfully, at the bottom of the procedures form or on an attached sheet. The procedures form and any outstanding deficiencies shall be provided to the VA and the Commissioning Agent within two days of completion.

    - The Commissioning Agent will review the report and submit comments to the VA. The Commissioning Agent will work with the Contractor to correct and verify deficiencies or uncompleted items. The Commissioning Agent will involve the VA and others as necessary. The Contractor shall correct all areas that are noncompliant or incomplete in the checklists in a timely manner, and shall notify the VA and Commissioning Agent as soon as outstanding items have been corrected. The Contractor shall submit an updated startup report and a Statement of Correction on the original noncompliance report. When satisfactorily completed, the Commissioning Agent will recommend approval of the checklists and startup of each system to the VA.

    - The Contractor shall be responsible for resolution of deficiencies as directed the VA.

  - PHASED COMMISSIONING

    - The project may require startup and initial checkout to be executed in phases. This phasing shall be planned and scheduled in a coordination meeting of the VA, Commissioning Agent, and the Contractor. Results will be added to the master construction schedule and the commissioning schedule. See ICRA phasing, as each TR room represents a phase. ICRA is indicated on the drawings.

  - DDC SYSTEM TRENDING FOR COMMISSIONING

    - Trending is a method of testing as a standalone method or to augment manual testing. The Contractor shall trend any and all points of the system or systems at intervals specified below.

    - Alarms are a means to notify the system operator that abnormal conditions are present in the system. Alarms shall be structured into three tiers – Critical, Priority, and Maintenance.

      - Critical alarms are intended to be alarms that require the immediate attention of and action by the Operator. These alarms shall be displayed on the Operator Workstation in a popup style window that is graphically linked to the associated unit's graphical display. The popup style window shall be displayed on top of any active window within the screen, including non DDC system software.

      - Priority level alarms are to be printed to a printer which is connected to the Operator’s Work Station located within the engineer’s office. Additionally Priority level alarms shall be able to be monitored and viewed through an active alarm application.

Priority level alarms are alarms which shall require reaction from the operator or maintenance personnel within a normal work shift, and not immediate action.

      - Maintenance alarms are intended to be minor issues which would require examination by maintenance personnel within the following shift. These alarms shall be generated in a scheduled report automatically by the DDC system at the start of each shift. The generated maintenance report will be printed to a printer located within the engineer’s office.

  - SYSTEMS FUNCTIONAL PERFORMANCE TESTING

    - This paragraph applies to Systems Functional Performance Testing of systems for all referenced specification Divisions.

    - Objectives and Scope: The objective of Systems Functional Performance Testing is to demonstrate that each system is operating according to the Contract Documents. Systems Functional Performance Testing facilitates bringing the systems from a state of substantial completion to full dynamic operation. Additionally, during the testing process, areas of noncompliant performance are identified and corrected, thereby improving the operation and functioning of the systems. In general, each system shall be operated through all modes of operation (seasonal, occupied, unoccupied, warm-up, cool-down, part- and full-load, fire alarm and emergency power) where there is a specified system response. The Contractor shall verify each sequence in the sequences of operation. Proper responses to such modes and conditions as power failure, freeze condition, low oil pressure, no flow, equipment failure, etc. shall also be tested.

    - Development of Systems Functional Performance Test Procedures: Before Systems Functional Performance Test procedures are written, the Contractor shall submit all requested documentation and a current list of change orders affecting equipment or systems, including an updated points list, program code, control sequences and parameters. Using the testing parameters and requirements found in the Contract Documents and approved submittals and shop drawings, the Commissioning Agent will develop specific Systems Functional Test Procedures to verify and document proper operation of each piece of equipment and system to be commissioned. The Contractor shall assist the Commissioning Agent in developing the Systems Functional Performance Test procedures as requested by the Commissioning Agent i.e. by answering questions about equipment, operation, sequences, etc. Prior to execution, the Commissioning Agent will provide a copy of the Systems Functional Performance Test procedures to the VA, the Architect/Engineer, and the Contractor, who shall review the tests for feasibility, safety, equipment and warranty protection.

    - Purpose of Test Procedures: The purpose of each specific Systems Functional Performance Test is to verify and document compliance with the stated criteria of acceptance given on the test form.

Representative test formats and examples are found in the Commissioning Plan for this project. (The Commissioning Plan is issued as a separate document and is available for review.) The test procedure forms developed by the Commissioning Agent will include, but not be limited to, the following information:

      - System and equipment or component name(s)

      - Equipment location and ID number

      - Unique test ID number, and reference to unique Pre-Functional Checklists and startup documentation, and ID numbers for the piece of equipment

      - Date

      - Project name

      - Participating parties

      - A copy of the specification section describing the test requirements

      - A copy of the specific sequence of operations or other specified parameters being verified

      - Formulas used in any calculations

      - Required pretest field measurements

      - Instructions for setting up the test.

      - Special cautions, alarm limits, etc.

      - Specific step-by-step procedures to execute the test, in a clear, sequential and repeatable format

      - Acceptance criteria of proper performance with a Yes / No check box to allow for clearly marking whether or not proper performance of each part of the test was achieved.

      - A section for comments.

      - Signatures and date block for the Commissioning Agent. A place for the Contractor to initial to signify attendance at the test.

    - Test Methods: Systems Functional Performance Testing shall be achieved by manual testing (i.e. persons manipulate the equipment and observe performance) and/or by monitoring the performance and analyzing the results using the control system's trend log capabilities or by standalone data loggers. The Contractor and Commissioning Agent shall determine which method is most appropriate for tests that do not have a method specified.

      - Simulated Conditions: Simulating conditions (not by an overwritten value) shall be allowed, although timing the testing to experience actual conditions is encouraged wherever practical.

      - Overwritten Values: Overwriting sensor values to simulate a condition, such as overwriting the outside air temperature reading in a control system to be something other than it really is, shall be allowed, but shall be used with caution and avoided when possible. Such testing methods often can only test a part of a system, as the interactions and responses of other systems will be erroneous or not applicable. Simulating a condition is preferable. e.g., for the above case, by heating the outside air sensor with a hair blower rather than overwriting the value or by altering the appropriate setpoint to see the desired response. Before simulating conditions or overwriting values,	sensors, transducers and devices shall have been calibrated.

      - Simulated Signals: Using a signal generator which creates a simulated signal to test and calibrate transducers and DDC constants is generally recommended over using the sensor to act as the signal generator via simulated conditions or overwritten values.

      - Altering Setpoints: Rather than overwriting sensor values, and when simulating conditions is difficult, altering setpoints to test a sequence is acceptable. For example, to see the Air Conditioning compressor lockout initiate at an outside air temperature below 12 C (54 F), when the outside air temperature is above 12 C (54 F), temporarily change the lockout setpoint to be 2 C (4 F) above the current outside air temperature.

      - Indirect Indicators: Relying on indirect indicators for responses or performance shall be allowed only after visually and directly verifying and documenting, over the range of the tested parameters, that the indirect readings through the control system represent actual conditions and responses. Much of this verification shall be completed during systems startup and initial checkout.

    - Setup: Each function and test shall be performed under conditions that simulate actual conditions as closely as is practically possible. The Contractor shall provide all necessary materials, system modifications, etc. to produce the necessary flows, pressures, temperatures, etc. necessary to execute the test according to the specified conditions. At

completion of the test, the Contractor shall return all affected building equipment and systems, due to these temporary modifications, to their pretest condition.

    - Sampling: No sampling is allowed in completing Pre-Functional Checklists.	Sampling is allowed for Systems Functional Performance Test Procedures execution. The Commissioning Agent will determine the sampling rate. If at any point, frequent failures are occurring and testing is becoming more troubleshooting than verification, the Commissioning Agent may stop the testing and require the Contractor to perform and document a checkout of the remaining units, prior to continuing with Systems Functional Performance Testing of the remaining units.

    - Cost of Retesting: The cost associated with expanded sample System Functional Performance Tests shall be solely the responsibility of the Contractor. Any required retesting by the Contractor shall not be considered a justified reason for a claim of delay or for a time extension by the Contractor.

    - Coordination and Scheduling: The Contractor shall provide a minimum of

7 days’ notice to the Commissioning Agent and the VA regarding the completion schedule for the Pre-Functional Checklists and startup of all equipment and systems. The Commissioning Agent will schedule Systems Functional Performance Tests with the Contractor and VA. The Commissioning Agent will witness and document the Systems Functional Performance Testing of systems. The Contractor shall execute the tests in accordance with the Systems Functional Performance Test Procedure.

    - Testing Prerequisites: In general, Systems Functional Performance Testing will be conducted only after Pre-Functional Checklists have been satisfactorily completed. The control system shall be sufficiently tested and approved by the Commissioning Agent and the VA before it is used to verify performance of other components or systems. The air balancing and water balancing shall be completed before Systems Functional Performance Testing of air-related or water-related equipment or systems are scheduled. Systems Functional Performance Testing will proceed from components to subsystems to systems. When the proper performance of all interacting individual systems has been

achieved, the interface or coordinated responses between systems will be checked.

    - Problem Solving: The Commissioning Agent will recommend solutions to problems found, however the burden of responsibility to solve, correct and retest problems is with the Contractor.

  - DOCUMENTATION, NONCONFORMANCE AND APPROVAL OF TESTS

    - Documentation: The Commissioning Agent will witness, and document the results of all Systems Functional Performance Tests using the specific procedural forms developed by the Commissioning Agent for that purpose. Prior to testing, the Commissioning Agent will provide these forms to the VA and the Contractor for review and approval. The Contractor shall include the filled out forms with the O&M manual data.

    - Nonconformance: The Commissioning Agent will record the results of the Systems Functional Performance Tests on the procedure or test form. All items of nonconformance issues will be noted and reported to the VA on Commissioning Field Reports and/or the Commissioning Master Issues Log.

      - Corrections of minor items of noncompliance identified may be made during the tests. In such cases, the item of noncompliance and resolution shall be documented on the Systems Functional Test Procedure.

      - Every effort shall be made to expedite the systems functional Performance Testing process and minimize unnecessary delays, while not compromising the integrity of the procedures. However, the Commissioning Agent shall not be pressured into overlooking noncompliant work or loosening acceptance criteria to satisfy scheduling or cost issues, unless there is an overriding reason to do so by direction from the VA.

      - As the Systems Functional Performance Tests progresses and an item of noncompliance is identified, the Commissioning Agent shall discuss the issue with the Contractor and the VA.

      - When there is no dispute on an item of noncompliance, and the Contractor accepts responsibility to correct it:

        - The Commissioning Agent will document the item of noncompliance and the Contractor's response and/or intentions. The Systems Functional Performance Test then continues or proceeds to another test or sequence. After the day's work is complete, the Commissioning Agent will submit a Commissioning Field Report to

the VA. The Commissioning Agent will also note items of noncompliance and the Contractor’s response in the Master Commissioning Issues Log. The Contractor shall correct the item of noncompliance and report completion to the VA and the Commissioning Agent.

        - The need for retesting will be determined by the Commissioning Agent. If retesting is required, the Commissioning Agent and the Contractor shall reschedule the test and the test shall be repeated.

      - If there is a dispute about item of noncompliance, regarding whether it is an item of noncompliance, or who is responsible:

        - The item of noncompliance shall be documented on the test form with the Contractor's response. The item of noncompliance with the Contractor’s response shall also be reported on a Commissioning Field Report and on the Master Commissioning Issues Log.

        - Resolutions shall be made at the lowest management level possible. Other parties are brought into the discussions as needed. Final interpretive and acceptance authority is with the Department of Veterans Affairs.

        - The Commissioning Agent will document the resolution process.

        - Once the interpretation and resolution have been decided, the Contractor shall correct the item of noncompliance, report it to the Commissioning Agent. The requirement for retesting will be determined by the Commissioning Agent. If retesting is required, the Commissioning Agent and the Contractor shall reschedule the test. Retesting shall be repeated until satisfactory performance is achieved.

Spec Writer Note: Verify that the following paragraph regarding cost of retesting is allowed for the specific project. Retain or delete the paragraph as necessary.

    - Cost of Retesting: The cost to retest a System Functional Performance Test shall be solely the responsibility of the Contractor. Any required retesting by the Contractor shall not be considered a

justified reason for a claim of delay or for a time extension by the Contractor.

Spec Writer’s Note: Verify that the paragraph and subparagraphs below do not conflict with other general or specific contract documents regarding manufacturer’s defects. Retain, delete, or modify the paragraphs accordingly.

    - Failure Due to Manufacturer Defect: If 10%, or three, whichever is greater, of identical pieces (size alone does not constitute a difference) of equipment fail to perform in compliance with the Contract Documents (mechanically or substantively) due to manufacturing defect, not allowing it to meet its submitted performance specifications, all identical units may be considered unacceptable by the VA. In such case, the Contractor shall provide the VA with the following:

      - Within one week of notification from the VA, the Contractor shall examine all other identical units making a record of the findings. The findings shall be provided to the VA within two weeks of the original notice.

      - Within two weeks of the original notification, the Contractor shall provide a signed and dated, written explanation of the problem, cause of failures, etc. and all proposed solutions which shall include full equipment submittals. The proposed solutions shall not significantly exceed the specification requirements of the original installation.

      - The VA shall determine whether a replacement of all identical units or a repair is acceptable.

      - Two examples of the proposed solution shall be installed by the Contractor and the VA shall be allowed to test the installations for up to one week, upon which the VA will decide whether to accept the solution.

      - Upon acceptance, the Contractor shall replace or repair all identical items, at their expense and extend the warranty accordingly, if the original equipment warranty had begun. The replacement/repair work shall proceed with reasonable speed beginning within one week from when parts can be obtained.

    - Approval: The Commissioning Agent will note each satisfactorily demonstrated function on the test form. Formal approval of the Systems Functional Performance Test shall be made later after review by the Commissioning Agent and by the VA. The Commissioning Agent will evaluate each test and report to the VA using a standard form. The VA will give final approval on each test using the same form, and provide signed copies to the Commissioning Agent and the Contractor.

  - DEFERRED TESTING

    - Unforeseen Deferred Systems Functional Performance Tests: If any Systems Functional Performance Test cannot be completed due to the building structure, required occupancy condition or other conditions, execution of the Systems Functional Performance Testing may be delayed upon approval of the VA. These Systems Functional Performance Tests shall be conducted in the same manner as the seasonal tests as soon as possible. Services of the Contractor to conduct these unforeseen Deferred Systems Functional Performance Tests shall be negotiated between the VA and the Contractor.

    - Deferred Seasonal Testing: Deferred Seasonal Systems Functional Performance Tests are those that must be deferred until weather conditions are closer to the systems design parameters. The Commissioning Agent will review systems parameters and recommend which Systems Functional Performance Tests should be deferred until weather conditions more closely match systems parameters. The Contractor shall review and comment on the proposed schedule for Deferred Seasonal Testing. The VA will review and approve the schedule for Deferred Seasonal Testing. Deferred Seasonal Systems Functional Performances Tests shall be witnessed and documented by the Commissioning Agent. Deferred Seasonal Systems Functional Performance Tests shall be executed by the Contractor in accordance with these specifications.

  - OPERATION AND MAINTENANCE TRAINING REQUIREMENTS

    - Training Preparation Conference: Before operation and maintenance training, the Commissioning Agent will convene a training preparation conference to include VA's Resident Engineer, VA’s Operations and Maintenance personnel, and the Contractor. The purpose of this conference will be to discuss and plan for Training and Demonstration of VA Operations and Maintenance personnel.

    - The Contractor shall provide training and demonstration as required by other Division 21, Division 22, Division 23, Division 26, Division 27, Division 28, and Division 31 sections. The Training and Demonstration shall include, but is not limited to, the following:

      - Review the Contract Documents.

      - Review installed systems, subsystems, and equipment.

      - Review instructor qualifications.

      - Review instructional methods and procedures.

      - Review training module outlines and contents.

      - Review course materials (including operation and maintenance manuals).

      - Review and discuss locations and other facilities required for instruction.

      - Review and finalize training schedule and verify availability of educational materials, instructors, audiovisual equipment, and facilities needed to avoid delays.

      - For instruction that must occur outside, review weather and forecasted weather conditions and procedures to follow if conditions are unfavorable.

    - Training Module Submittals: The Contractor shall submit the following information to the VA and the Commissioning Agent:

      - Instruction Program: Submit two copies of outline of instructional program for demonstration and training, including a schedule of proposed dates, times, length of instruction time, and instructors' names for each training module. Include learning objective and outline for each training module. At completion of training, submit two complete training manuals for VA's use.

      - Qualification Data: Submit qualifications for facilitator and/or instructor.

      - Attendance Record: For each training module, submit list of participants and length of instruction time.

      - Evaluations: For each participant and for each training module, submit results and documentation of performance-based test.

      - Demonstration and Training Recording:

        - General: Engage a qualified commercial photographer to record demonstration and training. Record each training module separately. Include classroom instructions and demonstrations,

board diagrams, and other visual aids, but not student practice. At beginning of each training module, record each chart containing learning objective and lesson outline.

        - Video Format: Provide high quality color DVD color on standard size DVD disks.

        - Recording: Mount camera on tripod before starting recording, unless otherwise necessary to show area of demonstration and training. Display continuous running time.

        - Narration: Describe scenes on video recording by audio narration by microphone while demonstration and training is recorded. Include description of items being viewed. Describe vantage point, indicating location, direction (by compass point), and elevation or story of construction.

        - Submit two copies within seven days of end of each training module.

      - Transcript: Prepared on 8-1/2-by-11-inch paper, punched and bound in heavy-duty, 3-ring, vinyl-covered binders. Mark appropriate identification on front and spine of each binder. Include a cover sheet with same label information as the corresponding videotape. Include name of Project and date of videotape on each page.

    - Quality Assurance:

      - Facilitator Qualifications: A firm or individual experienced in training or educating maintenance personnel in a training program similar in content and extent to that indicated for this Project, and whose work has resulted in training or education with a record of successful learning performance.

      - Instructor Qualifications: A factory authorized service representative, complying with requirements in Division 01 Section "Quality Requirements," experienced in operation and maintenance procedures and training.

      - Photographer Qualifications: A professional photographer who is experienced photographing construction projects.

    - Training Coordination:

      - Coordinate instruction schedule with VA's operations. Adjust schedule as required to minimize disrupting VA's operations.

      - Coordinate instructors, including providing notification of dates, times, length of instruction time, and course content.

      - Coordinate content of training modules with content of approved emergency, operation, and maintenance manuals. Do not submit instruction program until operation and maintenance data has been reviewed and approved by the VA.

    - Instruction Program:

      - Program Structure: Develop an instruction program that includes individual training modules for each system and equipment not part of a system, as required by individual Specification Sections, and as follows:

        - Fire protection systems, including fire alarm, fire pumps, and fire suppression systems.

        - Intrusion detection systems.

        - Conveying systems, including elevators, wheelchair lifts, escalators, and automated materials handling systems.

        - Medical equipment, including medical gas equipment and piping.

        - Laboratory equipment, including laboratory air and vacuum equipment and piping.

        - Heat generation, including boilers, feedwater equipment, pumps, steam distribution piping, condensate return systems, heating hot water heat exchangers, and heating hot water distribution piping.

        - Refrigeration systems, including chillers, cooling towers, condensers, pumps, and distribution piping.

        - HVAC systems, including air handling equipment, air distribution systems, and terminal equipment and devices.

        - HVAC instrumentation and controls.

        - Electrical service and distribution, including switchgear, transformers, switchboards, panelboards, uninterruptible power supplies, and motor controls.

        - Packaged engine generators, including synchronizing switchgear/switchboards, and transfer switches.

        - Lighting equipment and controls.

        - Communication systems, including intercommunication, surveillance, nurse call systems, public address, mass evacuation, voice and data, and entertainment television equipment.

        - Site utilities including lift stations, condensate pumping and return systems, and storm water pumping systems.

    - Training Modules: Develop a learning objective and teaching outline for each module. Include a description of specific skills and knowledge that participants are expected to master. For each module, include instruction for the following:

      - Basis of System Design, Operational Requirements, and Criteria: Include the following:

        - System, subsystem, and equipment descriptions.

        - Performance and design criteria if Contractor is delegated design responsibility.

        - Operating standards.

        - Regulatory requirements.

        - Equipment function.

        - Operating characteristics.

        - Limiting conditions. H, Performance curves.

      - Documentation: Review the following items in detail:

        - Emergency manuals.

        - Operations manuals.

        - Maintenance manuals.

        - Project Record Documents.

        - Identification systems.

        - Warranties and bonds.

        - Maintenance service agreements and similar continuing commitments.

      - Emergencies: Include the following, as applicable:

        - Instructions on meaning of warnings, trouble indications, and error messages.

        - Instructions on stopping.

        - Shutdown instructions for each type of emergency.

        - Operating instructions for conditions outside of normal operating limits.

        - Sequences for electric or electronic systems.

        - Special operating instructions and procedures.

      - Operations: Include the following, as applicable:

        - Startup procedures.

        - Equipment or system break-in procedures.

        - Routine and normal operating instructions.

        - Regulation and control procedures.

        - Control sequences.

        - Safety procedures.

        - Instructions on stopping.

        - Normal shutdown instructions.

        - Operating procedures for emergencies.

        - Operating procedures for system, subsystem, or equipment failure.

        - Seasonal and weekend operating instructions.

        - Required sequences for electric or electronic systems.

        - Special operating instructions and procedures.

      - Adjustments: Include the following:

        - Alignments.

        - Checking adjustments.

        - Noise and vibration adjustments.

        - Economy and efficiency adjustments.

      - Troubleshooting: Include the following:

        - Diagnostic instructions.

        - Test and inspection procedures.

      - Maintenance: Include the following:

        - Inspection procedures.

        - Types of cleaning agents to be used and methods of cleaning.

        - List of cleaning agents and methods of cleaning detrimental to product.

        - Procedures for routine cleaning

        - Procedures for preventive maintenance.

        - Procedures for routine maintenance.

        - Instruction on use of special tools.

      - Repairs: Include the following:

        - Diagnosis instructions.

        - Repair instructions.

        - Disassembly; component removal, repair, and replacement; and reassembly instructions.

        - Instructions for identifying parts and components.

        - Review of spare parts needed for operation and maintenance.

    - Training Execution:

      - Preparation: Assemble educational materials necessary for instruction, including documentation and training module. Assemble

training modules into a combined training manual. Set up instructional equipment at instruction location.

      - Instruction:

        - Facilitator: Engage a qualified facilitator to prepare instruction program and training modules, to coordinate instructors, and to coordinate between Contractor and Department of Veterans Affairs for number of participants, instruction times, and location.

        - Instructor: Engage qualified instructors to instruct VA's personnel to adjust, operate, and maintain systems, subsystems, and equipment not part of a system.

          - The Commissioning Agent will furnish an instructor to describe basis of system design, operational requirements, criteria, and regulatory requirements.

          - The VA will furnish an instructor to describe VA's operational philosophy.

          - The VA will furnish the Contractor with names and positions of participants.

      - Scheduling: Provide instruction at mutually agreed times. For equipment that requires seasonal operation, provide similar instruction at start of each season. Schedule training with the VA and the Commissioning Agent with at least seven days' advance notice.

      - Evaluation: At conclusion of each training module, assess and document each participant's mastery of module by use of an oral, or a written, performance-based test.

      - Cleanup: Collect used and leftover educational materials and remove from Project site. Remove instructional equipment. Restore systems and equipment to condition existing before initial training use.

    - Demonstration and Training Recording:

      - General: Engage a qualified commercial photographer to record demonstration and training. Record each training module separately. Include classroom instructions and demonstrations, board diagrams, and other visual aids, but not student practice. At beginning of each training module, record each chart containing learning objective and lesson outline.

      - Video Format: Provide high quality color DVD color on standard size DVD disks.

      - Recording: Mount camera on tripod before starting recording, unless otherwise necessary to show area of demonstration and training. Display continuous running time.

      - Narration: Describe scenes on videotape by audio narration by microphone while demonstration and training is recorded. Include description of items being viewed. Describe vantage point, indicating location, direction (by compass point), and elevation or story of construction.

END

SECTION 02 21 13 SITE SURVEYS

PART 1 - GENERAL

  - SUMMARY

    - Section Includes:

      - Researching and collecting documents informing surveys.

      - Performing utility survey.

      - Creating utility survey drawings.

  - APPLICABLE PUBLICATIONS

    - Comply with references to extent specified in this section.

    - Federal Geographic Data Committee (FGDC):

      - STD-007.03-98 - Geospatial Positioning Accuracy Standards Part 3: National Standard for Spatial Data Accuracy.

      - STD-007.04-02 - Geospatial Positioning Accuracy Standards Part 4: Standards for Architecture, Engineering, Construction (A/E/C) and Facility Management.

  - SUBMITTALS

    - Survey Drawings, as described in section 3.4.

  - QUALITY ASSURANCE

    - Land Surveyor: One of the following:

      - Professional Land Surveyor: One who possesses a valid state license as a "Professional Land Surveyor" from the state in which they practice, and where the project is located.

      - Professional Civil Engineer: One who possesses a valid state license as a "Professional Civil Engineer" from the state in which they practice, and where the project is located. For this section, the term "land surveyor" shall also include Professional Civil Engineers authorized to practice Land Surveying under the laws of the state in which they practice.

PART 2 - PRODUCTS

        - ACCESSORIES

          - Monuments: Iron pin, with driven 16 mm (5/8 inch) diameter, minimum 600 mm (24 inches) long to prevent displacement.

          - Stakes: Hardwood.

          - Flagging: Plastic, roll form, highly visible, solid color.

PART 3 - EXECUTION

  - EXAMINATION

    - Research public and VA facility records for deeds, maps, monuments, plats, surveys, title certificates or abstracts, rights-of-way, easements, section line, other boundary line locations, and other documents pertaining to project site.

    - Research public and VA facility utility records for aerial, surface, and subgrade structures and utility service lines and easements.

  - PREPARATION

    - Coordinate with Contracting Officer's Representative for site access.

    - Coordinate with adjacent property owners when access to adjoining properties is required.

      - Notify Contracting Officer's Representative when access is denied.

  - SURVEYS

    - Perform survey on ground according to the latest version of FGDC STD-007.3 and FGDC STD-007.4.

    - Utility Survey:

      - Locate piped utilities and utility structures. Identify service type, material, sizes, depths, and pressures. Establish inverts in and out on gravity sewer manholes. If depth is critical and manholes are not available identify depth with ground-penetrating radar (GPR).

      - Locate fire hydrants.

      - Locate wired utilities and utility structures. Identify service type, rated capacities, and elevations above and below grade.

      - Identify each utility authority including contact person and phone number.

    - Locate permanent structures within survey boundary by perpendicular dimension to property lines.

      - Determine structure plan dimensions, heights, and vertical offsets.

      - Determine projections and overhangs beyond structure footprint at grade.

      - Determine number of stories and primary building materials.

    - Locate rights-of-way, easements and encumbrances within and adjacent to survey boundary by perpendicular dimension to property line(s).

      - Locate project site access from rights-of-way by dimension from survey monument. Determine site access width.

  - SURVEY DRAWING REQUIREMENTS

    - Consult Contracting Officer's Representative to confirm the required survey scale and drawing size.

      - Drawing Size to plot: Maximum 760 by 1070 mm (30 by 42 inches).

      - Enlarged Detail Areas: Scale as required to present dimensional data and survey information clearly. Maintain orientation aligned with smaller scale view.

      - Plan Orientation: North at top of drawing sheet.

      - Unless specifically noted otherwise, develop electronic drawings files of the survey in accordance with the VA BIM Standard as required by PG-18-15 (https://www.cfm.va.gov/til/aeDesSubReq.asp) and VA's BIM Manual (https://www.cfm.va.gov/til/projReq.asp) (refer to section 2.3 BIM Technology and Platforms for CAD/BIM software). Verify software version with VA Project Manager / VA CAD/BIM Standards Manager.

      - Electronic files must be in accordance with the VA BIM Standard as required by PG-18-15 (https://www.cfm.va.gov/til/aeDesSubReq.asp) and VA's BIM Manual (https://www.cfm.va.gov/til/projReq.asp).

      - Electronic drawings files must be submitted in their native authoring software (AUTOCAD .dwg, AutoCAD Civil 3D, REVIT. rvt, etc. formats), and in PDF format.

      - Provide a photographic record (in hard and digital formats) of relevant or key features of the surveyed land.

      - Provide all field raw data files, field notes, field survey points, raw aerial mapping CAD files, LiDAR point clouds, photogrammetric drone image files, and all ground control data used for any remote (aerial, LiDAR, drone) mapping methods.

      - Remote Mapping: All data captured through LiDAR scanning, photogrammetric drone mapping, and when authorized, manned aerial mapping, is to be completely combined with all field survey data. Separate files containing data from different collection methods will not be accepted.

    - Drawing Notations:

      - Provide notes that the two installed monuments tied to the State Plane Coordinate system are the basis for the coordinate system indicated on the CADD survey drawings.

      - Land Surveyor: Name, address, telephone number, signature, seal, and registration number.

      - Survey Dates: Date survey was initially completed and subsequent revision dates.

      - Certification: Certify each drawing adjacent to land surveyor's seal:

      - "I hereby certify that all information indicated on this drawing was obtained or verified by actual measurements in the field and that every effort has been made to provide complete and accurate information."

      - Title, number, and total number of drawings on each drawing.

      - Scale in metric and imperial measurement.

      - Graphic scale in metric and imperial measurement.

      - Graphic symbol and abbreviation legends.

      - North arrow for plan view drawings.

      - Horizontal and vertical control datum.

      - Evidence of Possession: Indicate character and location of evidence of possession affecting project site. Notation absence signifies no observable evidence of possession.

    - Record Documents Forming Survey Basis: Indicate titles, source, and recording data of documents relied upon to complete survey.

    - Lots and Parcels: Indicate entire lots and parcels included within and intersected by survey boundary.

    - Structures and Site Improvements: Indicate buildings, and other visible improvements such as walls, fences, signs, parking areas, plazas, planter beds, benches, swimming pools, etc.

      - Indicate each building dimensioned to property lines and other structures.

      - Indicate exterior dimensions of buildings at ground level. Show area of exterior building footprint and gross floor area of entire building.

      - Indicate the number of stories and maximum measured height of all buildings above grade at a defined location. If no defined location is provided, the point of measurement shall be shown.

      - Indicate spot elevations at building entrances, first floor, service docks, corners, steps, ramps, and grade slabs.

      - Indicate structures and site improvements within 1500 mm (5 feet) of survey boundary.

      - Indicate encroachments on project site, adjoining property, easements, rights-of-way, and setback lines from fire escapes, bay windows, windows and doors opening out, flue pipes, stoops, eaves, cornices, areaways, stoops, other building projections, and site improvements.

      - Identify and show setback, height, and floor space area restrictions set by applicable zoning and building codes, and recorded subdivision maps. Indicate if no restrictions exist.

    - Easements:

      - Indicate easements evidenced by recorded documents.

        - Indicate when easements cannot be located.

      - Indicate observable easements created by roadways, rights-of-ways, water courses, drains, telephone, telegraph, electric and other wiring, water, sewer, oil, gas, and other pipelines within project site and on adjoining properties when potentially affecting project site.

      - Indicate observable surface improvements of underground easements.

    - Public and Private Utilities:

      - Indicate information source and operating authority for each utility.

      - Indicate utilities existing on or serving project site.

      - Indicate fire hydrants on project site and within 150 m (500 feet) of survey boundary.

      - Indicate manholes, catch basins, inlets, vaults, and other surface indications of subgrade services.

      - Indicate depths or invert elevations, sizes, materials, and pressures of utility pipes.

      - Indicate wires and cables serving, crossing, and adjacent to project site.

      - Indicate exterior lighting, traffic control facilities, security, and communications systems.

      - Indicate utility poles on project site and within 3 m (10 feet) of survey boundary.

      - Indicate dimensions of cross-wires or overhangs affecting project site.

    - Observable Evidence:

      - Indicate in-progress and recently completed earth moving work, building construction, and building additions.

      - Indicate in-progress and recently completed pavement construction and repairs.

      - Indicate observable evidence of site areas used as solid waste dump, sump, and sanitary landfill.

    - Trees:

      - Indicate individual trees with minimum 150 mm (6 inches) diameter measured at 1200 mm (48 inches) above grade.

      - Indicate wooded area perimeter outline and description of predominant vegetation.

- - - E N D - - -

PART 1 - GENERAL

  - DESCRIPTION

SECTION 02 41 10 DEMOLITION AND SITE CLEARING

    - This section specifies all site preparation work, demolition and removal of buildings, portions of buildings, utilities, other structures and debris from trash dumps shown.

  - RELATED WORK

    - Demolition and removal of roads, walks, curbs, and on-grade slabs outside buildings to be demolished: Section 31 20 00, EARTH MOVING .

    - Safety Requirements: GENERAL CONDITIONS Article, ACCIDENT PREVENTION.

    - Reserved items that are to remain the property of the Government:Section 01 00 02, GENERAL REQUIREMENTS (MINOR NCA PROJECTS).

    - Asbestos Removal: Section 02 82 11, TRADITIONAL ASBESTOS ABATEMENT.

    - Lead Paint: Section 02 83 33.13, LEAD-BASED PAINT REMOVAL AND DISPOSAL.

    - Environmental Protection: Section 01 57 19, TEMPORARY ENVIRONMENTAL CONTROLS.

    - Waste Management: Section 01 74 19, CONSTRUCTION WASTE MANAGEMENT

  - PROTECTION

    - Perform demolition in such manner as to eliminate hazards to persons and property; to minimize interference with use of adjacent areas, utilities and structures or interruption of use of such utilities; and to provide free passage to and from such adjacent areas of structures. Comply with requirements of GENERAL CONDITIONS Article, ACCIDENT PREVENTION.

    - Provide safeguards, including warning signs, barricades, temporary fences, warning lights, and other similar items that are required for protection of all personnel during demolition and removal operations. Comply with requirements of Section 01 00 02, GENERAL REQUIREMENTS (MINOR NCA PROJECTS), Article 1.10 PROTECTION OF EXISTING VEGETATION, STRUCTURES, EQUIPMENT, UTILITIES AND IMPROVEMENTS.

    - Maintain fences, barricades, lights, and other similar items around exposed excavations until such excavations have been completely filled.

    - Provide enclosed dust chutes with control gates from each floor to carry debris to truck beds and govern flow of material into truck. Provide overhead bridges of tight board or prefabricated metal

construction at dust chutes to protect persons and property from falling debris.

    - Prevent spread of flying particles and dust. Sprinkle rubbish and debris with water to keep dust to a minimum. Do not use water if it results in hazardous or objectionable condition such as, but not limited to; ice, flooding, or pollution. Vacuum and dust the work area daily.F.	In addition to previously listed fire and safety rules to be observed in performance of work, include following:

1. No wall or part of wall shall be permitted to fall outwardly from structures.

      - Wherever a cutting torch or other equipment that might cause a fire is used, provide and maintain fire extinguishers nearby ready for immediate use. Instruct all possible users in use of fire extinguishers.

      - Keep hydrants clear and accessible at all times. Prohibit debris from accumulating within a radius of 4500 mm (15 feet) of fire hydrants.

G. Before beginning any demolition work, survey the site and examine the drawings and specifications to determine the extent of the work. Take necessary precautions to avoid damages to existing items to remain in place, to be reused, or to remain the property of the Cemetery; any damaged items shall be repaired or replaced as approved by the Resident Engineer/Contracting Officer's Representative (RE/COR). Coordinate the work of this section with all other work. Construct and maintain shoring, bracing, and supports as required. Do not overload structural elements. Provide new supports and reinforcement for existing construction weakened by demolition or removal works. Repairs, reinforcement, or structural replacement must have RE/COR's approval.

H. The work shall comply with the requirements of Section 01 57 19, TEMPORARY ENVIRONMENTAL CONTROLS.

  - UTILITY SERVICES

    - Demolish and remove outside utility service lines shown to be removed.

    - Remove abandoned outside utility lines that would interfere with installation of new utility lines and new construction.

PART 2 - PRODUCTS (NOT USED) PART 3 – EXECUTION

  - SITE CLEARING

    - General: Remove trees, shrubs, grass, and other vegetation, pavements, improvements, or obstructions, as required, to permit installation of new construction. Remove all items off-site unless specifically directed otherwise. Removal includes digging out and off-site disposal of stumps and roots.

      - Cut minor roots and branches of trees indicated to remain in a clean and careful manner where such roots and branches obstruct installation of new construction.

    - Erosion Control: Provide erosion control measures to prevent erosion or displacement of soils and discharge of soil-bearing water runoff or airborne dust to adjacent properties and walkways. Install silt fence and inlet protection as shown and as per requirements of the SWPPP, prior to any soil disturbance activities. Provide temporary seeding as required by the SWPPP.

    - Maintain site controls in accordance with Storm Water Pollution Prevention Plan and repair as directed by RE/COR to sustain compliance with NPDES permit. Maintain all records as required by the SWPPP. Perform inspections as required by the SWPPP.

    - Topsoil - On-site: Topsoil is defined as friable clay loam surface soil found in a depth of not less than 150 mm (6 inches). Satisfactory topsoil is reasonably free and/or screened of subsoil, clay lumps, stones, and other objects over 25 mm (1 inch) in diameter, and without weeds, roots, and other objectionable material.

      - Strip topsoil to whatever depths encountered in a manner to prevent intermingling with underlying subsoil or other objectionable material. Remove heavy growths of grass from areas before stripping.

a. Where existing trees are indicated to remain, leave existing topsoil in place within drip lines to prevent damage to root system.

      - Stockpile topsoil in storage piles in areas indicated or directed. Construct storage piles to provide free drainage of surface water. Cover storage piles to prevent wind erosion in accordance with the

Storm Water Pollution Prevention Plan. Refer to Division 32 Section

32 90 00, “Planting" for soil amendments required prior to spreading topsoil.

a. Stockpile shall be contained with erosion and sediment controls (silt fence) and stabilized if undisturbed in accordance with the Storm Water Pollution Prevention Plan.

      - Dispose of unsuitable or excess topsoil off-site after approval of the RE/COR.

    - Clearing and Grubbing: Clear site of trees, shrubs, and other vegetation, except for those indicated to be left standing.

      - Completely remove stumps, roots, and other debris protruding through ground surface.

      - Use only hand methods for grubbing inside drip line of trees indicated to remain.

      - Fill depressions caused by clearing and grubbing operations with satisfactory soil material, unless further excavation or earthwork is indicated.

a. Place fill material in horizontal layers not exceeding 150 mm (6 inches) loose depth, and thoroughly compact each layer to a density equal to adjacent original ground.

    - Removal of Improvements: Remove existing above-grade and below-grade improvements as indicated and as necessary to facilitate new construction.

    - Continue maintenance of erosion controls in compliance with the Storm Water Pollution Prevention Plan until the work is completed and the threat of erosion is gone by either around surface stabilizer or lawn “grow-in” is at 85% complete. Temporary erosion control devices shall not be removed until the area is certified as being stabilized by the Qualified Inspector.

  - DEMOLITION

B. Debris, including brick, concrete, stone, metals and similar materials shall become property of Contractor and shall be disposed of by him daily, off the Medical Center Property to avoid accumulation at the demolition site. Materials that cannot be removed daily shall be stored in areas specified by the COR. Break up concrete slabs below grade that do not require removal from present location into pieces not exceeding

600 mm (24 inches) square to permit drainage. Contractor shall dispose debris in compliance with applicable federal, state or local permits, rules and/or regulations.

D. The removal of hazardous material shall be referred to Hazardous Materials specifications. Burning is not permitted on the property.

E. Remove existing utilities as indicated or uncovered by work and terminate in a manner conforming to the nationally recognized code covering the specific utility and approved by the RE/COR. When Utility lines are encountered that are not indicated on the drawings, the RE/COR shall be notified prior to further work in that area.

  - CLEAN-UP

    - On completion of work of this section and after removal of all debris, leave site in clean condition satisfactory to RE/COR. Clean-up shall include off the Cemetery Property disposal of all items and materials not required to remain property of the Government as well as all debris and rubbish resulting from demolition operations.

- - - E N D - - -

SECTION 02 82 13.13 GLOVEBAG ASBESTOS ABATEMENT

PART 1 - GENERAL

  - SUMMARY OF WORK

    - Contract Documents and Related Requirements: Drawings, general provisions of the contract, including general and supplementary conditions and other Division 01 specifications, shall apply to the work of this section. The contract documents show the work to be done under the contract and related requirements and conditions impacting the project. Related requirements and conditions include applicable codes and regulations, notices and permits, existing site conditions and restrictions on use of the site, requirements for partial owner occupancy during the work, coordination with other work and the phasing of the work. In the event the Asbestos Abatement Contractor discovers a conflict in the contract documents and/or requirements or codes, the conflict must be brought to the immediate attention of the Contracting Officer for resolution. Whenever there is a conflict or overlap in the requirements, the most stringent shall apply. Any actions taken by the Contractor without obtaining guidance from the Contracting Officer shall become the sole risk and responsibility of the Asbestos Abatement Contractor. All costs incurred due to such action are also the responsibility of the Asbestos Abatement Contractor.

    - Extent of Work: Below is a brief description of the estimated quantities of asbestos containing materials to be abated by the Glovebag method. These quantities are for informational purposes only and are based on the best information available at the time of the specification preparation. The Contractor shall satisfy himself as to the actual quantities to be abated. Nothing in this section may be interpreted as limiting the extent of work otherwise required by this contract and related documents.

      - Removal, clean-up and disposal of ACM piping and fittings and asbestos contaminated elements in an appropriate regulated area in the following approximate quantities:

(VA to provide acceptable linear meters) linear meters (feet) of <50 mm (<2 inches) diameter pipe insulation

(	VA to provide acceptable linear meters) linear meters (feet) of 50 - 150 mm (2 inches – 6 inches) diameter pipe insulation

(	VA to provide acceptable linear meters) linear meters (feet) of >150 mm (>6 inches) diameter pipe insulation

(	VA to provide acceptable linear meters) fittings, saddle blocks, valves, T’s, or other mechanical appurtenances 50 - 150 mm (2 inches – 6 inches) in diameter other //specify//

B. Related Work:

Section 07 84 00, FIRESTOPPING

Section 02 41 00, DEMOLITION

Division 09, FINISHES

C. TASKS:

The work tasks are summarized briefly as follows:

- Pre-abatement activities including pre-abatement meeting(s), inspection(s), notifications, permits, submittal approvals, work- site preparations, emergency procedures arrangements, and Asbestos Hazard Abatement Plans for Glovebag asbestos abatement work.

- Abatement activities including removal, clean-up and disposal of ACM waste, recordkeeping, security, monitoring, and inspections.

- Cleaning and decontamination activities including final visual inspection, air monitoring and certification of decontamination.

D. Abatement Contractor Use of Premises:

- The Contractor and Contractor's personnel shall cooperate fully with the VA Representative/consultant to facilitate efficient use of buildings and areas within buildings. The Contractor shall perform the work in accordance with the VA specifications, drawings, phasing plan and in compliance with any/all applicable Federal, State and Local regulations and requirements.

- The Contractor shall use the existing facilities in the building strictly within the limits indicated in contract documents as well as the approved VA Design and Construction Procedures. VA Design and Construction Procedures drawings of partially occupied buildings will show the limits of regulated areas; the placement of decontamination facilities; the temporary location of bagged waste ACM; the path of transport to outside the building; and the

temporary waste storage area for each building/regulated area. Any variation from the arrangements shown on drawings shall be secured in writing from the VA Representative through the pre-abatement plan of action. The following limitations of use shall apply to existing facilities shown on drawings.

  - VARIATIONS IN QUANTITY

    - The quantities and locations of ACM as indicated on the drawings and the extent of work included in this section are estimated, which are limited by the physical constraints imposed by occupancy of the buildings and accessibility to ACM. Accordingly, minor variations (+/- 10 percent) in quantities of ACM within the regulated area are considered as having no impact on contract price and time requirements of this contract. Where additional work is required beyond the above variation, the contractor shall provide unit prices for newly discovered ACM and those prices shall be used for additional work required under the contractor.

  - STOP ASBESTOS REMOVAL

    - If the Contracting Officer; their field representative; the facility Safety Officer/Manager or their designee, or the VA Professional Industrial Hygienist/Certified Industrial Hygienist (VPIH/CIH) presents a verbal Stop Asbestos Removal Order, the Contractor/Personnel shall immediately stop all asbestos removal and maintain HEPA filtered negative pressure air flow in the containment and adequately wet any exposed ACM. If a verbal Stop Asbestos Removal Order is issued, the VA shall follow-up with a written order to the Contractor as soon as it is practicable. The Contractor shall not resume any asbestos removal activity until authorized to do so in writing by the VA Contracting Officer. A stop asbestos removal order may be issued at any time the VA Contracting Officer determines abatement conditions/activities are not within VA specification, regulatory requirements or that an imminent hazard exists to human health or the environment. Work stoppage will continue until conditions have been corrected to the satisfaction of the VA. Standby time and costs for corrective actions will be borne by the Contractor, including the VPIH/CIH time. The occurrence of any of the following events shall be reported immediately by the Contractor’s competent person to the VA Contracting Office or field representative

using the most expeditious means (e.g., verbal or telephonic), followed up with written notification to the Contracting Officer as soon as practical. The Contractor shall immediately stop asbestos removal/disturbance activities and initiate fiber reduction activities if:

      - Airborne PCM analysis results equal to or greater than 0.01 f/cc above background levels inside the building but outside the regulated area;

      - breach or break in regulated area containment barrier(s);

      - less than –0.02 inch WCG pressure in the regulated area;

      - serious injury/death at the site;

      - fire/safety emergency at the site;

      - respiratory protection system failure;

      - power failure or loss or inadequate use of wetting agent; or

      - any visible emissions observed outside the regulated area; or

      - failure to follow project specification requirements.

  - DEFINITIONS

    - General: Definitions and explanations here are neither complete nor exclusive of all terms used in the contract documents, but are general for the work to the extent they are not stated more explicitly in another element of the contract documents. Drawings must be recognized as diagrammatic in nature and not completely descriptive of the requirements indicated therein.

    - Glossary:

Abatement - Procedures to control fiber release from asbestos- containing materials. Includes removal, encapsulation, enclosure, demolition, and renovation activities related to asbestos containing materials (ACM).

Aerosol - Solid or liquid particulate suspended in air.

Adequately wet - Sufficiently mixed or penetrated with liquid to prevent the release of particulates. If visible emissions are observed coming from the ACM, then that material has not been adequately wetted. Aggressive method - Removal or disturbance of building material by sanding, abrading, grinding, or other method that breaks, crumbles, or disintegrates intact ACM.

Aggressive air sampling - EPA AHERA defined clearance sampling method using air moving equipment such as fans and leaf blowers to aggressively disturb and maintain in the air residual fibers after abatement.

AHERA - Asbestos Hazard Emergency Response Act. Asbestos regulations for schools issued in 1987.

Aircell - Pipe or duct insulation made of corrugated cardboard which contains asbestos.

Air monitoring - The process of measuring the fiber content of a known volume of air collected over a specified period of time. The NIOSH 7400 Method, Issue 3, Fifth Edition is used to determine the fiber levels in air. For personal samples, area air samples and clearance air testing using Phase Contrast Microscopy (PCM) analysis, the NIOSH Method 7402 Issue 2, Fourth Edition) can be used when it is necessary to confirm fibers counted by PCM as being asbestos. The AHERA TEM analysis may be used for background, area samples and clearance samples when required by this specification, or at the discretion of the VPIH/CIH as appropriate.

Air sample filter - The filter used to collect fibers which are then counted. The filter is made of mixed cellulose ester membrane (MCE) for PCM (Phase Contrast Microscopy, 25 mm, 3-piece with 2 inches Static Extension Cowl, 0.8 micron pore size) and MCE for TEM (Transmission Electron Microscopy, 25 mm, 3-piece with 2 inches Static Extension Cowl, 0.45 micron pore size).

Amended water - Water to which a surfactant (wetting agent) has been added to increase the penetrating ability of the liquid.

Asbestos - Includes chrysotile, amosite, crocidolite, tremolite asbestos, anthophyllite asbestos, actinolite asbestos, and any of these minerals that have been chemically treated or altered. Asbestos also includes PACM, as defined below.

Asbestos Hazard Abatement Plan (AHAP) - Asbestos work procedures required to be submitted by the contractor before work begins.

Asbestos-containing material (ACM) - Any material containing more than one percent of asbestos.

Asbestos contaminated elements (ACE) - Building elements such as ceilings, walls, lights, or ductwork that are contaminated with asbestos.

Asbestos-contaminated soil (ACS) – Soil found in the work area or in adjacent areas such as crawlspaces or pipe tunnels which is contaminated with asbestos-containing material debris and cannot be easily separated from the material.

Asbestos-containing waste (ACW) material - Asbestos-containing material or asbestos contaminated objects requiring disposal.

Asbestos Project Monitor – Some States require that any person conducting asbestos abatement air sampling, clearance inspections and clearance air sampling be licensed as an asbestos project monitor.

Asbestos waste decontamination facility - A system consisting of drum/bag washing facilities and a temporary storage area for cleaned containers of asbestos waste. Used as the exit for waste and equipment leaving the regulated area. In an emergency, it may be used to evacuate personnel.

Authorized person - Any person authorized by the VA, the Contractor, or government agency and required by work duties to be present in regulated areas.

Authorized visitor - Any person approved by the VA; the contractor; or any government agency representative having jurisdiction over the regulated area (e.g., OSHA, Federal and State EPA).

Barrier - Any surface that isolates the regulated area and inhibits fiber migration from the regulated area.

Containment Barrier - An airtight barrier consisting of walls, floors, and/or ceilings of sealed plastic sheeting which surrounds and seals the outer perimeter of the regulated area.

Critical Barrier - The barrier responsible for isolating the regulated area from adjacent spaces, typically constructed of 2-layers of 6-mil independently installed plastic sheeting (Polyethylene) secured in place at openings such as doors, windows, penetrations or any other opening into the regulated area.

Primary Barrier – Plastic barriers placed over critical barriers and exposed directly to abatement work or to secondary barrier.

Secondary Barrier - Any additional plastic barriers used to isolate and provide protection from debris during abatement work.

Breathing zone - The hemisphere forward of the shoulders with a radius of about 150 - 225 mm (6 - 9 inches) from the worker's nose.

Bridging encapsulant - An encapsulant that forms a layer on the surface of the ACM.

Building/facility owner - The legal entity, including a lessee, which exercises control over management and recordkeeping functions relating to a building and/or facility in which asbestos activities take place. Bulk testing - The collection and analysis of suspect asbestos containing materials.

Certified Industrial Hygienist (CIH) - A person certified in the comprehensive practice of industrial hygiene by the American Board of Industrial Hygiene.

Class I asbestos work - Activities involving the removal of Thermal System Insulation (TSI) and surfacing ACM and Presumed Asbestos Containing Material (PACM).

Class II asbestos work - Activities involving the removal of ACM which is not thermal system insulation or surfacing material. This includes, but is not limited to, the removal of asbestos-containing wallboard, floor tile and sheeting, roofing and siding shingles, and construction mastic.

Clean room/Changing room - An uncontaminated room having facilities for the storage of employee's street clothing and uncontaminated materials and equipment.

Clearance sample - The final air sample taken after all asbestos work has been done and visually inspected. Performed by the VA's Professional Industrial Hygiene Consultant/Certified Industrial Hygienist (VPIH/CIH).

Closely resemble - The major workplace conditions which have contributed to the levels of historic asbestos exposure, are no more protective than conditions of the current workplace.

Competent person - In addition to the definition in 29 CFR 1926.32(f), one who is capable of identifying existing asbestos hazards in the workplace and selecting the appropriate control strategy for asbestos exposure, who has the authority to take prompt corrective measures to

eliminate them, as specified in 29 CFR 1926.32(f); in addition, for Class I and II work who is specially trained in a training course which meets the criteria of EPA's Model Accreditation Plan (40 CFR 763) for supervisor.

Contractor's Professional Industrial Hygienist (CPIH/CIH) - The asbestos abatement contractor's industrial hygienist. The industrial hygienist must meet the qualification requirements of a PIH and may report to a certified industrial hygienist (CIH).

Count - Refers to the fiber count or the average number of fibers greater than five microns in length with a length-to-width (aspect) ratio of at least 3 to 1, per cubic centimeter of air.

Crawlspace – An area which can be found either in or adjacent to the work area. This area has limited access and egress and may contain asbestos materials and/or asbestos contaminated soil.

Decontamination area/unit - An enclosed area adjacent to and connected to the regulated area and consisting of an equipment room, shower room, and clean room, which is used for the decontamination of workers, materials, and equipment that are contaminated with asbestos.

Demolition - The wrecking or taking out of any load-supporting structural member and any related razing, removing, or stripping of asbestos products.

Disposal bag - Typically 6-mil thick sift-proof, dustproof, leak-tight container used to package and transport asbestos waste from regulated areas to the approved landfill. Each bag/container must be labeled/marked in accordance with EPA, OSHA and DOT requirements.

Disturbance - Asbestos Operations and Maintenance Activities (OSHA Class III) that disrupt the matrix of ACM or PACM, crumble or pulverize ACM or PACM, or generate visible debris from ACM or PACM. Disturbance includes cutting away small amounts of ACM or PACM, no greater than the amount that can be contained in one standard sized glove bag or waste bag, in order to access a building component. In no event shall the amount of ACM or PACM so disturbed exceed that which can be contained in one glove bag or disposal bag, which shall not exceed 60 inches in length or width.

Drum - A rigid, impermeable container made of cardboard fiber, plastic, or metal which can be sealed in order to be sift-proof, dustproof, and leak-tight.

Employee exposure - The exposure to airborne asbestos that would occur if the employee were not wearing respiratory protection equipment.

Encapsulant - A material that surrounds or embeds asbestos fibers in an adhesive matrix and prevents the release of fibers.

Encapsulation - Treating ACM with an encapsulant.

Enclosure - The construction of an air tight, impermeable, permanent barrier around ACM to control the release of asbestos fibers from the material and also eliminate access to the material.

Equipment room - A contaminated room located within the decontamination area that is supplied with impermeable bags or containers for the disposal of contaminated protective clothing and equipment.

Fiber - A particulate form of asbestos, 5 microns or longer, with a length to width (aspect) ratio of at least 3 to 1.

Fibers per cubic centimeter (f/cc) - Abbreviation for fibers per cubic centimeter, used to describe the level of asbestos fibers in air.

Filter - Media used in respirators, vacuums, or other machines to remove particulate from air.

Firestopping - Material used to close the open parts of a structure in order to prevent a fire from spreading.

Friable asbestos containing material - Any material containing more than one (1) percent asbestos as determined using the method specified

40 CFR 763, Polarized Light Microscopy, that, when dry, can be crumbled, pulverized, or reduced to powder by hand pressure.

Glovebag - Not more than a 60 x 60 inch impervious plastic bag-like enclosure affixed around an asbestos-containing material, with glove- like appendages through which materials and tools may be handled.

High efficiency particulate air (HEPA) filter – An ASHRAE MERV 17 filter capable of trapping and retaining at least 99.97 percent of all mono-dispersed particles of 0.3 micrometers in diameter.

HEPA vacuum - Vacuum collection equipment equipped with a HEPA filter system capable of collecting and retaining asbestos fibers.

Homogeneous area - An area of surfacing, thermal system insulation or miscellaneous ACM that is uniform in color, texture and date of application.

HVAC - Heating, Ventilation and Air Conditioning

Industrial hygienist (IH) - A professional qualified by education, training, and experience to anticipate, recognize, evaluate and develop controls for occupational health hazards. Meets definition requirements of the American Industrial Hygiene Association (AIHA).

Industrial hygienist technician (IH Technician) - A person working under the direction of an IH or CIH who has special training, experience, certifications and licenses required for the industrial hygiene work assigned. Some States require that an industrial hygienist technician conducting asbestos abatement air sampling, clearance inspection and clearance air sampling be licensed as an asbestos project monitor.

Intact - The ACM has not crumbled, been pulverized, or otherwise deteriorated so that the asbestos is no longer likely to be bound with its matrix.

Lockdown - Applying encapsulant, after a final visual inspection, on all abated surfaces at the conclusion of ACM removal prior to removal of critical barriers.

National Emission Standards for Hazardous Air Pollutants (NESHAP) - EPA's rule to control emissions of asbestos to the environment (40 CFR Part 61, Subpart M).

Negative initial exposure assessment - A demonstration by the employer which complies with the criteria in 29 CFR 1926.1101 (f)(2)(iii), that employee exposure during an operation is expected to be consistently below the PEL or Excursion Limit (EL).

Negative pressure - Air pressure which is lower than the surrounding area, created by exhausting air from a sealed regulated area through HEPA equipped filtration units. OSHA requires maintaining -0.02 inch water column gauge inside the negative pressure enclosure.

Negative pressure respirator - A respirator in which the air pressure inside the facepiece is negative during inhalation relative to the air pressure outside the respirator facepiece.

Non-friable ACM - Material that contains more than 1 percent asbestos but cannot be crumbled, pulverized, or reduced to powder by hand pressure.

Organic vapor cartridge - The type of cartridge used on air purifying respirators to remove organic vapor hazardous air contaminants.

Outside air - The air outside buildings and structures, including, but not limited to, the air under a bridge or in an open ferry dock.

Owner/operator - Any person who owns, leases, operates, controls, or supervises the facility being demolished or renovated or any person who owns, leases, operates, controls, or supervises the demolition or renovation operation, or both.

Penetrating encapsulant - Encapsulant that is absorbed into the ACM matrix without leaving a surface layer.

Permissible exposure limit (PEL) - The level of exposure OSHA allows for an 8-hour time weighted average. For asbestos fibers, the eight (8) hour time-weighted average PEL is 0.1 fibers per cubic centimeter (0.1 f/cc) of air and the 30-minute Excursion Limit (EL) is 1.0 fibers per cubic centimeter (1 f/cc).

Personal protective equipment (PPE) – equipment designed to protect user from injury and/or specific job hazard. Such equipment may include protective clothing, hard hats, safety glasses, fall protection, and respirators.

Personal sampling/monitoring - Representative air samples obtained in the breathing zone for one or more workers within the regulated area using a filter cassette and a calibrated air sampling pump to determine asbestos exposure.

Pipe tunnel – An area, typically located adjacent to mechanical spaces or boiler rooms in which the pipes servicing the heating system in the building are routed to allow the pipes to access heating elements.

These areas may contain asbestos pipe insulation, asbestos fittings, debris or asbestos-contaminated soil.

Polarized light microscopy (PLM) - Light microscopy using dispersion staining techniques and refractive indices to identify and quantify the type of asbestos present in a bulk sample.

Polyethylene sheeting - Strong plastic barrier material 4 to 6-mils thick, semi-transparent, flame retardant per NFPA 241.

Positive/negative fit check - A method of verifying the seal of a facepiece respirator by temporarily occluding the filters and breathing in (inhaling) and then temporarily occluding the exhalation valve and breathing out (exhaling) while checking for inward or outward leakage of the respirator respectively.

Presumed ACM (PACM) - Thermal system insulation, surfacing, and flooring material installed in buildings prior to 1981. If the building owner has actual knowledge, or should have known through the exercise of due diligence that other materials are ACM, they too must be treated as PACM. The designation of PACM may be rebutted pursuant to 29 CFR 1926.1101 (k)(5).

Professional IH - An IH who meets the definition requirements of AIHA; meets the definition requirements of OSHA as a "Competent Person" at 29 CFR 1926.1101 (b); has completed two specialized EPA approved courses on management and supervision of asbestos abatement projects; has formal training in respiratory protection and waste disposal; and has a minimum of four projects of similar complexity with this project of which at least three projects serving as the supervisory IH. The PIH may be either the VA’s PIH (VPIH/CIH) or Contractor’s PIH (CPIH/CIH).

Project designer - A person who has successfully completed the training requirements for an asbestos abatement project designer as required by

40 CFR 763 Subpart E, Appendix C, Part I; (B)(5).

Assigned Protection factor - A value assigned by OSHA/NIOSH to indicate the expected protection provided by each respirator class, when the respirator is properly selected and worn correctly. The number indicates the reduction of exposure level from outside to inside the respirator facepiece.

Qualitative fit test (QLFT) - A fit test using a challenge material that can be sensed by the wearer if leakage in the respirator occurs. Quantitative fit test (QNFT) - A fit test using a challenge material which is quantified outside and inside the respirator thus allowing the determination of the actual fit factor.

Regulated area - An area established by the employer to demarcate where Class I, II, III asbestos work is conducted, and any adjoining area where debris and waste from such asbestos work may accumulate; and a

work area within which airborne concentrations of asbestos exceed, or there is a reasonable possibility they may exceed the PEL.

Regulated ACM (RACM) - Friable ACM; Category I non-friable ACM that has become friable; Category I non-friable ACM that will be or has been subjected to sanding, grinding, cutting, or abrading or; Category II non-friable ACM that has a high probability of becoming or has become crumbled, pulverized, or reduced to powder by the forces expected to act on the material in the course of the demolition or renovation operation.

Removal - All operations where ACM, PACM and/or RACM is taken out or stripped from structures or substrates, including demolition operations.

Renovation - Altering a facility or one or more facility components in any way, including the stripping or removal of asbestos from a facility component which does not involve demolition activity.

Repair - Overhauling, rebuilding, reconstructing, or reconditioning of structures or substrates, including encapsulation or other repair of ACM or PACM attached to structures or substrates.

Shower room - The portion of the PDF where personnel shower before leaving the regulated area.

Supplied air respirator (SAR) - A respiratory protection system that supplies minimum Grade D respirable air per ANSI/Compressed Gas Association Commodity Specification for Air, G-7.1-2018.

Surfacing ACM - A material containing more than 1 percent asbestos that is sprayed, troweled on or otherwise applied to surfaces for acoustical, decorative, fireproofing and other purposes.

Surfactant - A chemical added to water to decrease water's surface tension thus making it more penetrating into ACM.

Thermal system ACM - A material containing more than 1 percent asbestos applied to pipes, fittings, boilers, breeching, tanks, ducts, or other structural components to prevent heat loss or gain.

Transmission electron microscopy (TEM) - A microscopy method that can identify and count asbestos fibers.

VA Professional Industrial Hygienist (VPIH/CIH) – The Department of Veterans Affairs Professional Industrial Hygienist must meet the

qualifications of a PIH, and may report to a Certified Industrial Hygienist (CIH).

VA Representative - The VA official responsible for on-going project work.

VA Total – means a building or substantial part of the building is completely removed, torn or knocked down, bulldozed, flattened, or razed, including removal of building debris.

Visible emissions - Any emissions, which are visually detectable without the aid of instruments, coming from ACM/PACM/RACM/ACS or ACM waste material.

Waste/Equipment decontamination facility (W/EDF) – The area in which equipment is decontaminated before removal from the regulated area. Waste generator - Any owner or operator whose act or process produces asbestos-containing waste material.

Waste shipment record - The shipping document, required to be originated and signed by the waste generator, used to track and substantiate the disposition of asbestos-containing waste material. Wet cleaning - The process of thoroughly eliminating, by wet methods, any asbestos contamination from surfaces or objects.

    - Referenced Standards Organizations: See Section 01 42 19 REFERENCED STANDARDS.

  - APPLICABLE CODES AND REGULATIONS

    - General Applicability of Codes, Regulations, and Standards:

      - All work under this contract shall be done in strict accordance with all applicable Federal, State, and Local regulations, standards and codes governing asbestos abatement, and any other trade work done in conjunction with the abatement. All applicable codes, regulations and standards are adopted into this specification and will have the same force and effect as this specification.

      - The most recent edition of any relevant regulation, standard, document or code shall be in effect. Where conflict among the requirements or with these specification, exists, the most stringent requirement(s) shall be utilized.

      - Copies of all standards, regulations, codes and other applicable documents, including this specification and those listed in Section

1.5 shall be available at the worksite in the clean change area of

the worker decontamination system and/or the Contractor’s on-site Field Office. These standards, regulations, codes and other applicable documents, including this specification and those listed in Section 1.5 may be made available electronically.

    - Asbestos Abatement Contractor Responsibility: The Asbestos Abatement Contractor (Contractor) shall assume full responsibility and liability for compliance with all applicable Federal, State and Local regulations related to any and all aspects of the asbestos abatement project. The Contractor is responsible for providing and maintaining training, accreditations, medical exams, medical records, personal protective equipment (PPE), respiratory protection, and respirator fit testing, as required by applicable Federal, State and Local regulations. The Contractor shall hold the VA and VPIH/CIH consultants harmless for any Contractor’s failure to comply with any applicable work, packaging, transporting, disposal, safety, health, or environmental requirement on the part of himself, his employees, or his subcontractors. The Contractor will incur all costs of the CPIH/CIH, including all sampling/analytical costs to assure compliance with OSHA/EPA/State/Local requirements related to failure to comply with the regulations applicable to the work.

    - Federal Requirements: Federal requirements which govern some aspect of asbestos abatement include, but are not limited to, the following regulations.

Occupational Safety and Health Administration (OSHA)

Title 29 CFR 1926.1101 - Construction Standard for Asbestos

- Title 29 CFR 1926 Subpart E - Personal Protective Equipment and Life Saving Equipment

- Title 29 CFR 1910.134 - Respiratory Protection

- Title 29 CFR 1926 - Construction Industry Standards

- Title 29 CFR 1926.33 - Access to Employee Exposure and Medical Records

- Title 29 CFR 1926.59 same as 1910.1200 - Hazard Communication

- Title 29 CFR 1926 Subpart C – General Safety and Health Provisions and Subpart D – Occupational Health and Environmental Controls

- Environmental Protection Agency (EPA)

1.40 CFR 61 Subpart M - National Emission Standard for Hazardous Air Pollutants - Asbestos

  - 2.40 CFR 763.80 - Asbestos Hazard Emergency Response Act (AHERA) and Asbestos Hazard Abatement Reauthorization Act (ASHARA)

- Department of Transportation (DOT)

  - Title 49 CFR 171 - 180 – Transportation

    - State Requirements:

State requirements that apply to the asbestos abatement work, disposal, clearance, etc., include, but are not limited to, the following:

    - Local Requirements:

      - If Local requirements are more stringent than Federal or State standards, the local standards are to be followed.

    - Standards:

      - Standards which govern asbestos abatement activities include, but are not limited to, the following:

        - American National Standards Institute (ANSI/ASSP) Z9.2-2018 - Fundamentals Governing the Design and Operation of Local Exhaust Systems and ANSI/ASSE Z88.2-2015 - Practices for Respiratory Protection.

        - Underwriters Laboratories (UL) 586-2009 - UL Standard for Safety of HEPA filter Units, 9th Edition; ANSI Approval 2017-12-19.

      - Standards which govern encapsulation work include, but are not limited to, the following:

        - American Society for Testing and Materials International (ASTM).

      - Standards which govern the fire and safety concerns in abatement work include, but are not limited to, the following:

        - National Fire Protection Association (NFPA) 241 - Standard for Safeguarding Construction, Alteration, and Demolition Operations.

        - NFPA 701 - Standard Methods for Fire Tests for Flame Resistant Textiles and Film.

        - NFPA 101 - Life Safety Code.

    - EPA Guidance Documents:

      - EPA guidance documents which discuss asbestos abatement work activities are listed below. These documents are made part of this section by reference. Guidance for Controlling ACM in Buildings (Purple Book) EPA 560/5-85-024.

      - Asbestos Waste Management Guidance EPA 530-SW-85-007.

      - A Guide to Respiratory Protection for the Asbestos Abatement Industry EPA-560-OPTS-86-001.

      - Guide to Managing Asbestos in Place (Green Book) TS 799 20T July 1990.

    - Notices:

      - State and Local agencies: Send written notification as required by state and local regulations including the local fire department prior to beginning any work on ACM as follows:

      - Copies of notifications shall be submitted to the VA for the facility's records in the same time frame notification are given to EPA, State, and Local authorities.

    - Permits/Licenses: The contractor shall apply for and have all required permits and licenses to perform asbestos abatement work as required by Federal, State, and Local regulations prior to beginning any work on ACM as follows.

    - Posting and Filing of Regulations: Maintain two (2) copies of applicable Federal, State, and Local regulations. Post one copy of each at the regulated area where workers will have daily access to the regulations and keep another copy in the Contractor's office.

    - VA Responsibilities Prior to Commencement of Work:

      - Notify occupants adjacent to regulated areas of project dates and requirements for relocation, if needed. Arrangements must be made prior to starting work for relocation of desks, files, equipment, and personal possessions to avoid unauthorized access into the regulated area. Note: Notification of adjacent personnel is required by OSHA in 29 CFR 1926.1101 (k) to prevent unnecessary or unauthorized access to the regulated area.

      - Submit to the Contractor results of background air sampling; including location of samples, person who collected the samples, equipment utilized, calibration data and method of analysis. During abatement, submit to the Contractor, results of bulk material analysis and air sampling data collected during the course of the abatement. This information shall not release the Contractor from any responsibility for OSHA compliance.

    - Emergency Action Plan and Arrangements:

      - An Emergency Action Plan shall be developed by prior to commencing abatement activities and shall be agreed to by the Contractor and the VA. The Plan shall meet the requirements of 29 CFR 1926, Subpart C, Standard 1926.35 Employee Emergency Action Plans.

      - Emergency procedures shall be in written form and prominently posted in the clean room and equipment room of the decontamination unit. Everyone, prior to entering the regulated area, must read and sign these procedures to acknowledge understanding of the regulated area layout, location of emergency exits and emergency procedures.

      - Emergency planning shall include written notification of police, fire, and emergency medical personnel of planned abatement activities; work schedule; layout of regulated area; and access to the regulated area, particularly barriers that may affect response capabilities.

      - Emergency planning shall include consideration of fire, explosion, hazardous atmospheres, electrical hazards, slips/trips and falls, confined spaces, and heat stress illness. Written procedures for response to emergency situations shall be developed and employee training in procedures shall be provided.

      - Employees shall be trained in regulated area/site evacuation procedures in the event of workplace emergencies.

        - For non-life-threatening situations - employees injured or otherwise incapacitated shall be decontaminated following normal procedures with assistance from fellow workers, if necessary, before exiting the regulated area to obtain proper medical treatment.

        - For life-threatening injury or illness, worker decontamination shall take least priority after measures to stabilize the injured worker, medical personnel shall remove them from the regulated area if back or neck injury is present, and secure proper medical treatment.

      - Telephone numbers of any/all emergency response personnel shall be prominently posted in the clean room, along with the location of the nearest telephone.

      - The Contractor shall provide verification of first aid/CPR training for personnel responsible for providing first aid/CPR. OSHA requires

medical assistance within 3-4 minutes of a life-threatening injury/illness. Bloodborne Pathogen training shall also be verified for those personnel required to provide first aid/CPR.

      - The Emergency Action Plan shall provide for a Contingency Plan in the event that an incident occurs that may require the modification of the Asbestos Hazard Abatement Plans during abatement. Such incidents include, but are not limited to, fire; accident; power failure; negative pressure failure; and supplied air system failure. The Contractor shall detail procedures to be followed in the event of an incident assuring that asbestos abatement work is stopped and wetting is continued until correction of the problem.

    - Pre-Construction Meeting:

      - Prior to commencing the work, the Contractor shall meet with the VPIH/CIH to present and review, as appropriate, the items following this paragraph. The Contractor's Competent Person(s) who will be on- site shall participate in the pre-start meeting. The pre-start meeting is to discuss and determine procedures to be used during the project. At this meeting, the Contractor shall provide:

        - Plan for testing and inspecting areas of work with correct individuals within the VA and the team.

        - Proof of Contractor licensing.

        - Proof the Competent Person is trained and accredited and approved for working in this State. Verification of the experience of the Competent Person shall also be presented.

        - A list of all workers who will participate in the project, including experience and verification of training and accreditation.

        - A list of and verification of training for all personnel who have current first-aid/CPR training. A minimum of one person per shift must have adequate training.

        - Current medical written opinions for all personnel working on- site meeting the requirements of 29 CFR 1926.1101 (m).

        - Current fit-tests for all personnel wearing respirators on-site meeting the requirements of 29 CFR 1926.1101 (h) and Appendix C.

        - A copy of the Contractor's Asbestos Hazard Abatement Plan. In these procedures, the following information must be detailed,

specific for this project. A copy of the Contractor's Asbestos Hazard Abatement Plan (AHAP) for Class I Glovebag Asbestos Abatement. In these procedures, the following information must be detailed, specific for this project.

          - Regulated area preparation procedures;

          - Notification requirements procedure of Contractor as required in 29 CFR 1926.1101 (d) Multi-Employer Worksites;

          - If required, decontamination area set-up/layout and decontamination procedures for employees;

          - Glovebag abatement methods/procedures and equipment to be used; and

          - Personal protective equipment to be used

      - At this meeting the Contractor shall provide all submittals as required.

      - Procedures for handling, packaging and disposal of asbestos waste.

      - Emergency Action Plan and Contingency Plan Procedures.

  - PROJECT COORDINATION

    - The following are the minimum administrative and supervisory personnel necessary for coordination of the work.

      - Personnel

        - Administrative and supervisory personnel shall consist of a qualified Competent Person(s) as defined by OSHA in the Construction Standards and the Asbestos Construction Standard; Contractor Professional Industrial Hygienist and Industrial Hygiene Technicians. These employees are the Contractor's representatives responsible for compliance with these specifications and all other applicable requirements.

        - Non-supervisory personnel shall consist of an adequate number of qualified personnel to meet the schedule requirements of the project. Personnel shall meet required qualifications. Personnel utilized on-site shall be pre-approved by the VA Representative. A request for approval shall be submitted for any person to be employed during the project giving the person's name; last four digits of social security number; qualifications; accreditation card with color picture if required by State; Certificate of

Worker's Acknowledgment; and Affidavit of Medical Surveillance and Respiratory Protection and current Respirator Fit Test.

        - Minimum qualifications for Contractor and assigned personnel are:

          - The Contractor has conducted within the last three (3) years, three (3) projects of similar complexity and dollar value as this project; has not been cited and penalized for serious violations of Federal (and State or Local as applicable) EPA and OSHA asbestos regulations in the past three (3) years; has adequate liability/occurrence insurance for asbestos work as required by the State; is licensed in applicable State; has adequate and qualified personnel available to complete the work; has comprehensive Asbestos Hazard Abatement Plans (AHAPs) for asbestos work; and has adequate materials, equipment and supplies to perform the work.

          - The Competent Person has four (4) years of abatement experience of which two (2) years were as the Competent Person on the project; meets the OSHA definition of a Competent Person; has been the Competent Person on two (2) projects of similar size and complexity as this project within the past three (3) years; has completed EPA AHERA/OSHA/State/Local training requirements/accreditation(s) and refreshers; and has all required OSHA documentation related to medical and respiratory protection.

          - The Contractor Professional Industrial Hygienist/CIH (CPIH/CIH) shall have five (5) years of monitoring experience and supervision of asbestos abatement projects; has participated as senior IH on five (5) abatement projects, three (3) of which are similar in size and complexity as this project; has specialized EPA AHERA/OSHA training in asbestos abatement management, respiratory protection, waste disposal and asbestos inspection; has completed the NIOSH 582 Course or equivalent, Contractor/Supervisor course; and has appropriate medical/respiratory protection records/documentation.

          - The Abatement Personnel shall have completed the EPA AHERA/OSHA abatement worker course; have training on the Asbestos Hazard Abatement Plans of the Contractor; has one

year of asbestos abatement experience within the past three

(3) years of similar size and complexity; has applicable medical and respiratory protection documentation; has certificate of training/current refresher and State accreditation/license.

      - All personnel shall be in compliance with OSHA construction safety training as applicable and submit certification.

  - RESPIRATORY PROTECTION

    - General - Respiratory Protection Program: The Contractor shall develop and implement a written Respiratory Protection Program (RPP) which is in compliance with OSHA requirements found at 29 CFR 1926.1101 and 29 CFR 1910.134. ANSI Standard Z88.2-2015 provides excellent guidance for developing a respiratory protection program. All respirators used must be NIOSH approved for asbestos abatement activities. The written RPP shall, at a minimum, contain the basic requirements found at 29 CFR 1910.134 (c) - Respiratory Protection Program.Respiratory Protection Program Coordinator: The Respiratory Protection Program Coordinator (RPPC) must be identified and shall have two (2) years of experience coordinating RPP of similar size and complexity. The RPPC must submit a signed statement attesting to the fact that the program meets the above requirements.

    - Selection and Use of Respirators: The procedure for the selection and use of respirators must be submitted to the VA as part of the Contractor's qualifications. The procedure must be written clearly enough for workers to understand. A copy of the Respiratory Protection Program must be available in the clean room of the decontamination unit or in the onsite Contractor’s office, for reference by employees or authorized visitors.

    - Minimum Respiratory Protection: Minimum respiratory protection shall be a ½-mask negative pressure air purifying respirator equipped with P100 filters, provided personal air samples in the workplace remain at or below 0.1 f/cc, determined as an 8-hour TWA. Full face powered air purifying respirator equipped with P100 filters shall be required until Contractor demonstrates that personal air samples are at or below 0.1 f/cc, determined as an 8-hour TWA. A higher level of respiratory protection shall be required, if fiber levels exceed 1 f/cc as an 8-

hour TWA, inside the regulated work area. Respirator selection shall meet the requirements of 29 CFR 1926.1101 (h) and 29 CFR 1910.134 (d)(3)(i)(A) Table 1, except as indicated in this paragraph. Abatement personnel must have a respirator for their exclusive use.

    - Medical Written Opinion: No employee shall be allowed to wear a respirator unless a physician or other licensed health care professional has provided a written determination they are medically qualified to wear the class of respirator to be used on the project while wearing whole body impermeable garments and subjected to heat or cold stress.

    - Respirator Fit Test: All personnel wearing respirators shall have a current quantitative fit test which was conducted in accordance with 29 CFR 1910.134 (f) and Appendix A. Fit tests shall be done for PAPR's which have been put into a failure mode.

    - Respirator Fit Check: The Competent Person shall assure that the positive/negative pressure user seal check is done each time the respirator is donned by an employee. Head coverings must cover respirator head straps. Any situation that prevents an effective facepiece to face seal as evidenced by failure of a user seal check shall preclude that person from entering the regulated area until resolution of the problem.

    - Maintenance and Care of Respirators: The Respiratory Protection Program Coordinator shall submit evidence and documentation showing compliance with 29 CFR 1910.134 (h) maintenance and care of respirators.

  - WORKER PROTECTION

    - Training of Abatement Personnel: Prior to beginning any abatement activity, all personnel shall be trained in accordance with OSHA 29 CFR 1926.1101 (k)(9) and any additional State/Local requirements. Training must include, at a minimum, the elements listed at 29 CFR 1926.1101 (k)(9)(viii). Training shall have been conducted by a third party, EPA/State approved trainer meeting the requirements of EPA 40 CFR 763 Appendix C (AHERA MAP). Initial training certificates and current refresher and accreditation proof must be submitted for each person working at the site.

    - Medical Examinations: Medical examinations meeting the requirements of

29 CFR 1926.1101 (m) shall be provided for all personnel working in the

regulated area, regardless of exposure levels. A current physician's written opinion as required by 29 CFR 1926.1101 (m)(4) shall be provided for each person and shall include in the medical opinion that the person has been evaluated for working in a heat and cold stress environment while wearing personal protective equipment (PPE) and is able to perform the work without risk of material health impairment.

    - Personal Protective Equipment: Provide whole body clothing, head coverings, foot coverings and any other personal protective equipment as determined by conducting the hazard assessment required by OSHA at

29 CFR 1910.132 (d). The Competent Person shall ensure the integrity of personal protective equipment worn for the duration of the project. Duct tape shall be used to secure all suit sleeves to wrists and to secure foot coverings at the ankle.

    - Regulated Area Entry Procedure: The Competent Person shall ensure that each time workers enter the regulated area; they remove ALL street clothes in the clean room of the decontamination unit and put on new disposable coveralls, head coverings, a clean respirator, and then proceed through the shower room to the equipment room where they put on non-disposable required personal protective equipment

    - Decontamination Procedure: The Competent Person shall require all personnel to adhere to following decontamination procedures whenever they leave the regulated area.

      - When exiting the regulated area, remove disposable coveralls, and ALL other clothes, disposable head coverings, and foot coverings or boots in the equipment room.

      - Still wearing the respirator and completely naked, proceed to the shower. Showering is MANDATORY. Care must be taken to follow reasonable procedures in removing the respirator to avoid inhaling asbestos fibers while showering. The following procedure is required as a minimum:

        - Thoroughly wet body including hair and face. If using a PAPR hold blower above head to keep filters dry.

        - With respirator still in place, thoroughly decontaminate body, hair, respirator face piece, and all other parts of the respirator except the blower and battery pack on a PAPR. Pay

particular attention to cleaning the seal between the face and respirator facepiece and under the respirator straps.

        - Take a deep breath, hold it and/or exhale slowly, completely wetting hair, face, and respirator. While still holding breath, remove the respirator and hold it away from the face before starting to breathe.

      - Carefully decontaminate the facepiece of the respirator inside and out. If using a PAPR, shut down using the following sequence: a) first cap inlets to filters; b) turn blower off to keep debris collected on the inlet side of the filter from dislodging and contaminating the outside of the unit; c) thoroughly decontaminate blower and hoses; d) carefully decontaminate battery pack with a wet rag being cautious of getting water in the battery pack thus preventing destruction. (THIS PROCEDURE IS NOT A SUBSTITUTE FOR RESPIRATOR CLEANING!)

      - Shower and wash body completely with soap and water. Rinse thoroughly.

      - Rinse shower room walls and floor to drain prior to exiting.

      - Proceed from shower to clean room; dry off and change into street clothes or into new disposable work clothing.

    - Regulated Area Requirements: The Competent Person shall meet all requirements of 29 CFR 1926.1101 (o) and assure that all requirements for Class I Glovebag regulated areas at 29 CFR 1926.1101 (e), 29 CFR 1926.1101 (g)(1)(i)(ii)(iii), 29 CFR 1926.1101 (g)(5)(ii)(iii)(iv) are

met. All personnel in the regulated area shall not be allowed to eat, drink, smoke, chew tobacco or gum, apply cosmetics, or in any way interfere with the fit of their respirator.

  - DECONTAMINATION FACILITIES

    - Description: Provide each regulated area with separate personnel decontamination facilities (PDF) and waste/equipment decontamination facilities (W/EDF). Ensure that the PDF are the only means of ingress and egress to the regulated area and that all equipment, bagged waste, and other material exit the regulated area only through the W/EDF.

    - General Requirements: All personnel entering or exiting a regulated area must go through the PDF and shall follow the requirements at 29 CFR 1926.1101 (j)(1) and these specifications. All waste, equipment and

contaminated materials must exit the regulated area through the W/EDF and be decontaminated in accordance with these specifications. Walls and ceilings of the PDF and W/EDF must be constructed of a minimum of 3-layers of 6-mil opaque fire retardant polyethylene sheeting and be securely attached to existing building components and/or an adequate temporary framework. A minimum of 3-layers of 6-mil poly shall also be used to cover the floor under the PDF and W/EDF units. Construct doors so that they overlap and secure to adjacent surfaces. Weight inner doorway sheets with layers of duct tape so that they close quickly after release. Put arrows on sheets so they show direction of travel and overlap. If the building adjacent area is occupied, construct a solid barrier on the occupied side(s) to protect the sheeting and reduce potential for non-authorized personnel entering the regulated area.

    - Temporary Facilities to the PDF and W/EDF: The Competent Person shall provide temporary water service connections to the PDF and W/EDF. Backflow prevention must be provided at the point of connection to the VA system. Water supply must be of adequate pressure and meet requirements of 29 CFR 1910.141(d)(3). Provide adequate temporary overhead electric power with ground fault circuit interruption (GFCI) protection. Provide a sub-panel equipped with GFCI protection for all temporary power in the clean room. Provide adequate lighting to provide a minimum of 50 foot candles in the PDF and W/EDF. Provide temporary heat, if needed, to maintain 70˚F throughout the PDF and W/EDF.

    - Personnel Decontamination Facility (PDF): The Competent Person shall provide a PDF consisting of shower room which is contiguous to a clean room and equipment room. The PDF must be sized to accommodate the number of personnel scheduled for the project. The shower room, located in the center of the PDF, shall be fitted with as many portable showers as necessary to insure all employees can complete the entire decontamination procedure within 15 minutes. The PDF shall be constructed of opaque poly for privacy. The PDF shall be constructed to eliminate any parallel routes of egress without showering.

      - Clean Room: The clean room must be physically and visually separated from the rest of the building to protect the privacy of personnel changing clothes. The clean room shall be constructed of at least

3─layers of 6-mil opaque fire retardant poly to provide an air tight room. Provide a minimum of 2 - 900 mm (3 foot) wide 6-mil poly opaque fire retardant doorways. One doorway shall be the entry from outside the PDF and the second doorway shall be to the shower room of the PDF. The floor of the clean room shall be maintained in a clean, dry and sanitary condition. Shower overflow shall not be allowed into the clean room. Provide 1 storage locker per person. A portable fire extinguisher, minimum 10 pounds capacity, Type ABC, shall be provided in accordance with OSHA and NFPA Standard 10. All persons entering the regulated area shall remove all street clothing in the clean room and dress in disposable protective clothing and respiratory protection. Any person entering the clean room does so either from the outside with street clothing on or is coming from the shower room completely naked and thoroughly washed. //Any person entering the regulated area to perform Glovebag removal work, in which a negative exposure assessment has been performed, shall don a double outer protective suit and respirator//. Male/Females required to enter the regulated area shall be ensured of their privacy throughout the entry/exit process by posting guards at both entry points to the PDF so no male/female can enter or exit the PDF during his/her stay in the PDF.

      - Shower Room: The Competent Person shall assure that the shower room is a completely water tight compartment to be used for the movement of all personnel from the clean room to the equipment room and for the showering of all personnel going from the equipment room to the clean room. Each shower shall be constructed so water runs down the walls of the shower and into a drip pan. Install a freely draining smooth floor on top of the shower pan. The shower room shall be separated from the rest of the building and from the clean room and equipment room using air tight walls made from at least 3-layers of 6-mil opaque fire retardant poly. The shower shall be equipped with a shower head and controls, hot and cold water, drainage, soap dish and continuous supply of soap, and shall be maintained in a sanitary condition throughout its use. The controls shall be arranged so an individual can shower without assistance. Provide a flexible hose shower head, hose bibs and all other items shown on Shower

Schematic. Waste water will be pumped to a drain after being filtered through a minimum of a 100 micron sock in the shower drain; a 20 micron filter; and a final 5 micron filter. Filters will be changed a minimum of once per day or more often as needed. Filter changes must be done in the shower to prevent loss of contaminated water. Hose down all shower surfaces after each shift and clean any debris from the shower pan. Residue is to be disposed of as asbestos waste. //The Competent Person shall provide a decontamination area at the outer perimeter of the regulated work area where the employees will decontaminate the outer protective suit and respirator by wet wiping and HEPA vacuuming//.

      - Equipment Room: The Competent Person shall provide an equipment room which shall be an air tight compartment for the storage of work equipment/tools, reusable personal protective equipment, except for a respirator and for use as a gross decontamination area for personnel exiting the regulated area. The equipment room shall be separated from the regulated area by a minimum 3 foot wide door made with 2-layers of 6-mil opaque fire retardant poly. The equipment room shall be separated from the regulated area, the shower room and the rest of the building by air tight walls and ceiling constructed of a minimum of 3-layers of 6-mil opaque fire retardant poly. Damp wipe all surfaces of the equipment room after each shift change. Provide an additional loose layer of 6-mil fire retardant poly per shift change and remove this layer after each shift. If needed, provide a temporary electrical sub-panel equipped with GFCI in the equipment room to accommodate any equipment required in the regulated area. The Competent Person shall provide a decontamination area at the outer perimeter of the regulated work area where the employees will decontaminate the outer protective suit and respirator by wet wiping and HEPA vacuuming.

      - The PDF shall be as follows: Clean room at the entrance followed by a shower room followed by an equipment room leading to the regulated area. Each doorway in the PDF shall be a minimum of 2-layers of 6- mil opaque fire retardant poly.

    - . Waste/Equipment Decontamination Facility (W/EDF)

      - The Competent Person shall provide a W/EDF consisting of a wash room, holding room, and clean room for removal of waste, equipment and contaminated material from the regulated area. Personnel shall not enter or exit the W/EDF except in the event of an emergency. Clean debris and residue in the W/EDF daily. All surfaces in the W/EDF shall be wiped/hosed down after each shift and all debris shall be cleaned from the shower pan. The W/EDF shall consist of the following:

        - Wash Down Station: Provide an enclosed shower unit in the regulated area just outside the Wash Room as an equipment bag and container cleaning station.

        - Wash Room: Provide a wash room for cleaning of bagged or containerized asbestos containing waste materials passed from the regulated area. Construct the wash room using 50 x 100 mm (2 inches x 4 inches) wood framing and 3-layers of 6-mil fire retardant poly. Locate the wash room so that packaged materials, after being wiped clean, can be passed to the Holding Room. Doorways in the wash room shall be constructed of 2-layers of 6- mil fire retardant poly.

        - Holding Room: Provide a holding room as a drop location for bagged materials passed from the wash room. Construct the holding room using 50 x 100 mm (2 inches x 4 inches) wood framing or approved equivalent and 3-layers of 6-mil fire retardant poly. The holding room shall be located so that bagged material cannot be passed from the wash room to the clean room unless it goes

through the holding room. Doorways in the holding room shall be constructed of 2-layers of 6-mil fire retardant poly.

        - Clean Room: Provide a clean room to isolate the holding room from the exterior of the regulated area. Construct the clean room using 2 inches x 4 inches wood framing or approved equivalent and 2-layers of 6-mil fire retardant poly. The clean room shall be located so as to provide access to the holding room from the building exterior. Doorways to the clean room shall be constructed of 2-layers of 6-mil fire retardant poly. When a negative pressure differential system is used, a rigid enclosure separation between the W/EDF clean room and the adjacent areas shall be provided.

        - The W/EDF shall be as follows: Wash Room leading to a Holding Room followed by a Clean Room leading to outside the regulated area. See diagram.

    - Waste/Equipment Decontamination Procedures: At the washdown station in the regulated area, thoroughly wet wipe/clean contaminated equipment and/or sealed polyethylene bags and pass into Wash Room after visual inspection. When passing anything into the Wash Room, close all doorways of the W/EDF, other than the doorway between the washdown station and the Wash Room. Keep all outside personnel clear of the W/EDF. Once inside the Wash Room, wet clean the equipment and/or bags. After cleaning and inspection, pass items into the Holding Room. Close all doorways except the doorway between the Holding Room and the Clean Room. Workers from the Clean Room/Exterior shall enter the Holding Room

and remove the decontaminated/cleaned equipment/bags for removal and disposal. At no time shall personnel from the clean side be allowed to enter the Wash Room.

PART 2 - PRODUCTS, MATERIALS AND EQUIPMENT

  - MATERIALS AND EQUIPMENT

    - General Requirements (all abatement projects): Prior to the start of work, the contractor shall provide and maintain a sufficient quantity of materials and equipment to assure continuous and efficient work throughout the duration of the project. Work shall not start unless the following items have been delivered to the site and the CPIH/CIH has submitted verification to the VA's Representative.

      - All materials shall be delivered in their original package, container or bundle bearing the name of the manufacturer and the brand name (where applicable).

      - Store all materials subject to damage off the ground, away from wet or damp surfaces and under cover sufficient enough to prevent damage or contamination. Flammable and combustible materials cannot be stored inside buildings. Replacement materials shall be stored outside of the regulated area until abatement is completed.

      - The Contractor shall not block or hinder use of buildings by patients, staff, and visitors to the VA in partially occupied buildings by placing materials/equipment in any unauthorized location.

      - The Competent Person shall inspect for damaged, deteriorating or previously used materials. Such materials shall not be used and shall be removed from the worksite and disposed of properly.

      - Polyethylene sheeting for walls in the regulated area shall be a minimum of 4-mils. For floors and all other uses, sheeting of at least 6-mils shall be used in widths selected to minimize the frequency of joints. Fire retardant poly shall be used throughout.

      - The method of attaching polyethylene sheeting shall be agreed upon in advance by the Contractor and the VA and selected to minimize damage to equipment and surfaces. Method of attachment may include any combination of moisture resistant duct tape, poly tape, furring strips, spray glue, staples, nails, screws, lumber and plywood for enclosures or approved equivalent procedures capable of sealing

polyethylene to dissimilar finished or unfinished surfaces under both wet and dry conditions.

      - Polyethylene sheeting utilized for the PDF shall be opaque white or black in color, 6-mil fire retardant poly.

      - Installation and plumbing hardware, showers, hoses, drain pans, sump pumps and waste water filtration system shall be provided by the Contractor.

      - An adequate number of HEPA vacuums, scrapers, sprayers, nylon brushes, brooms, disposable mops, rags, sponges, staple guns, shovels, ladders and scaffolding of suitable height and length as well as meeting OSHA requirements, fall protection devices, water hose to reach all areas in the regulated area, airless spray equipment, and any other tools, materials or equipment required to conduct the abatement project. All electrically operated hand tools, equipment, electric cords shall be connected to GFCI protection.

      - Special protection for objects in the regulated area shall be detailed (e.g., plywood over carpeting or hardwood floors to prevent damage from scaffolds, water and falling material).

      - Disposal bags – 2-layers of 6-mil poly for asbestos waste shall be pre-printed with labels, markings and address as required by OSHA, EPA and DOT regulations.

      - The VA shall be provided an advance copy of the Safety Data Sheets (SDS) as required for all hazardous chemicals under OSHA 29 CFR 1910.1200 - Hazard Communication in the pre-project submittal.

Chlorinated compounds shall not be used with any spray adhesive, mastic remover or other product. Appropriate encapsulant(s) shall be provided.

      - OSHA DANGER demarcation signs, as many and as required by OSHA 29 CFR 1926.1101(k)(7) shall be provided and placed by the Competent Person. All other posters and notices required by Federal, State and Local regulations shall be posted in the Clean Room.

      - Adequate and appropriate PPE for the project and number of personnel/shifts shall be provided. All personal protective equipment issued must be based on a written hazard assessment conducted under 29 CFR 1910.132(d)

  - CONTAINMENT BARRIERS AND COVERINGS IN THE REGULATED AREA

    - General: Using critical barriers, seal off the perimeter to the regulated area to completely isolate the regulated area from adjacent spaces. All horizontal surfaces in the regulated area must be covered with 2-layers of 6-mil fire retardant poly to prevent contamination and to facilitate clean-up. Should adjacent areas become contaminated, immediately stop work and clean up the contamination at no additional cost to the Government. Provide firestopping and identify all fire barrier penetrations due to abatement work as specified in Section

2.2.7; FIRESTOPPING.

    - Preparation Prior to Sealing the Regulated Area: Place all tools, scaffolding, materials and equipment needed for working in the regulated area prior to erecting any plastic sheeting. Remove all uncontaminated removable furniture, equipment and/or supplies from the regulated area before commencing work, or completely cover with 2- layers of 6-mil fire retardant poly sheeting and secure with duct tape. Lock out and tag out any HVAC systems in the regulated area.

    - Controlling Access to the Regulated Area: Access to the regulated area is allowed only through the personnel decontamination facility (PDF), if required. All other means of access shall be eliminated and OSHA Danger demarcation signs posted as required by OSHA. If the regulated area is adjacent to or within view of an occupied area, provide a visual barrier of 6-mil opaque fire retardant poly sheeting to prevent building occupant observation. If the adjacent area is accessible to the public, the barrier must be solid.

    - Critical Barriers: Completely separate any openings into the regulated area from adjacent areas using fire retardant poly at least 6-mils thick and duct tape. Individually seal with 2-layers of independently installed 6-mil poly and duct tape all HVAC openings into the regulated area. Individually seal all lighting fixtures, clocks, doors, windows, convectors, speakers, or any other objects in the regulated area. Heat must be shut off any objects covered with poly.

    - Secondary Barriers: A loose layer of 6-mil fire retardant poly shall be used as a drop cloth to protect the floor/horizontal surfaces from debris generated during the Glovebag abatement. This layer shall be replaced as needed during the work.

    - Extension of the Regulated Area: If the enclosure of the regulated area is breached in any way that could allow contamination to occur, the affected area shall be included in the regulated area and constructed as per this section. If the affected area cannot be added to the regulated area, decontamination measures must be started immediately and continue until air monitoring indicates background levels are met.

    - Firestopping:

      - Through penetrations caused by cables, cable trays, pipes, sleeves must be firestopped with a fire-rated firestop system providing an air tight seal.

      - Firestop materials that are not equal to the wall or ceiling penetrated shall be brought to the attention of the VA Representative. The Contractor shall list all areas of penetration, the type of sealant used, and whether or not the location is fire rated. Any discovery of penetrations during abatement shall be brought to the attention of the VA Representative immediately. All walls, floors and ceilings are considered fire rated unless otherwise determined by the VA Representative or Fire Marshall.

      - Any visible openings whether or not caused by a penetration shall be reported by the Contractor to the VA Representative for a sealant system determination. Firestops shall meet ASTM E814 and UL 1479 requirements for the opening size, penetrant, and fire rating needed

  - MONITORING, INSPECTION AND TESTING

    - General:

      - Perform throughout abatement work monitoring, inspection and testing inside and around the regulated area in accordance with the OSHA requirements and these specifications. OSHA requires that the employee exposure to asbestos must not exceed 0.1 fibers per cubic centimeter (f/cc) of air, averaged over an 8-hour work shift. The CPIH/CIH is responsible for and shall inspect and oversee the performance of the Contractor IH Technician. The IH Technician shall continuously inspect and monitor conditions inside the regulated area to ensure compliance with these specifications. In addition, the CPIH/CIH shall personally manage air sample collection, analysis, and evaluation for personnel, regulated area, and adjacent area samples inside the building, but outside the regulated area.

Inside the building, but outside the regulated area air samples shall be collected at the boundary of the regulated area and/or Clean Room of the PDF, at the approximate location of HEPA exhaust discharge (if used), and at a minimum of three (3) locations in areas immediately outside the regulated work area to satisfy this specification. Additional inspection and testing requirements are also indicated in other parts of this specification.

      - The VA will employ an independent industrial hygienist (VPIH/CIH) consultant and/or use its own IH to perform various services on behalf of the VA. The VPIH/CIH will perform the necessary monitoring, inspection, testing, and other support services to ensure that VA patients, employees, and visitors will not be adversely affected by the abatement work, and that the abatement work proceeds in accordance with these specifications, that the abated areas or abated buildings have been successfully decontaminated. The work of the VPIH/CIH consultant in no way relieves the Contractor from their responsibility to perform the work in accordance with contract/specification requirements, to perform continuous inspection, monitoring and testing for the safety of their employees, and to perform other such services as specified. The cost of the VPIH/CIH and their services will be borne by the VA except for any repeat of final inspection and testing that may be required due to unsatisfactory initial results. Any repeated final inspections and/or testing, if required, will be paid for by the Contractor.

      - If fibers counted by the VPIH/CIH during abatement work, either inside or outside the regulated area, utilizing the NIOSH 7400 air monitoring method, exceed the specified respective limits, the Contractor shall stop work. The Contractor may request confirmation of the results by analysis of the samples by TEM. Request must be in writing and submitted to the VA's Representative. Cost for the confirmation of results will be borne by the Contractor for both the collection and analysis of samples and for the time delay that may/does result for this confirmation. Confirmation sampling and analysis will be the responsibility of the CPIH/CIH with review and approval of the VPIH/CIH. An agreement between the CPIH/CIH and the

VPIH/CIH shall be reached on the exact details of the confirmation effort, in writing, including such things as the number of samples, location, collection, quality control on-site, analytical laboratory, interpretation of results and any follow-up actions.

This written agreement shall be co-signed by the IH's and delivered to the VA's Representative.

    - Scope of Services of the VPIH/CIH Consultant:

      - The purpose of the work of the VPIH/CIH is to: Assure quality; resolve problems; and prevent the spread of contamination beyond the regulated area. In addition, their work includes performing the final inspection and testing to determine whether the regulated area or building has been adequately decontaminated. All air monitoring is to be done utilizing PCM/TEM. The VPIH/CIH will perform the following tasks:

        - Task 1: Establish background levels before abatement begins by collecting background samples. Retain samples for possible TEM analysis.

        - Task 2: Perform representative air monitoring, inspection, and testing outside the regulated area during actual abatement work to detect any faults in the regulated area isolation and any adverse impact on the surroundings from regulated area activities.

        - Task 3: Perform unannounced visits to spot check overall compliance of work with contract/specifications. These visits may include any inspection, monitoring, and testing inside and outside the regulated area and all aspects of the operation except personnel monitoring.

        - Task 4: Provide support to the VA Representative such as evaluation of submittals from the Contractor, resolution of unforeseen developments, etc.

        - Task 5: Perform, in the presence of the VA Representative, final inspection and testing of a decontaminated regulated area or building at the conclusion of the abatement and clean-up work to certify compliance with all regulations and the VA requirements/specifications.

        - Task 6: Issue certificate of decontamination for each regulated area or building and project report.

      - All data, inspection results and testing results generated by the VPIH/CIH will be available to the Contractor for information and consideration. The Contractor shall cooperate with and support the VPIH/CIH for efficient and smooth performance of their work.

      - The monitoring and inspection results of the VPIH/CIH will be used by the VA to issue any Stop Removal orders to the Contractor during abatement work and to accept or reject a regulated area or building as decontaminated.

      - Monitoring, Inspection and Testing by Abatement Contractor CPIH/CIH: The Contractor’s CPIH/CIH is responsible for managing all monitoring, inspections, and testing required by these specifications, as well as any and all regulatory requirements adopted by these specifications. The CPIH/CIH is responsible for the continuous monitoring of all subsystems and procedures which could affect the health and safety of the Contractor’s personnel. Safety and health conditions and the provision of those conditions inside the regulated area for all persons entering the regulated area is the exclusive responsibility of the Contractor/Competent Person. The person performing the personnel and area air monitoring inside the regulated area shall be an IH Technician, who shall be trained and shall have specialized field experience in sampling and analysis. The IH Technician shall have successfully completed a NIOSH 582 Course or equivalent and provide documentation. The IH Technician shall participate in the AIHA Asbestos Analysis Registry or participate in the Proficiency Analytical Testing program of AIHA for fiber counting quality control assurance. The IH Technician shall also be an accredited EPA AHERA/State Contractor/Supervisor and Building Inspector. The IH Technician shall have participated in five abatement projects collecting personal and area samples and have experience in substantially similar projects in size and scope. The analytical laboratory used by the Contractor to analyze the samples shall be AIHA accredited for asbestos PAT and approved by the VA prior to start of the project. A daily log shall be maintained by the CPIH/CIH or IH Technician, documenting all OSHA

requirements for personal and area air monitoring for asbestos in 29 CFR 1926.1101(f), (g) and Appendix A. This log shall be made available to the VA Representative and the VPIH/CIH upon request.

The log will contain, at a minimum, information on personnel or area samples, other persons represented by the sample, the date of sample collection, start and stop times for sampling, sample volume, flow rate, and fibers/cc. The CPIH/CIH shall collect and analyze samples for each representative job being done in the regulated area, i.e., removal, wetting, clean-up, and load-out. No fewer than two (2) personal air samples or 25% of representative workforce per shift shall be collected, whichever is greater, in the regulated area; a minimum of three (3) area air samples at locations inside the building but immediately outside the regulated work area; one (1) area air sample shall be collected daily at the boundary of the regulated area and/or Clean Room of the PDF; and one (1) area air sample shall be collected daily at the approximate location of HEPA exhaust discharge, if used. In addition to the continuous monitoring required, the CPIH/CIH will perform inspection and testing at the final stages of abatement for each regulated area as specified in the CPIH/CIH responsibilities. Additionally, the CPIH/CIH will monitor and record pressure readings within the containment daily with a minimum of two readings at the beginning and at the end of a shift, and submit the data in the daily report. Pressure readings with the containment may be omitted if negative pressure Glovebag procedures are used.

  - ASBESTOS HAZARD ABATEMENT PLAN

    - The Contractor shall have established Asbestos Hazard Abatement Plan (AHAP) in printed form and loose leaf folder consisting of simplified text, diagrams, sketches, and pictures that establish and explain clearly the ways and procedures to be followed during all phases of the work by the Contractor's personnel. The AHAP must be modified as needed to address specific requirements of the project. The AHAP shall be submitted for review and approval prior to the start of any abatement work. The minimum topics and areas to be covered by the AHAP(s) are:

      - Minimum Personnel Qualifications

      - Contingency Plans and Arrangements

      - Security and Safety Procedures

      - Respiratory Protection/Personal Protective Equipment Program and Training

      - Medical Surveillance Program and Recordkeeping

      - Regulated Area Requirements for Glovebag Abatement

      - Decontamination Facilities and Entry/Exit Procedures (PDF and W/EDF) or approved equivalent.

      - Monitoring, Inspections, and Testing

      - Removal Procedures for Piping ACM Using the Glovebag Method

      - Disposal of ACM waste

      - Regulated Area Decontamination/Clean-up

      - Regulated Area Visual and Air Clearance

      - Project Completion/Closeout

  - SUBMITTALS

    - Pre-Start Meeting Submittals:

      - Submit to the VA a minimum of 14 days prior to the pre-start meeting the following for review and approval. Meeting this requirement is a prerequisite for the pre-start meeting for this project:

        - Submit a detailed work schedule for the entire project reflecting contract documents and the phasing/schedule requirements from the CPM chart.

        - Submit a staff organization chart showing all personnel who will be working on the project and their capacity/function. Provide their qualifications, training, accreditations, and licenses, as appropriate. Provide a copy of the "Certificate of Worker's Acknowledgment" and the "Affidavit of Medical Surveillance and Respiratory Protection" for each person.

        - Submit Asbestos Hazard Abatement Plan developed specifically for this project, incorporating the requirements of the specifications, prepared, signed and dated by the CPIH/CIH.

        - Submit the specifics of the materials and equipment to be used for this project with manufacturer names, model numbers, performance characteristics, pictures/diagrams, and number available for the following:

          - Supplied air system, negative air machines, HEPA vacuums, air monitoring pumps, calibration devices, pressure differential monitoring device and emergency power generating system.

          - Waste water filtration system, shower system, containment barriers.

          - Encapsulantys, surfactants, hand held sprayers, airless sprayers, Glovebas, and fire extinguishers.

          - Respirators, water filtration system, shower system, containment barriers equipment.

          - Fire safety equipment to be used in the regulated area.

        - Submit the name, location, and phone number of the approved landfill; proof/verification the landfill is approved for ACM disposal; the landfill's requirements for ACM waste; the type of vehicle to be used for transportation; and name, address, and phone number of subcontractor, if used. Proof of asbestos training for transportation personnel shall be provided.

        - Submit required notifications and arrangements made with regulatory agencies having regulatory jurisdiction and the specific contingency/emergency arrangements made with local health, fire, ambulance, hospital authorities and any other notifications/arrangements.

        - Submit the name, location and verification of the laboratory and/or personnel to be used for analysis of air and/or bulk samples. Personal air monitoring must be done in accordance with OSHA 29 CFR 1926.1101(f) and Appendix A. Area or clearance air monitoring shall be conducted in accordance with EPA AHERA protocols.

        - Submit qualifications verification: Submit the following evidence of qualifications. Make sure that all references are current and verifiable by providing current phone numbers and documentation.

          - Asbestos Abatement Company: Project experience within the past

3 years; listing projects first most similar to this project; Project Name; Type of Abatement; Duration; Cost; Reference Name/Phone Number; Final Clearance; and Completion Date.

          - List of project(s) halted by owner, A/E, IH, regulatory agency in the last 3 years: Project Name; Reason; Date; Reference Name/Number; and Resolution.

          - List asbestos regulatory citations (e.g., OSHA), notices of violations (e.g., Federal, State, Local NESHAP), penalties, and legal actions taken against the company including the company’s officers (including damages paid) in the last 3 years. Provide copies and all information needed for verification.

        - Submit information on personnel: Provide a resume; address each item completely; copies of certificates, accreditations, and licenses. Submit an affidavit signed by the CPIH/CIH stating that all personnel submitted below have medical records in accordance with OSHA 29 CFR 1926.1101(m) and that the company has implemented a medical surveillance program and written respiratory protection program, and maintains recordkeeping in accordance with the above regulations. Submit the phone number and doctor/clinic/hospital used for medical evaluations.

          - CPIH/CIH and IH Technician: Name; years of abatement experience; list of projects similar to this one; certificates, licenses, accreditations for proof of AHERA/OSHA specialized asbestos training; professional affiliations; medical opinion; and current respirator fit test.

          - Competent Person(s)/Supervisor(s): Number; names; last four digits of social security numbers; years of abatement experience as Competent Person/Supervisor; list of similar projects in size/complexity as Competent Person/Supervisor; as a worker; certificates, licenses, accreditations; proof of AHERA/OSHA specialized asbestos training; maximum number of personnel supervised on a project; medical opinion (asbestos surveillance and respirator use); and current respirator fit test.

          - Workers: Numbers; names; last four digits of social security numbers; years of abatement experience; certificates, licenses, accreditations; training courses in asbestos abatement and respiratory protection; medical opinion

(asbestos surveillance and respirator use); and current respirator fit test.

        - Submit copies of State license for asbestos abatement; copy of insurance policy, including exclusions with a letter from agent stating in plain language the coverage provided and the fact that asbestos abatement activities are covered by the policy; copy of AHAP(s) incorporating the requirements of this specification; information on who provides your training, how often; who provides medical surveillance, how often; who performs and how is personal air monitoring of abatement workers conducted; a list of references of independent laboratories/IH's familiar with your air monitoring and Asbestos Hazard Abatement Plans; copies of monitoring results of the five referenced projects listed and analytical method(s) used.

        - Rented equipment must be decontaminated prior to returning to the rental agency.

        - Submit, before the start of work, the manufacturer's technical data for all types of encapsulants, all SDS, and application instructions.

    - Submittals During Abatement:

      - The Competent Person shall maintain and submit a daily log at the regulated area documenting the dates and times of the following: purpose, attendees and summary of meetings; all personnel entering/exiting the regulated area; document and discuss the resolution of unusual events such as barrier breeching, equipment failures, emergencies, and any cause for stopping work; representative air monitoring and results/TWAs/ELs. Submit this information daily to the VA's Representative.

      - The CPIH/CIH shall document and maintain the inspection and approval of the regulated area preparation prior to start of work and daily during work.

        - Removal of any poly barriers and/or failure of negative pressure Glovebags.

        - Visual inspection/testing by the CPIH/CIH or IH Technician prior to application of lockdown encapsulant.

        - Packaging and removal of ACM waste from regulated area.

        - Disposal of ACM waste materials; copies of Waste Shipment Records/landfill receipts to the VA's Representative on a weekly basis.

    - Submittals at Completion of Abatement: The CPIH/CIH shall submit a project report consisting of the daily log book requirements and documentation of events during the abatement project including Waste Shipment Records signed by the landfill's agent. It will also include information on the containment and transportation of waste from the containment with applicable Chain of Custody forms. The report shall include a certificate of completion, signed and dated by the CPIH/CIH, in accordance with Attachment #1. All clearance and perimeter area samples must be submitted. The VA Representative will retain the abatement report after completion of the project and provide copies of the abatement report to VAMC Office of Engineer and the Safety Office.

  - ENCAPSULANTS

    - Types of Encapsulants:

      - The following four types of encapsulants must comply with performance requirements as stated in paragraph 2.6.2:

        - Removal encapsulant - used as a wetting agent to remove ACM.

        - Bridging encapsulant - provides a tough, durable coating on ACM.

        - Penetrating encapsulant - penetrates/encapsulates ACM at least 13 mm (1/2 inch).

        - Lockdown encapsulant - seals microscopic fibers on surfaces after ACM removal.

    - Performance Requirements:

      - Encapsulants shall meet the latest requirements of EPA; shall not contain toxic or hazardous substances; or solvents; and shall comply with the following performance requirements:

        - General Requirements for all Encapsulants:

          - ASTM E84: Flame spread of 25; smoke emission of 50.

          - University of Pittsburgh Protocol: Combustion Toxicity; zero mortality.

          - ASTM C732: Accelerated Aging Test; Life Expectancy - 20 years.

          - ASTM E96: Permeability - minimum of 0.4 perms.

        - Bridging/Penetrating Encapsulants:

          - ASTM E736: Cohesion/Adhesion Test - 24 kPa (50 pounds/square foot).

          - ASTM E119: Fire Resistance - 3 hours (Classified by UL for use on fibrous/cementitious fireproofing).

          - ASTM D2794: Gardner Impact Test; Impact Resistance - minimum

11.5 kg-mm (43 in/lb).

          - ASTM D522: Mandrel Bend Test; Flexibility - no rupture or cracking

        - Lockdown Encapsulants:

          - ASTM E119: Fire resistance - 3 hours (tested with fireproofing over encapsulant applied directly to steel member).

          - ASTM E736: Bond Strength - 48 kPa (100 pounds/square foot) (test compatibility with cementitious and fibrous fireproofing).

          - In certain situations, encapsulants may have to be applied to hot pipes/equipment. The encapsulant must be able to withstand high temperatures without cracking or creating any noxious gaseous or vapors during or after application.

  - CERTIFICATES OF COMPLIANCE

    - The Contractor shall submit to the VA Representative certification from the manufacturer indicating compliance with performance requirements for encapsulants when applied according to manufacturer recommendations.

    - Recyclable Protective Clothing: If recyclable clothing is provided, all requirements of EPA, DOT and OSHA shall be met.

PART 3 - EXECUTION

  - REGULATED AREA PREPARATIONS

    - Site Security:

      - Regulated area access is to be restricted only to authorized, trained/accredited and protected personnel. These may include the Contractor's employees, employees of Subcontractors, VA employees and representatives, State and Local inspectors, and any other designated individuals. A list of authorized personnel shall be established prior to commencing the project and shall be posted in the clean room of the decontamination unit or in a designated area

located immediately outside of the regulated area established for Glovebag removal activities.

      - Entry into the regulated area by unauthorized individuals shall be reported immediately to the Competent Person by anyone observing the entry. The Competent Person shall immediately require any unauthorized person to leave the regulated area and then notify the VA Contracting Officer or VA Representative using the most expeditious means.

      - A log book shall be maintained in the clean room of the decontamination unit or in a designated area located immediately outside of the regulated area established for Glovebag removal activities. Anyone who enters the regulated area must record their name, affiliation, time in, and time out for each entry.

      - Access to the regulated area shall be through a single decontamination unit or in an area designated by the Competent Person for Glovebag removal activities. All other access (doors, windows, hallways, etc.) shall be sealed or locked to prevent entry to or exit from the regulated area. The only exceptions for this requirement are the waste/equipment load-out area which shall be sealed except during the removal of containerized asbestos waste from the regulated area, and emergency exits. Emergency exits shall not be locked from the inside; however, they shall be sealed with poly sheeting and taped until needed. In any situation where exposure to high temperatures which may result in a flame hazard, fire retardant poly sheeting must be used.

      - The Contractor's Competent Person shall control site security during abatement operations in order to isolate work in progress and protect adjacent personnel. A 24 hour security system shall be provided at the entrance to the regulated area to assure that all entrants are logged in/out and that only authorized personnel are allowed entrance.

      - The Contractor will have the VA's assistance in notifying adjacent personnel of the presence, location and quantity of ACM in the regulated area and enforcement of restricted access by the VA's employees.

      - The regulated area shall be locked during non-working hours and secured by VA Representative or Competent Person. The VA Police shall be informed of asbestos abatement regulated areas to provide security checks during facility rounds and emergency response.

    - OSHA Danger Signs: Post OSHA DANGER signs meeting the specifications of OSHA 29 CFR 1926.1101 at any location and approaches to the regulated area where airborne concentrations of asbestos may exceed ambient background levels. Signs shall be posted at a distance sufficiently far enough away from the regulated area to permit any personnel to read the sign and take the necessary measures to avoid exposure. Additional signs will be posted following construction of the regulated area enclosure.

    - Shut Down - Lock Out Electrical: Shut down and lock out/tag out electric power to the regulated area. Provide temporary power and lighting. Insure safe installation including GFCI of temporary power sources and equipment by compliance with all applicable electrical code requirements and OSHA requirements for temporary electrical systems. Electricity shall be provided by the VA.

    - Shut Down - Lock Out HVAC: Shut down and lock out/tag out heating, cooling, and air conditioning system (HVAC) components that are in, supply or pass through the regulated area. Investigate the regulated area and agree on pre-abatement condition with the VA's Representative. Seal all intake and exhaust vents in the regulated area with duct tape and 2-ayers of independently installed 6-mil poly. Also, seal any seams in system components that pass through the regulated area. Remove all contaminated HVAC system filters and place in labeled 6-mil poly disposal bags for disposal as asbestos waste.

    - Containment Barriers and Coverings for the Regulated Area:

      - General: Seal off any openings at the perimeter of the regulated area with critical barriers to completely isolate the regulated area and to contain all airborne asbestos contamination created by the abatement activities. Should the adjacent area past the regulated area become contaminated due to improper work activities, the Contractor shall suspend work inside the regulated area, continue wetting, and clean the adjacent areas in accordance with procedures

described in these specifications. Any and all costs associated with the adjacent area cleanup shall not be borne by the VA.

      - Preparation Prior to Sealing Off: Place all materials, equipment and supplies necessary to isolate the regulated area inside the regulated area. Remove all movable material/equipment as described above and secure all unmovable material/equipment as described above. Properly secured material/ equipment shall be considered to be outside the regulated area.

      - Controlling Access to the Regulated Area: Access to the regulated area is allowed only through the personnel decontamination facility (PDF) or in an area designated by the Competent Person for Glovebag removal activities. All other means of access shall be eliminated and OSHA DANGER demarcation signs posted as required by OSHA. If the regulated area is adjacent to, or within view of an occupied area, provide a visual barrier of 6-mil opaque fire retardant poly to prevent building occupant observation. If the adjacent area is accessible to the public, the barrier must be solid and capable of withstanding the negative pressure.

      - Critical Barriers: The regulated area must be completely separated from the adjacent area(s) and the outside by at least 2-layers of independently installed 6-mil fire retardant poly and duct tape/spray adhesive. Individually seal all supply and exhaust ventilation openings, lighting fixtures, clocks, doorways, windows, convectors, speakers, and other openings into the regulated area with 2-layers of 6-mil fire retardant poly, and taped securely in place with duct tape/spray adhesive. Critical barriers must remain in place until all work and clearances have been completed. Light fixtures shall not be operational during abatement. Auxiliary lighting shall be provided. If needed, provide plywood squares 6 inches x 6 inches x 3/8 inch (150mm x 150mm x 18mm) or approved equivalent, held in place with 6d smooth masonry/galvanized nail or approved equivalent driven through the center of the plywood square and duct tape on the poly so as to clamp the poly to the wall/surface. Locate plywood squares at each end, corner, and 4 feet (1200mm) maximum on centers

      - Extension of the Regulated Area: If the regulated area barrier is breached in any manner that could allow the passage of asbestos fibers or debris, the Competent Person shall immediately stop work, continue wetting, and proceed to extend the regulated area to enclose the affected area as per procedures described in this specification. If the affected area cannot be enclosed, decontamination measures and cleanup shall start immediately. All personnel shall be isolated from the affected area until decontamination/cleanup is completed as verified by visual inspection and air monitoring. Air monitoring at completion must indicate background levels.

      - Floor Barriers: All floors within 10 feet of Glovebag work shall be covered with 2-layers of 6-mil fire retardant poly. If no breach occurs during the Glovebag abatement operation, these layers of 6─mil fire retardant poly may be reused

    - Sanitary Facilities: The Contractor shall provide sanitary facilities for abatement personnel and maintain them in a clean and sanitary condition throughout the abatement project.

    - Pre-Cleaning:

      - Pre-Cleaning Movable Objects:

        - The VA will provide water for abatement purposes. The Contractor shall connect to the existing VA system. The service to the shower(s), if used, shall be supplied with backflow prevention.

        - Pre-cleaning of ACM contaminated items shall be performed after the enclosure has been erected and negative pressure has been established in the work area. PPE must be donned by all workers performing pre-cleaning activities. After items have been pre- cleaned and decontaminated, they may be removed from the work area for storage until the completion of abatement in the work area.

        - Pre-clean all movable objects within the regulated area using a HEPA filtered vacuum and/or wet cleaning methods as appropriate. After cleaning, these objects shall be removed from the regulated area and carefully stored in an uncontaminated location.

      - Pre-Cleaning Fixed Objects:

        - Pre-cleaning of ACM contaminated items shall be performed after the enclosure has been erected and negative pressure has been established in the work area.

        - Pre-clean all fixed objects in the regulated area using HEPA filtered vacuums and wet cleaning techniques as appropriate. Careful attention must be paid to machinery behind grills or gratings where access may be difficult but contamination may be significant. Also, pay particular attention to wall, floor and ceiling penetration behind fixed items. After pre-cleaning, enclose fixed objects with 2-layers of 6-mil poly and seal securely in place with duct tape. Objects (e.g., permanent fixtures, shelves, electronic equipment, laboratory tables, sprinklers, alarm systems, closed circuit TV equipment and computer cables) which must remain in the regulated area and that require special ventilation or enclosure requirements should be designated here along with specified means of protection. Contact the manufacturer for special protection requirements.

      - Pre-Cleaning Surfaces in the Regulated Area:

        - Pre-cleaning of ACM contaminated items shall be performed after the enclosure has been erected and negative pressure has been established in the work area.

        - Pre-clean all surfaces in the regulated area using HEPA filtered vacuums and wet cleaning methods as appropriate. Do not use any methods that would raise dust such as dry sweeping or vacuuming with equipment not equipped with HEPA filters. Do not disturb asbestos-containing materials during this pre-cleaning phase.

    - Pre-Abatement Activities:

      - Pre-Abatement Meeting: The VA Representative, upon receipt, review, and substantial approval of all pre-abatement submittals and verification by the CPIH/CIH that all materials and equipment required for the project are on the site, will arrange for a pre- abatement meeting between the Contractor, the CPIH/CIH, Competent Person, the VA Representatives, and the VPIH/CIH. The purpose of the meeting is to discuss any aspect of the submittals needing clarification or amplification and to discuss any aspect of the project execution and the sequence of the operation. The Contractor

shall be prepared to provide any supplemental information or documentation to the VA's Representative regarding any submittals, materials or equipment. Upon satisfactory resolution of any outstanding issues, the VA's representative will issue a written order to proceed to the Contractor. No abatement work of any kind described in the following provisions shall be initiated prior to the VA written order to proceed.

      - Pre-Abatement Inspections and Preparations:

        - Before any work begins on the construction of the regulated area, the Contractor will:

          - Conduct a space-by-space inspection with an authorized VA Representative and prepare a written inventory of all existing damage in those spaces where asbestos abatement will occur. Still or video photography may be used to supplement the written damage inventory. Document will be signed and certified as accurate by both parties.

          - The VA Representative, the Contractor, and the VPIH/CIH must be aware of AEQA 10-95 indicating the failure to identify asbestos in the areas listed as well as common issues when preparing specifications and contract documents. This is especially critical when demolition is planned, because AHERA surveys are non-destructive, and ACM may remain undetected. A NESHAP (destructive) ACM inspection should be conducted on all building structures that will be demolished. Ensure the following areas are inspected on the project: Lay-in ceilings concealing ACM; ACM behind walls/windows from previous renovations; inside utility chases/walls; transite piping/ductwork/sheets; behind radiators; lab fume hoods; transite lab countertops; roofing materials; below window sills; water/sewer lines; electrical conduit coverings; crawl spaces( previous abatement contamination); flooring/mastic covered by carpeting/new flooring; exterior insulated wall panels; on underground fuel tanks; and steam line trench coverings.

          - Ensure that all furniture, machinery, equipment, curtains, drapes, blinds, and other movable objects required to be

removed from the regulated area have been cleaned and removed or properly protected from contamination.

          - Inspect existing firestopping in the regulated area. Correct as needed.

      - Pre-Abatement Construction and Operations:

        - Perform all preparatory work for the first regulated area in accordance with the approved work schedule and with this specification.

        - Upon completion of all preparatory work, the CPIH/CIH will inspect the work and systems and will notify the VA's Representative when the work is completed in accordance with this specification. The VA's Representative may inspect the regulated area and the systems with the VPIH/CIH and may require that upon satisfactory inspection, the Contractor's employees perform all major aspects of the approved AHAP(s), especially worker protection, respiratory systems, contingency plans, decontamination procedures, and monitoring to demonstrate satisfactory operation.

        - The CPIH/CIH shall document the pre-abatement activities described above and deliver a copy to the VA's Representative.

        - Upon satisfactory inspection of the installation of and operation of systems the VA's Representative will notify the Contractor in writing to proceed with the asbestos abatement work in accordance with this specification.

  - REMOVAL OF PIPING ACM

    - Wetting Materials:

      - Use amended water for the wetting of ACM prior to removal. The Competent Person shall assure that the wetting of ACM meets the definition of "adequately wet" in the EPA NESHAP regulation and OSHA’s “wet methods” for the duration of the project. A removal encapsulant may be used instead of amended water with written approval of the VA's Representative.

      - Amended Water: Provide water to which a surfactant has been added to wet the ACM and reduce the potential for fiber release during disturbance of ACM. The mixture must be equal to or greater than the wetting provided by water amended by a surfactant consisting of one

ounce of 50 percent polyoxyethylene ester and 50 percent polyoxyethylene ether mixed with 5 gallons (19L) of water.

      - Removal Encapsulant: Provide a penetrating encapsulant designed specifically for the removal of ACM. The material must, when used, result in adequate wetting of the ACM and retard fiber release during disturbance equal to or greater than the amended water described above in B.

    - Secondary Barrier and Walkways: Install as a drop cloth a 6-mil poly sheet at the beginning of each work shift where removal is to be done during that shift. Secure the drop cloth (6-mil poly sheet) with duct tape or approved equivalent to prevent it from moving or debris from getting behind it. Remove the drop cloth (6-mil poly sheet) at the end of the shift or as work in the area is completed. Keep residue on the drop cloth (6-mil poly sheet) wetted. When removing, fold inward to prevent spillage and place in a disposal bag.

    - Wet Removal of ACM: Using acceptable Glovebag procedures, adequately and thoroughly wet the ACM to be removed prior to removal with amended water or when authorized by VA, removal encapsulant to reduce/prevent fiber release to the air. Adequate time must be allowed for the amended water or removal encapsulant to saturate the ACM. Abatement personnel must not disturb dry ACM. Use a fine spray of amended water or removal encapsulant. Saturate the material sufficiently to wet to the substrate without causing excessive dripping. The material must be sprayed repeatedly/continuously during the removal process in order to maintain adequately wet conditions. Removal encapsulants must be applied in accordance with the manufacturer's written instructions. Perforate or carefully separate, using wet methods, an outer covering that is painted or jacketed in order to allow penetration and wetting of the material. Where necessary, carefully remove covering while wetting to minimize fiber release.

  - GLOVEBAG REMOVAL PROCEDURES

    - General: All applicable OSHA requirements and Glovebag manufacturer’s recommendations shall be met during Glovebag removal operations. In cases where live steam lines are present, the lines must be shut down prior to any work being performed on the system. No abatement work shall be conducted on live, pressurized steam lines. The Contractor may

choose to use a High Temperature Glovebag in which a temperature rating ranges from 300˚F to 700˚F on steam lines that have recently been shut down and remain at high temperature for some time. In the case where a Glovebag is not feasible, the Contractor will need to build a full negative pressure containment of sufficient size or work within a negative pressure mini-enclosure and follow all regulations as it pertains to removal. The Contractor shall provide enough HEPA negative air machines to continuously maintain a negative pressure differential of -0.02 inch water column gauge (WCG) inside the regulated work area relative to adjacent non-work building areas. OSHA 29 CFR 1926.1101 (g)(5)(i)(A)(2) also requires at least four (4) air changes per hour.

Contractor shall increase air changes per hour as necessary to maintain volatile organic compounds below the applicable OSHA PEL. Contractor shall protect pipe insulation from being disturbed on either side of the Glovebag removal operations with a “candy stripe” layer of 6-mil poly sheet and duct tape, if Glove bag removal activities cause the piping to dislodge ACM during performance of their work.

      - Mix the surfactant with water in the garden sprayer, following the manufacturer's directions.

      - Have each employee put on a HEPA filtered respirator approved for asbestos and check the fit using the positive/negative fit check.

      - Have each employee put on a disposable full-body suit. Remember, the hood goes over the respirator straps.

      - Check closely the integrity of the glove bag to be used. Check all seams, gloves, sleeves, and glove openings. OSHA requires the bottom of the bag to be seamless.

      - Check the pipe where the work will be performed. If it is damaged (broken lagging, hanging, etc.), wrap the entire length of the pipe in poly sheeting and "candy stripe" it with duct tape.

      - Attach Glovebag with required tools per manufacturer’s instructions.

      - Using the smoke tube and aspirator bulb, test 10 percent of Glovebags by placing the tube into the water porthole (two-inch opening to glove bag), and fill the bag with smoke and squeeze it. If leaks are found, they shall be taped closed using duct tape and the bag shall be retested with smoke.

      - Insert the wand from the water sprayer through the water porthole.

      - Insert the hose end from a HEPA vacuum into the upper portion of the glove bag.

      - Wet and remove the pipe insulation.

      - If the section of pipe is covered with an aluminum jacket, remove it first using the wire cutters to cut any bands and then use tin snips to remove the aluminum. It is important to fold the sharp edges in to prevent cutting the bag when placing it in the bottom.

      - When the work is complete, spray the upper portion of the bag and move all residue into the bottom of the bag with the other waste material. Be very thorough. Use adequate water.

      - Put all tools, after washing them off in the bag, in one of the sleeves of glove bag and turn it inside out, drawing it outside of the bag. Twist the sleeve tightly several times to seal it and tape it several tight turns with duct tape. Cut through the middle of the duct tape and remove the sleeve. Put the sleeve in the next glove bag or put it in a bucket of water to decontaminate the tools after cutting the sleeve open.

      - Turn on the HEPA vacuum and collapse the bag completely. Remove the vacuum nozzle, seal the hole with duct tape, twist the bag tightly several times in the middle, and tape it to keep the material in the bottom during removal of the glove bag from the pipe.

      - Slip a disposal bag over the glove bag (still attached to the pipe).

Remove the tape securing the ends, and slit open the top of the glove bag and carefully fold it down into the disposal bag. Double bag and gooseneck waste materials.

    - Negative Pressure Glovebag Procedure:

      - In addition to the above requirements, the HEPA vacuum shall be run continuously during the Glovebag procedure until completion at which time the Glovebag will be collapsed by the HEPA vacuum prior to removal from the pipe/component.

      - The HEPA vacuum shall be attached and operated as needed to prevent collapse of the Glovebag during the removal process.

  - LOCKDOWN ENCAPSULATION

    - General: Lockdown encapsulation is an integral part of the ACM removal. At the conclusion of ACM removal and before removal of the primary

barriers, all piping surfaces shall be encapsulated with a bridging encapsulant.

    - Sealing Exposed Edges: Seal edges of ACM exposed by removal work with two coats of encapsulant. Prior to sealing, permit the exposed edges to dry completely to permit penetration of the encapsulant.

  - DISPOSAL OF ACM WASTE MATERIALS

    - General: Dispose of waste ACM and debris which is packaged in accordance with these specifications, OSHA, EPA and DOT. The landfill requirements for packaging must also be met. Transport will be in compliance with 49 CFR 171 - 180 regulations. Disposal shall be done at an approved landfill. Disposal of non-friable ACM shall be done in accordance with applicable regulations.

    - Procedures:

      - The VA must be notified at least 24 hours in advance of any waste removed from the containment

      - Asbestos waste shall be packaged and moved through the W/EDF into a covered transport container in accordance with procedures in this specification. Waste shall be double-bagged and wetted with amended water prior to disposal. Wetted waste can be very heavy. Bags shall not be overfilled. Bags shall be securely sealed to prevent accidental opening and/or leakage. The top shall be tightly twisted and goose necked prior to tightly sealing with at least three wraps of duct tape. Ensure that unauthorized persons do not have access to the waste material once it is outside the regulated area. All transport containers must be covered at all times when not in use. OSHA Danger signs must be displayed during loading and unloading. Material shall not be transported in open vehicles. If drums are used for packaging, the drums shall be labeled properly and shall not be re-used.

      - Waste Load Out: Waste load out shall be done in accordance with the procedures in W/EDF Decontamination Procedures. Sealed waste bags shall be decontaminated on exterior surfaces by wet cleaning and HEPA vacuuming before being placed in the second waste bag and sealed, which then must also be wet wiped and HEPA vacuumed.

      - Asbestos waste with sharp edged components, i.e., nails, screws, lath, strapping, tin sheeting, jacketing, metal mesh, etc., which

might tear poly bags shall be wrapped securely in burlap before packaging and, if needed, use a poly lined fiber drum as the second container, prior to disposal.

  - PROJECT DECONTAMINATION

    - General:

      - The entire work related to project decontamination shall be performed under the close supervision and monitoring of the CPIH/CIH.

      - If the asbestos abatement work is in an area which was contaminated prior to the start of abatement, the decontamination will be done by cleaning the primary poly barrier prior to its removal and cleanings of the surfaces of the regulated area after the primary barrier removal.

      - If the asbestos abatement work is in an area which was uncontaminated prior to the start of abatement, the decontamination will be done by cleaning the primary poly barrier prior to its removal, thus preventing contamination of the building when the regulated area critical barriers are removed.

    - Regulated Area Clearance: Air testing and other requirements which must be met before release of the Contractor and re-occupancy of the regulated area space are specified in Final Testing Procedures.

    - Work Description: Decontamination includes the clearance air testing in the regulated area and the decontamination and removal of the enclosures/facilities installed prior to the abatement work including primary/critical barriers, PDF and W/EDF facilities, and negative pressure systems.

    - Pre-Decontamination Conditions:

      - Before decontamination starts, all ACM waste from the regulated area shall be removed, all waste collected and removed, and the secondary barrier of poly removed and disposed of along with any gross debris generated by the work.

      - At the start of decontamination, the following shall be in place.

        - Critical barriers over all openings consisting of two layers of 6-mil poly which is the sole barrier between the regulated area and the rest of the building or outside.

        - Decontamination facilities, if required for personnel and equipment in operating condition.

    - First Cleaning: Carry out a first cleaning of all surfaces of the regulated area including items of remaining poly sheeting, tools, scaffolding, ladders/staging by wet methods and HEPA vacuuming. Do not use dry dusting/sweeping/air blowing methods. Use each surface of a wetted cleaning cloth one time only and then dispose of as contaminated waste. Continue this cleaning until there is no visible residue from abated surfaces or poly or other surfaces. Remove all filters in the air handling system and dispose of as ACM waste in accordance with these specifications. The negative pressure system shall remain in operation during this time, if used. Additional cleaning may be needed as determined by the CPIH/VPIH/CIH.

    - Pre-Clearance Inspection and Testing: The CPIH/CIH and VPIH/CIH will perform a thorough and detailed visual inspection at the end of the cleaning to determine whether there is any visible residue in the regulated area. If the visual inspection is acceptable, the CPIH/CIH will perform pre-clearance sampling using aggressive clearance as detailed in 40 CFR 763 Subpart E (AHERA) Appendix A (III)(B)(7)(d). If the sampling results show values below 0.01 f/cc, then the Contractor shall notify the VA's Representative of the results with a brief report from the CPIH/CIH documenting the inspection and sampling results and a statement verifying that the regulated area is ready for lockdown encapsulation. The VA reserves the right to utilize their own VPIH/CIH to perform a pre-clearance inspection and testing for verification.

    - Lockdown Encapsulation of Abated Surfaces: With the express written permission of the VA's Representative, perform lockdown encapsulation of all surfaces from which asbestos was abated in accordance with the procedures in this specification.

  - FINAL VISUAL INSPECTIONS AND AIR CLEARANCE TESTING

    - General: Notify the VA Representative 24 hours in advance for the performance of the final visual inspection and testing. The final visual inspection and testing will be performed by the VPIH/CIH after the final cleaning.

    - Final Visual Inspection: Final visual inspection will include the entire regulated area, the PDF, all poly sheeting, seals over HVAC

openings, doorways, windows, and any other openings. If any debris, residue, dust or any other suspect material is detected, the final cleaning shall be repeated at no additional cost to the VA. Dust/material samples may be collected and analyzed at no additional cost to the VA at the discretion of the VPIH/CIH to confirm visual findings. When the regulated area is visually clean the final testing can be done.

    - Final Air Clearance Testing:

      - After an acceptable final visual inspection by the VPIH/CIH and VA Representative, the VPIH/CIH will perform the final clearance testing. Air samples will be collected and analyzed in accordance with procedures for AHERA in this specification. If work is less than 260 lf/160 sf/35 cf, 5 PCM samples shall be collected for clearance and a minimum of two field blank. If work is equal to or more than 260 lf/160 sf/35 cf, AHERA TEM sampling shall be performed for clearance. TEM analysis shall be done in accordance with procedures for EPA AHERA presented in this specification. If the release criteria are not met, the Contractor shall repeat the final cleaning and continue decontamination procedures until clearance is achieved. All additional inspection and testing costs will be borne by the Contractor.

      - If release criteria are met, proceed to perform the abatement closeout and to issue the certificate of completion in accordance with these specifications.

    - Final Air Clearance Procedures:

      - Contractor's Release Criteria: Work in a regulated area is complete when the regulated area is visually clean and airborne fiber levels have been reduced to or below 0.01 f/cc as measured by the AHERA PCM protocol, and < 70 AHERA asbestos structures per square millimeter (s/mm2) by AHERA TEM. No averaging of results will be used for this project. All five (5) TEM samples inside the regulated area shall be at or below 70 asbestos s/mm2 to satisfy the project final clearance criteria.

      - Air Monitoring and Final Clearance Sampling: To determine if the elevated airborne fiber counts encountered during abatement operations have been reduced to the specified level, the VPIH/CIH

will secure samples and analyze them according to the following procedures:

        - Fibers Counted: “Fibers” referred to in this section shall be either all fibers regardless of composition as counted in the NIOSH 7400 PCM method or asbestos fibers counted using the AHERA TEM method.

        - Aggressive Sampling: All final air testing samples shall be collected using aggressive sampling techniques except where soil is not encapsulated or enclosed. Samples will be collected on 0.8 MCE filters for PCM analysis and 0.45 MCE for TEM. A minimum of 3850 Liters of air using calibrated sampling pumps shall be collected for PCM samples and a minimum of 1200 Liters of air using calibrated sampling pumps shall be collected for TEM clearance samples. Before pumps are started, initiate aggressive air mixing sampling as detailed in 40 CFR 763 Subpart E (AHERA) Appendix A (III)(B)(7)(d). Air samples will be collected in areas subject to normal air circulation away from corners, obstructed locations, and locations near windows, doors, or vents. After air sampling pumps have been shut off, circulating fans shall be shut off. The negative pressure system shall continue to operate.

    - Clearance Sampling Using PCM:

      - The VPIH/CIH will perform clearance samples as indicated by the specification.

      - The NIOSH 7400 PCM method will be used for clearance sampling with a minimum collection volume of 3850 Liters of air. A minimum of 5 PCM clearance samples shall be collected. All samples must be equal to or less than 0.01 f/cc to clear the regulated area.

    - Clearance Sampling Using TEM:

      - Clearance requires 13 samples be collected; 5 inside the regulated area; 5 outside the regulated area; and 3 field blanks.

      - The TEM method will be used for clearance sampling with a minimum collection volume of 1200 Liters of air. A minimum of 13 clearance samples shall be collected. All samples must be equal to or less than 70 AHERA structures per square millimeter (s/mm2) AHERA TEM, no averaging of results for this specific project.

    - Laboratory Testing of PCM Samples: The services of an AIHA accredited laboratory will be employed by the VA to perform analysis for the PCM air samples. The accredited laboratory shall be successfully participating in the AIHA Proficiency Analytical Testing (PAT) program. Samples will be sent daily by the VPIH/CIH so that verbal/faxed reports can be received within 24-36 hours. A complete record, certified by the laboratory, of all air monitoring tests and results will be furnished to the VA’s Representative and the Contractor.

    - Laboratory Testing of Tem Samples: Samples shall be sent by the VPIH/CIH to a NIST NVLAP accredited laboratory for analysis by TEM. The laboratory shall be successfully participating in the NIST NVLAP Airborne Asbestos Analysis (TEM) program. Verbal/faxed results from the laboratory shall be available within 24-36 hours after receipt of the samples. A complete record, certified by the laboratory, of all TEM results shall be furnished to the VA's Representative and the Contractor.

  - ABATEMENT CLOSEOUT AND CERTIFICATE OF COMPLIANCE

    - Completion of Abatement Work: After thorough decontamination, seal negative air machines with 2-layers of 6-mil poly and duct tape to form a tight seal at the intake/outlet ends before removal from the regulated area. Complete asbestos abatement work upon meeting the regulated area visual and air clearance criteria and fulfilling the following:

      - Remove all equipment, materials, and debris from the project area.

      - Package and dispose of all asbestos waste as required. Dispose of waste ACM and debris which is packaged in accordance with these specifications, OSHA, EPA and DOT. The landfill requirements for packaging must also be met. Transport will be in compliance with 49 CFR 171 – 180 regulations.

      - Repair or replace all interior finishes damaged during the abatement work.

      - The VA will be notified of any waste removed from the containment prior to 24 hours.

      - Fulfill other project closeout requirements as specified elsewhere in this specification.

    - Certificate of Completion by Contractor: The CPIH/CIH shall complete and sign the "Certificate of Completion" in accordance with Attachment

1 at the completion of the abatement and decontamination of the regulated area.

    - Work Shifts: All work shall generally be done during administrative hours (8:00 AM to 4:30 PM) Monday - Friday excluding Federal Holidays. Any change in the work schedule must be approved in writing by the VA Representative.

    - Re-Insulation: If required as part of the contract, replace all asbestos containing insulation with suitable non-asbestos material. Provide SDS for all replacement materials. Refer to Section 23 07 11, HVAC, PLUMBING, AND BOILER PLANT INSULATION.

ATTACHMENT #1

CERTIFICATE OF COMPLETION

DATE: 		 VA Project #:	 PROJECT NAME:	 Abatement Contractor:	 VAMC/ADDRESS:

- I certify that I have personally inspected, monitored and supervised the abatement work of (specify regulated area or Building):

which took place from	/	/	to	/	/

- That throughout the work all applicable requirements/regulations and the VA's specifications were met.

- That any person who entered the regulated area was protected with the appropriate personal protective equipment and respirator and that they followed the proper entry and exit procedures and the proper operating procedures for the duration of the work.

- That all employees of the Abatement Contractor engaged in this work were trained in respiratory protection, were experienced with abatement work, had proper medical surveillance documentation, were fit-tested for their respirator, and were not exposed at any time during the work to asbestos without the benefit of appropriate respiratory protection.

- That I performed and supervised all inspection and testing specified and required by applicable regulations and VA specifications.

- That the conditions inside the regulated area were always maintained in a safe and healthy condition and the maximum fiber count never exceeded 0.5 f/cc, except as described below.

- That all abatement work was done in accordance with OSHA requirements and the manufacturer’s recommendations.

CPIH/CIH Signature/Date:

CPIH/CIH Print Name:

Abatement Contractor Signature/Date:

Abatement Contractor Print Name:

ATTACHMENT #2

CERTIFICATE OF WORKER'S ACKNOWLEDGMENT

PROJECT NAME:	DATE:	 PROJECT ADDRESS:		 ABATEMENT CONTRACTOR'S NAME:

WORKING WITH ASBESTOS CAN BE HAZARDOUS TO YOUR HEALTH. INHALING ASBESTOS HAS BEEN LINKED WITH VARIOUS TYPES OF CANCERS. IF YOU SMOKE AND INHALE ASBESTOS FIBERS, YOUR CHANCES OF DEVELOPING LUNG CANCER IS GREATER THAN THAT OF THE NON-SMOKING PUBLIC.

Your employer's contract with the owner for the above project requires that: You must be supplied with the proper personal protective equipment including an adequate respirator and be trained in its use. You must be trained in safe and healthy work practices and in the use of the equipment found at an asbestos abatement project. You must receive/have a current medical examination for working with asbestos. These things shall be provided at no cost to you. By signing this certificate of worker’s acknowledgement you are indicating to the owner that your employer has met these obligations.

RESPIRATORY PROTECTION: I have been trained in the proper use of respirators and have been informed of the type of respirator to be used on the above indicated project. I have a copy of the written Respiratory Protection Program issued by my employer. I have been provided for my exclusive use, at no cost, with a respirator to be used on the above indicated project.

TRAINING COURSE: I have been trained by a third party, State/EPA accredited trainer in the requirements for an AHERA/OSHA Asbestos Abatement Worker training course, 32-hours minimum duration. I currently have a valid State accreditation certificate. The topics covered in the course include, as a minimum, the following:

Physical Characteristics and Background Information on Asbestos Potential Health Effects Related to Exposure to Asbestos Employee Personal Protective Equipment

Establishment of a Respiratory Protection Program State of the Art Work Practices

Personal Hygiene Additional Safety Hazards Medical Monitoring

Air Monitoring

Relevant Federal, State and Local Regulatory Requirements, Procedures, and Standards

Asbestos Waste Disposal

MEDICAL EXAMINATION: I have had a medical examination within the past 12 months which was paid for by my employer. This examination included: health history, occupational history, pulmonary function test, and may have included a chest x-ray evaluation. The physician issued a positive written opinion after the examination.

Signature:

Printed Name:	 Social Security Number:	 Witness:

ATTACHMENT #3

AFFIDAVIT OF MEDICAL SURVEILLANCE, RESPIRATORY PROTECTION AND TRAINING/ACCREDITATION

VA PROJECT NAME AND NUMBER:	 VA MEDICAL FACILITY:	 ABATEMENT CONTRACTOR'S NAME AND ADDRESS:

- I verify that the following individual

Name:	 Social Security Number:	 who is proposed to be employed in asbestos abatement work associated with the above project by the named Abatement Contractor, is included in a medical surveillance program in accordance with 29 CFR 1926.1101(m), and that complete records of the medical surveillance program as required by

29 CFR 1926.1101(m)(n) and 29 CFR 1910.20 are kept at the offices of the Abatement Contractor at the following address.

Address:

- I verify that this individual has been trained, fit-tested and instructed in the use of all appropriate respiratory protection systems and that the person is capable of working in safe and healthy manner as expected and required in the expected work environment of this project.

- I verify that this individual has been trained as required by 29 CFR 1926.1101(k). This individual has also obtained a valid State accreditation certificate. Documentation will be kept on-site.

- I verify that I meet the minimum qualifications criteria of the VA specifications for a CPIH.

Signature of CPIH/CIH:	 Date:

Printed Name of CPIH/CIH:

Signature of Contractor:	 Date:

Printed Name of Contractor:

ATTACHMENT #4

ABATEMENT CONTRACTOR/COMPETENT PERSON(S) REVIEW AND ACCEPTANCE OF THE VA’S ASBESTOS SPECIFICATIONS

VA Project Location:		 VA Project #:	 VA Project Description:

This form shall be signed by the Asbestos Abatement Contractor Owner and the Asbestos Abatement Contractor’s Competent Person(s) prior to any start of work at the VA related to this Specification. If the Asbestos Abatement Contractor’s/Competent Person(s) has not signed this form, they shall not be allowed to work on-site.

I, the undersigned, have read VA’s Asbestos Specification regarding the asbestos abatement requirements. I understand the requirements of the VA’s Asbestos Specification and agree to follow these requirements as well as all required rules and regulations of OSHA/EPA/DOT and State/Local requirements. I have been given ample opportunity to read the VA’s Asbestos Specification and have been given an opportunity to ask any questions regarding the content and have received a response related to those questions. I do not have any further questions regarding the content, intent and requirements of the VA’s Asbestos Specification.

At the conclusion of the asbestos abatement, I will certify that all asbestos abatement work was done in accordance with the VA’s Asbestos Specification and all ACM was removed properly and no fibrous residue remains on any abated surfaces.

Abatement Contractor Owner’s Signature	Date

- - - END - - -

PART 1 - GENERAL

  - DESCRIPTION

SECTION 07 84 00 FIRESTOPPING

    - Tested and listed firestopping systems, combination of materials, or devices to form an effective barrier against the spread of flame, smoke and gases, and maintain the integrity of fire resistance rated walls, partitions, floors, and ceiling-floor assemblies, including through- penetrations and construction joints and gaps.

      - Through-penetrations include the annular space around pipes, tubes, conduit, wires, cables and vents.

      - Construction joints include those used to accommodate expansion, contraction, wind, or seismic movement; firestopping material cannot interfere with the required movement of the joint.

      - Gaps requiring firestopping include gaps between the top of the fire-rated walls and the roof or floor deck above and at the

intersection of shaft assemblies and adjoining fire resistance rated assemblies.

    - Closure of openings in walls against penetration of gases or smoke in smoke partitions.

  - RELATED WORK

B. Spray applied fireproofing: Section 07 81 00, APPLIED FIREPROOFING

C. Sealants and application: Section 07 92 00, JOINT SEALANTS.

  - SUBMITTALS

    - Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

    - Submit manufacturer's descriptive data, typical details conforming to UL Fire Resistance or other details certified by another nationally recognized testing laboratory, installation instructions or UL listing details for a firestopping assembly instead of fire-test data or report. For those firestop applications for which no UL tested system is available through a manufacturer, submit a manufacturer's engineering judgment, derived from similar UL system designs or other tests, for review and approval prior to installation. Submittal must indicate the firestopping material to be provided for each type of application; when more than a total of 5 penetrations and/or

construction joints are to receive firestopping, provide drawings that indicate location, "F", "T" and "L" ratings, and type of application.

    - Submit certificates attesting that firestopping material complies with the specified requirements. For all intumescent firestop materials used in through penetration systems, manufacturer must provide certification from UL of passing the "Aging and Environmental Exposure Testing" portion of UL 1479.

    - Submit manufacturer's representative certification stating that firestopping work has been inspected and found to be applied according to the manufacturer's recommendations and the specified requirements. Manufacturer’s representative must be a direct employee of the manufacturer (not a distributor or an agent) and be qualified to perform the specified inspections and certify the firestopping installation.

  - DELIVERY AND STORAGE

    - Deliver materials in their original unopened containers with manufacturer’s name and product identification.

    - Store in a location providing protection from damage and exposure to the elements.

  - WARRANTY

    - Firestopping work subject to the terms of the Article “Warranty of Construction”, FAR clause 52.246-21, except extend the warranty period to five years.

  - QUALITY ASSURANCE

    - FM, UL, or WH or other approved laboratory tested products will be acceptable.

  - APPLICABLE PUBLICATIONS

    - Publications listed below form a part of this specification to extent referenced. Publications are referenced in text by the basic designation only. Comply with applicable provisions and recommendations of the following, except as otherwise shown or specified.

    - American Society for Testing and Materials (ASTM):

E84-22	Surface Burning Characteristics of Building Materials

E814-13a(2017)	Fire Tests of Penetration Firestop Systems E2174-20a	On-Site Inspection of Installed Fire Stops

E2393-20a	On-Site Inspection of Installed Fire Resistive Joint Systems and Perimeter Fire Barriers

    - FM Global (FM):

Annual Issue	Approval Guide Building Materials

    - Underwriters Laboratories, Inc. (UL):

Annual Issue	Building Materials Directory

Annual Issue	Fire Resistance Directory

1479	Fire Tests of Through-Penetration Firestops

    - Warnock Hersey (WH):

Annual Issue	Certification Listings

  - SEQUENCING

    - Coordinate the specified work with other trades.

    - Apply firestopping materials, at penetrations of pipes and ducts, prior to insulating, unless insulation meets requirements specified for firestopping.

    - Apply firestopping materials at building joints and construction gaps, prior to completion of enclosing walls or assemblies.

    - Locate and install cast-in-place firestop devices in place before concrete placement. Install pipe, conduit or cable bundles through cast-in-place device after concrete placement but before area is concealed or made inaccessible.

    - Inspect and receive approval for firestop material prior to final completion and enclosing of any assemblies that may conceal installed firestop.

PART 2 - PRODUCTS

  - FIRESTOP SYSTEMS

    - Use factory built (Firestop Devices) or field erected (through- Penetration Firestop Systems) to form a specific building system maintaining required integrity of the fire barrier and stop the passage of gases or smoke.

    - Through-penetration firestop systems and firestop devices tested in accordance with ASTM E814 or UL 1479 using the "F" or "T" rating must maintain the same rating and integrity as the fire barrier being sealed. "T" ratings are not required for penetrations smaller than or equal to 100 mm (4 in) nominal pipe or 0.01 m2 (16 sq. in.) in overall cross-sectional area.

    - Products requiring heat activation that seal an opening by its intumescence must exhibit a demonstrated ability to function as designed to maintain the fire barrier.

    - Provide firestop sealants used for firestopping or smoke sealing with the following properties:

      - Contain no flammable or toxic solvents.

      - Have no dangerous or flammable out gassing during the drying or curing of products.

      - Water-resistant after drying or curing and unaffected by high humidity, condensation or transient water exposure.

      - When used in exposed areas, firestop sealant can be sanded and finished with similar surface treatments as used on the surrounding wall or floor surface.

    - Provide firestopping system or devices used for penetrations by glass pipe, plastic pipe or conduits, unenclosed cables, or other non- metallic materials with following properties:

      - Classified for use with the particular type of penetrating material used.

      - Penetrations containing loose electrical cables, computer data cables, and communications cables protected using firestopping systems that allow unrestricted cable changes without damage to the seal.

      - Intumescent products which would expand to seal the opening and act as fire, smoke, toxic fumes, and water sealant.

    - Provide products with maximum flame spread of 25 and smoke development of 50 when tested in accordance with ASTM E84.

    - Provide products FM, UL, or WH rated or tested by an approved laboratory in accordance with ASTM E814.

    - Materials must be asbestos free.

  - SMOKE STOPPING IN SMOKE PARTITIONS

    - Use silicone sealant in smoke partitions as specified in Section 07 92 00, JOINT SEALANTS.

    - Use mineral fiber filler and bond breaker behind sealant.

    - Sealants must have a maximum flame spread of 25 and smoke developed of

50 when tested in accordance with E84.

    - When used in exposed areas capable of being sanded and finished with similar surface treatments as used on the surrounding wall or floor surface.

PART 3 - EXECUTION

  - EXAMINATION

    - Submit product data and installation instructions, as required by article, submittals, after an on-site examination of areas to receive firestopping.

  - PREPARATION

    - Remove dirt, grease, oil, loose materials, or other substances that prevent adherence and bonding or application of the firestopping or smoke stopping materials.

    - Remove insulation on insulated pipe for a distance of 150 mm (6 inches) on either side of the fire rated assembly prior to applying the firestopping materials unless the firestopping materials are tested and approved for use on insulated pipes.

  - INSTALLATION

    - Do not begin work until the specified material data and installation instructions of the proposed firestopping systems have been submitted and approved.

    - Install firestopping systems with smoke stopping in accordance with FM, UL, WH, or other approved system details and installation instructions.

    - Install smoke stopping seals in smoke partitions.

  - INSPECTIONS

    - Manufacturer’s technical representative to inspect all firestopping in accordance with ASTM standards for firestop inspection, and document inspection results; ASTM E2174 and E2393.

  - CLEAN-UP AND ACCEPTANCE OF WORK

    - As work on each floor is completed, remove materials, litter, and debris.

    - Do not move materials and equipment to the next-scheduled work area until completed work is inspected and accepted by the RE/COR; RE/COR inspection does not supersede requirement for inspection by manufacturer's representative or requirements of local jurisdiction.

    - Clean up spills of liquid type materials.

- - - E N D - - -

PART 1 - GENERAL

  - DESCRIPTION

SECTION 07 92 00 JOINT SEALANTS

    - Section covers all sealant and caulking materials and their application, wherever required for complete installation of building materials or systems.

  - RELATED WORK

    - Sealing of site work concrete paving: Section 32 05 23, CEMENT AND CONCRETE FOR EXTERIOR IMPROVEMENTS.

EB.	Firestopping penetrations: Section 07 84 00, FIRESTOPPING.

  - QUALITY CONTROL

    - Installer Qualifications: An experienced installer who has specialized in installing joint sealants similar in material, design, and extent to those indicated for this Project and whose work has resulted in joint- sealant installations with a record of successful in-service performance.

    - Source Limitations: Obtain each type of joint sealant through one source from a single manufacturer.

.

- Test other joint sealants for compliance with requirements indicated by referencing standard specifications and test methods.

    - Preconstruction Field-Adhesion Testing: Before installing elastomeric sealants, field test their adhesion to joint substrates in accordance with sealant manufacturer’s recommendations:

      - Locate test joints where indicated or, if not indicated, as directed by Contracting Officer.

      - Conduct field tests for each application indicated below:

        - Each type of elastomeric sealant and joint substrate indicated.

        - Each type of non-elastomeric sealant and joint substrate indicated.

      - Notify COR seven days in advance of dates and times when test joints will be erected.

      - Arrange for tests to take place with joint sealant manufacturer’s technical representative present. Provide written acceptance from manufacturer’s technical representative that materials pass for adhesion and compatibility.

    - Meet VOC requirements of pertinent CARB and/or SCAQMD Rule for sealants VOC (4 percent by weight VOC or less in less than 16-ounce package or less than 250 g/L in larger package). All non-porous sealant primers must be below 250g/L and primers for porous substrates less than 775 g/L.

  - SUBMITTALS

    - Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

    - Manufacturer's installation instructions for each product used.

    - Cured samples of exposed sealants for each color where required to match adjacent material.

    - Manufacturer's Literature and Data:

      - Caulking compound.

      - Primers.

      - Sealing compound, each type, including compatibility when different sealants are in contact with each other.

    - Preconstruction Laboratory Test Reports: From sealant manufacturer, indicating the following:

      - Materials forming joint substrates and joint-sealant backings have been tested for compatibility and adhesion with joint sealants.

      - Interpretation of test results and written recommendations for primers and substrate preparation are needed for adhesion.

  - PRE-INSTALLATION CONFERENCE

    - Convene a meeting on site, after submittals are received and approved but before any work, to review drawings and specifications, submittals, schedule, manufacturer instructions, site logistics and pertinent matters of coordination, temporary protection, governing regulations, tests and inspections; participants to include RE/COR and all parties whose work is effected or related to the work of this section.

  - PROJECT CONDITIONS

    - Environmental Limitations:

      - Do not proceed with installation of joint sealants under following conditions:

        - When ambient and substrate temperature conditions are outside limits permitted by joint sealant manufacturer or are below 4.4 °C (40 °F).

        - When joint substrates are wet.

    - Joint-Width Conditions: Do not proceed with installation of joint sealants where joint widths are less than those allowed by joint sealant manufacturer for applications indicated.

    - Joint-Substrate Conditions: Do not proceed with installation of joint sealants until contaminants capable of interfering with adhesion are removed from joint substrates.

  - DELIVERY, HANDLING, AND STORAGE

    - Deliver materials in manufacturers' original unopened containers, with brand names, date of manufacture, shelf life, and material designation clearly marked thereon.

    - Carefully handle and store to prevent inclusion of foreign materials.

    - Do not subject to sustained temperatures less than 5° C (40° F) or exceeding 32° C (90° F).

  - DEFINITIONS

    - Definitions of terms in accordance with ASTM C717 and as specified.

    - Back-up Rod: A type of sealant backing.

    - Bond Breakers: A type of sealant backing.

    - Filler: A sealant backing used behind a back-up rod.

  - WARRANTY

    - Warranty exterior sealing against leaks, adhesion, and cohesive failure, and subject to terms of "Warranty of Construction", FAR clause 52.246-21, except that warranty period to be extended to five (5) years.

    - General Warranty: Special warranty specified in this Article will not deprive Government of other rights Government may have under other provisions of Contract Documents and are in addition to, and run concurrent with, other warranties made by Contractor under requirements of Contract Documents.

  - APPLICABLE PUBLICATIONS

    - Publications listed below form a part of this specification to extent referenced. Publications are referenced in text by the basic designation only. Comply with applicable provisions and recommendations of the following, except as otherwise shown or specified.

    - American Society for Testing and Materials (ASTM):

C612-14(2019)	Mineral Fiber Block and Board Thermal

Insulation

C717-19	Standard Terminology of Building Seals and Sealants

C734-15(2019)	Low Temperature Flexibility of Latex Sealants

after Artificial Weathering

C834-17	Latex Sealants

C919-22	Use of Sealants in Acoustical Applications

C920-18	Elastomeric Joint Sealants

C1021-08(2019)	Laboratories Engaged in Testing of Building

Sealants

C1193-16	Use of Joint Sealants

C1248-22	Staining of Porous Substrate by Joint Sealants

C1330-18	Cylindrical Sealant Backing for Use with Cold Liquid-Applied Sealants

D217-21a	Cone Penetration of Lubricating Grease

D1056-20	Flexible Cellular Materials—Sponge or Expanded Rubber

E84-22	Surface Burning Characteristics of Building Materials

    - California Air Resources Board (CARB)

    - South Coast Air Quality Management District (SCAQMD)

    - Sealant, Waterproofing and Restoration Institute (SWRI): The Professionals’ Guide

PART 2 - PRODUCTS

2.1 CAULKING COMPOUND

- C-1: ASTM C834, acrylic latex.

- C-2: Polymer-based acoustical sealant conforming to ASTM C919 must have a flame spread of 25 or less and a smoke developed rating of 50 or less

when tested in accordance with ASTM E84. Acoustical sealant must have a consistency of 250 to 310 when tested in accordance with ASTM D217 and must remain flexible and adhesive after 500 hours of accelerated weathering as specified in ASTM C734 and must be non-staining.

  - JOINT SEALANT BACKING

    - General: Provide sealant backings of material and type that are non- staining; are compatible with joint substrates, sealants, primers, and other joint fillers; and are approved for applications indicated by sealant manufacturer based on field experience and laboratory testing.

    - Cylindrical Sealant Backings: ASTM C1330, of type indicated below and of size and density to control sealant depth and otherwise contribute to producing optimum sealant performance:

      - Type C: Closed-cell material with a surface skin.

    - Elastomeric Tubing Sealant Backings: Neoprene, butyl, EPDM, or silicone tubing complying with ASTM D1056, nonabsorbent to water and gas, and capable of remaining resilient at temperatures down to minus 32° C (minus 26° F). Provide products with low compression set and of size and shape to provide a secondary seal, to control sealant depth, and otherwise contribute to optimum sealant performance.

    - Bond-Breaker Tape: Polyethylene tape or other plastic tape recommended by sealant manufacturer for preventing sealant from adhering to rigid, inflexible joint-filler materials or joint surfaces at back of joint where such adhesion would result in sealant failure. Provide self- adhesive tape where applicable.

  - FILLER

    - Mineral fiber board: ASTM C612, Type IVA.

    - Thickness same as joint width.

    - Depth to fill void completely behind back-up rod.

  - PRIMER

    - As recommended by manufacturer of caulking or sealant material.

    - Stain free type.

  - CLEANERS-NON POUROUS SURFACES

    - Chemical cleaners acceptable to manufacturer of sealants and sealant backing material, free of oily residues and other substances capable of staining or harming joint substrates and adjacent non-porous surfaces and formulated to promote adhesion of sealant and substrates.

PART 3 - EXECUTION

  - INSPECTION

    - Inspect substrate surface for bond breaker contamination and unsound materials at adherent faces of sealant.

    - Coordinate for repair and resolution of unsound substrate materials.

    - Inspect for uniform joint widths and that dimensions are within tolerance established by sealant manufacturer.

  - PREPARATIONS

    - Prepare joints in accordance with manufacturer's instructions and as specified only when installers are ready to initiate sealant application as soon as practicable after preparation and before subsequent surface deterioration.

    - Clean surfaces of joint to receive caulking or sealants leaving joint dry to the touch, free from frost, moisture, grease, oil, wax, lacquer paint, or other foreign matter that would tend to destroy or impair adhesion.

      - Clean, porous joint substrate surfaces by brushing, grinding, blast cleaning, mechanical abrading, or a combination of these methods to produce a clean, sound substrate capable of developing optimum bond with joint sealants.

      - Remove loose particles remaining from above cleaning operations by vacuuming or blowing out joints with oil-free compressed air. Porous joint surfaces include the following:

- Concrete.

- Masonry.

- Unglazed surfaces of ceramic tile.

      - Remove laitance and form-release agents from concrete.

      - Clean nonporous surfaces with chemical cleaners or other means that do not stain, harm substrates, or leave residues capable of interfering with adhesion of joint sealants.

- Metal.

- Glass.

- Porcelain enamel.

- Glazed surfaces of ceramic tile.

    - Do not cut or damage joint edges.

    - Apply masking tape to face of surfaces adjacent to joints before applying primers, caulking, or sealing compounds.

      - Do not leave gaps between ends of sealant backings.

      - Do not stretch, twist, puncture, or tear sealant backings.

      - Remove absorbent sealant backings that have become wet before sealant application and replace them with dry materials.

    - Apply primer to sides of joints wherever required by compound manufacturer's printed instructions.

      - Apply primer prior to installation of back-up rod or bond breaker tape.

      - Use brush or other approved means that will reach all parts of joints.

    - Take all necessary steps to prevent three-sided adhesion of sealants.

  - BACKING INSTALLATION

    - Install back-up material, to form joints enclosed on three sides as required for specified depth of sealant.

    - Where deep joints occur, install filler to fill space behind the back- up rod and position the rod at proper depth.

    - Cut fillers installed by others to proper depth for installation of back-up rod and sealants.

    - Install back-up rod, without puncturing the material, to a uniform depth, within plus or minus 3 mm (1/8 inch) for sealant depths specified.

    - Where space for back-up rod does not exist, install bond breaker tape strip at bottom (or back) of joint so sealant bonds only to two opposing surfaces.

    - Take all necessary steps to prevent three-sided adhesion of sealants.

  - SEALANT DEPTHS AND GEOMETRY

    - At widths up to 6 mm (1/4 inch), sealant depth equal to width.

    - At widths over 6 mm (1/4 inch), sealant depth 1/2 of width up to 13 mm (1/2 inch) maximum depth at center of joint with sealant thickness at center of joint approximately 1/2 of depth at adhesion surface.

  - INSTALLATION

    - General:

- Comply with manufacturer’s written installation instructions for products and applications indicated.

    - For application of sealants, follow requirements of ASTM C1193 unless specified otherwise.

    - Where gypsum board partitions are of sound rated, fire rated, or smoke barrier construction, follow requirements of ASTM C919 only to seal all cut-outs and intersections with the adjoining construction unless specified otherwise.

      - Coordinate with application of gypsum board to install sealant immediately prior to application of gypsum board.

      - Openings: Apply a 6 mm (1/4 inch) bead of sealant around all cut- outs to seal openings of electrical boxes, ducts, pipes and similar penetrations. To seal electrical boxes, seal sides and backs.

  - CLEANING

    - Fresh compound accidentally smeared on adjoining surfaces: Scrape off immediately and rub clean with a solvent as recommended by the caulking or sealant manufacturer.

    - After filling and finishing joints, remove masking tape.

    - Leave adjacent surfaces in a clean and unstained condition.

  - PROTECTION

    - Protect joint sealants during and after curing period from contact with contaminating substances and from damage resulting from construction operations or other causes so sealants are without deterioration or damage at time of completion. If, despite such protection, damage or deterioration occurs, cut out and remove damaged or deteriorated joint sealants immediately so installations with repaired areas are indistinguishable from original work.

  - LOCATIONS

    - Interior Caulking:

3. Joints at Masonry Walls and Columns, Piers, Concrete Walls or Exterior Walls: Types C-1, C-2 and C-3.

- - - E N D - - -

PART 1 - GENERAL

  - DESCRIPTION

SECTION 09 91 00 PAINTING

    - Work of this Section includes all labor, materials, equipment, and services necessary to complete the painting and finishing as shown on the construction documents andor specified herein, including, but not limited to, the following:

- Prime coats which may be applied in shop under other sections.

- Prime painting unprimed surfaces to be painted under this Section.

- Painting items furnished with a prime coat of paint, including touching up of or repairing of abraded, damaged or rusted prime coats applied by others.

- Painting ferrous metal (except stainless steel) exposed to view.

- Painting galvanized ferrous metals exposed to view.

- Painting interior concrete block exposed to view.

- Painting gypsum drywall exposed to view.

- Painting of wood exposed to view, except items which are specified to be painted or finished under other Sections of these specifications. Back painting of all wood in contact with concrete, masonry or other moisture areas.

- Painting pipes, pipe coverings, conduit, ducts, insulation, hangers, supports and other mechanical and electrical items and equipment exposed to view.

- Painting surfaces above, behind or below grilles, gratings, diffusers, louvers lighting fixtures, and the like, which are exposed to view through these items.

- Painting includes shellacs, stains, varnishes, coatings specified, and striping or markers and identity markings.

- Incidental painting and touching up as required to produce proper finish for painted surfaces, including touching up of factory finished items.

- Painting of any surface not specifically mentioned to be painted herein or on construction documents, but for which painting is obviously necessary to complete the job, or work which comes within the intent of these specifications, is to be included as though specified.

  - RELATED WORK

    - Section 01 35 26, SAFETY REQUIREMENTS: Activity Hazard Analysis.

    - Section 01 81 13, SUSTAINABLE CONSTUCTION REQUIREMENTS: Sustainable

Design Requirements.

    - Section 02 83 33.13, LEAD-BASED PAINT REMOVAL AND DISPOSAL: Lead Paint

Removal.

    - Section 04 05 13, MASONRY MORTARING: Masonry Repairs.

    - Section 04 05 16, MASONRY GROUTING: Masonry Repairs.

    - Division 05 METALS: Shop prime painting of steel and ferrous metals.

    - Division 08 OPENINGS: Shop prime painting of steel and ferrous metals.

    - Section 08 14 00, INTERIOR WOOD DOORS: Prefinished flush doors with transparent finishes.

    - Section 09 06 00, SCHEDULE FOR FINISHES: Type of Finish, Color, and Gloss Level of Finish Coat.

    - Section 09 94 19, MULTICOLOR INTERIOR FINISHING: Multi-color Textured Wall Finish.

    - Section 09 96 59, RESINOUS SPECIALTY GLAZED COATING SYSTEMS FOR WALLS, CEILINGS, WALLBOARD, AND BLOCK CMU (RES-W1, RES-W2): Glazed wall surfacing

or tile like coatings.

    - Section 09 96 59, RESINOUS SPECIALTY GLAZED COATING SYSTEMS FOR WALLS, CEILINGS, WALLBOARD, AND BLOCK CMU (RES-W1, RES-W2): Glazed wall surfacing

or tile like coatings.

    - Division 10 SPECIALTIES: Shop prime painting of steel and ferrous metals.

    - Division 11 EQUIPMENT: Shop prime painting of steel and ferrous metals.

    - Division 12 FURNISHINGS: Shop prime painting of steel and ferrous metals.

    - Division 13 SPECIAL CONSTRUCTION: Shop prime painting of steel and ferrous metals.

    - Division 14 CONVEYING EQUIPMENT: Shop prime painting of steel and ferrous metals.

    - Division 21 FIRE SUPPRESSION: Shop prime painting of steel and ferrous metals.

    - Division 22 PLUMBING: Shop prime painting of steel and ferrous metals.

    - Division 23 HEATING; VENTILATION AND AIR-CONDITIONING: Shop prime painting of steel and ferrous metals.

    - Division 26 ELECTRICAL: Shop prime painting of steel and ferrous metals.

    - Division 27 COMMUNICATIONS: Shop prime painting of steel and ferrous metals.

    - Division 28 ELECTRONIC SAFETY AND SECURITY: Shop prime painting of steel and ferrous metals.

    - Division 32 EXTERIOR IMPROVEMENTS: Shop prime painting of steel and ferrous metals.

    - Section 32 17 23, PAVEMENT MARKINGS: Asphalt and concrete pavement marking.

  - SUBMITTALS

    - Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

    - Painter qualifications.

    - Manufacturer's Literature and Data:

1. Before work is started, or sample panels are prepared, submit manufacturer's literature and technical data, the current Master Painters Institute (MPI) "Approved Product List" indicating brand label, product name and product code as of the date of contract award, will be used to determine compliance with the submittal requirements of this specification. The Contractor may choose to use subsequent MPI "Approved Product List", however, only one (1) list may be used for the entire contract and each coating system is to be from a single manufacturer. All coats on a particular substrate must be from a single manufacturer. No variation from the MPI "Approved Product List" where applicable is acceptable.

    - Sample Panels:

- After painters' materials have been approved and before work is started, submit sample panels showing each type of finish and color specified.

- Panels to Show Color: Composition board, 100 x 250 mm (4 x 10 inch).

- Panel to Show Transparent Finishes: Wood of same species and grain pattern as wood approved for use, 100 x 250 mm (4 x 10 inch face) minimum, and where both flat and edge grain will be exposed, 250 mm

(10 inches) long by sufficient size, 50 x 50 mm (2 x 2 inch) minimum or actual wood member to show complete finish.

- Attach labels to panel stating the following:

  - Federal Specification Number or manufacturers name and product number of paints used.

  - Specification code number specified in Section 09 06 00, SCHEDULE FOR FINISHES.

  - Product type and color.

  - Name of project.

- Strips showing not less than 50 mm (2 inch) wide strips of undercoats and 100 mm (4 inch) wide strip of finish coat.

    - Manufacturers' Certificates indicating compliance with specified requirements:

- Manufacturer's paint substituted for Federal Specification paints meets or exceeds performance of paint specified.

- High temperature aluminum paint.

- Epoxy coating.

- Intumescent clear coating or fire-retardant paint.

- Plastic floor coating.

  - DELIVERY AND STORAGE

    - Deliver materials to site in manufacturer's sealed container marked to show following:

- Name of manufacturer.

- Product type.

- Batch number.

- Instructions for use.

- Safety precautions.

    - In addition to manufacturer's label, provide a label legibly printed as following:

- Federal Specification Number, where applicable, and name of material.

- Surface upon which material is to be applied.

- Specify Coat Types: Prime; body; finish; etc.

    - Maintain space for storage, and handling of painting materials and equipment in a ventilated, neat and orderly condition to prevent spontaneous combustion from occurring or igniting adjacent items.

    - Store materials at site at least 24 hours before using, at a temperature between 7 and 30 degrees C (45 and 85 degrees F).

  - QUALITY ASSURANCE

    - Qualification of Painters: Use only qualified journeyman painters for the mixing and application of paint on exposed surfaces. Submit evidence that key personnel have successfully performed surface preparation and application of coating on a minimum of three (3) similar projects within the past three (3) years.

    - Paint Coordination: Provide finish coats which are compatible with the prime paints used. Review other Sections of these specifications in which prime paints are to be provided to ensure compatibility of the total coatings system for the various substrates. Upon request from other subcontractors, furnish information on the characteristics of the finish materials proposed to be used, to ensure that compatible prime coats are used. Provide barrier coats over incompatible primers or remove and re- prime as required. Notify the Contracting Officer Representative (COR) in writing of any anticipated problems using the coating systems as specified with substrates primed by others.

  - REGULATORY REQUIREMENTS

    - Paint materials are to conform to the restrictions of the local Environmental and Toxic Control jurisdiction.

- Volatile Organic Compounds (VOC) Emissions Requirements: Field-applied paints and coatings that are inside the waterproofing system to not exceed limits of authorities having jurisdiction.

- Lead-Base Paint:

  - Comply with Section 410 of the Lead-Based Paint Poisoning Prevention Act, as amended, and with implementing regulations promulgated by Secretary of Housing and Urban Development.

  - Regulations concerning prohibition against use of lead-based paint in federal and federally assisted construction, or rehabilitation of residential structures are set forth in Subpart F, Title 24, Code of Federal Regulations, Department of Housing and Urban Development.

  - Do not use coatings having a lead content over 0.06 percent by weight of non-volatile content.

  - For lead-paint removal, see Section 02 83 33.13, LEAD-BASED PAINT REMOVAL AND DISPOSAL.

- Asbestos: Provide materials that do not contain asbestos.

- Chromate, Cadmium, Mercury, and Silica: Provide materials that do not contain zinc-chromate, strontium-chromate, Cadmium, mercury or mercury compounds or free crystalline silica.

- Human Carcinogens: Provide materials that do not contain any of the ACGIH-BKLT and ACGHI-DOC confirmed or suspected human carcinogens.

- Use high performance acrylic paints in place of alkyd paints.

  - SAFETY AND HEALTH

    - Apply paint materials using safety methods and equipment in accordance with the following:

1. Comply with applicable Federal, State, and local laws and regulations, and with the ACCIDENT PREVENTION PLAN, including the Activity Hazard Analysis (AHA) as specified in Section 01 35 26, SAFETY REQUIREMENTS. The AHA is to include analyses of the potential impact of painting operations on painting personnel and on others involved in and adjacent to the work zone.

    - Safety Methods Used During Paint Application: Comply with the requirements of SSPC PA Guide 10.

    - Toxic Materials: To protect personnel from overexposure to toxic materials, conform to the most stringent guidance of:

- The applicable manufacturer’s Material Safety Data Sheets (MSDS) or local regulation.

- 29 CFR 1910.1000.

- ACHIH-BKLT and ACGHI-DOC, threshold limit values.

  - APPLICABLE PUBLICATIONS

    - Publications listed below form a part of this specification to the extent referenced. Publications are referenced in the text by basic designation only.

    - American Conference of Governmental Industrial Hygienists (ACGIH): ACGIH TLV-BKLT-2012 ....Threshold Limit Values (TLV) for Chemical

Substances and Physical Agents and Biological Exposure Indices (BEIs)

ACGIH TLV-DOC-2012 .....Documentation of Threshold Limit Values and

Biological Exposure Indices, (Seventh Edition)

    - ASME International (ASME):

A13.1-07(R2013) ........Scheme for the Identification of Piping Systems

    - Code of Federal Regulation (CFR):

40 CFR 59 ..............Determination of Volatile Matter Content, Water

Content, Density Volume Solids, and Weight Solids of Surface Coating

    - Commercial Item Description (CID):

A-A-1272A ..............Plaster Gypsum (Spackling Compound)

    - Federal Specifications (Fed Spec):

TT-P-1411A .............Paint, Copolymer-Resin, Cementitious (For

Waterproofing Concrete and Masonry Walls) (CEP)

    - Master Painters Institute (MPI):

1 ......................Aluminum Paint

- ......................Primer, Alkali Resistant, Water Based

- ......................Interior Exterior Latex Block Filler

- ......................Exterior Alkyd Wood Primer

- ......................Exterior, Latex for Exterior Wood Primer

- ......................Exterior Oil Wood Primer

- ......................Exterior Alkyd, Flat MPI Gloss Level 1

- ......................Exterior Alkyd Enamel MPI Gloss Level 6

- .....................Exterior Latex, Flat

- .....................Exterior Latex, Semi-Gloss

15 .....................Exterior Latex, Low Sheen (MPI Gloss Level 3-4)

17 .....................Primer, Bonding, Waterbased

18 .....................Organic Zinc Rich Primer

22 .....................Aluminum Paint, High Heat (up to 590% - 1100F)

23 .....................Primer, Metal, Surface Tolerant

27 .....................Exterior Interior Alkyd Floor Enamel, Gloss

31 .....................Polyurethane, Moisture Cured, Clear Gloss

36 .....................Knot Sealer

39 .....................Primer, Latex, for Interior Wood

40 .....................Exterior, Latex High Build

- .....................Textured Coating, Latex, Flat

- .....................Interior Satin Latex, MPI Gloss Level 4

- .....................Interior Low Sheen Latex, MPI Gloss Level 2

- .....................Interior Primer Sealer

- .....................Interior Enamel Undercoat

- .....................Interior Alkyd, Semi-Gloss, MPI Gloss Level 5

- .....................Interior Alkyd, Gloss, MPI Gloss Level 6

- .....................Interior Latex Primer Sealer

- .....................Interior Alkyd, Eggshell, MPI Gloss Level 3

- .....................Interior Latex, MPI Gloss Level 3

- .....................Interior Latex, Flat, MPI Gloss Level 1

- .....................Interior Latex, Semi-Gloss, MPI Gloss Level 5

- .....................InteriorExterior Alkyd Porch & Floor Enamel, Low

Gloss

- .....................InteriorExterior Latex Porch & Floor Paint, Low

Gloss

66 .....................Interior Alkyd Fire Retardant, Clear Top-Coat (ULC

Approved)

67 .....................Interior Latex Fire Retardant, Top-Coat (ULC

Approved)

68 .....................Interior Exterior Latex Porch & Floor Paint, Gloss

71 .....................Polyurethane, Moisture Cured, Clear, Flat

77 .....................Epoxy Cold Cured, Gloss

79 .....................Marine Alkyd Metal Primer

90 .....................Interior Wood Stain, Semi-Transparent

91 .....................Wood Filler Paste

94 .....................Exterior Alkyd, Semi-Gloss

95 .....................Fast Drying Metal Primer

98 .....................High Build Epoxy Coating

99 .....................Sealer, Water-based, for Concrete Floors

101 ....................Epoxy Anti-Corrosive Metal Primer

107 ....................Primer, Rust-Inhibitive, Water-based

108 ....................High Build Epoxy Coating, Low Gloss

113 ....................Elastomeric, Pigmented, Exterior, Water-based,

Flat

114 ....................Interior Latex, Gloss

115 ....................Epoxy-Modified Latex, Interior Gloss (MPI gloss

level 6)

118 ....................Dry Fall, Latex Flat

119 ....................Exterior Latex, High Gloss (acrylic)

134 ....................Galvanized Water Based Primer

135 ....................Non-Cementitious Galvanized Primer

138 ....................Interior High Performance Latex, MPI Gloss Level 2

139 ....................Interior High Performance Latex, MPI Gloss Level 3

140 ....................Interior High Performance Latex, MPI Gloss Level 4

141 ....................Interior High Performance Latex (SG) MPI Gloss

Level 5

144 ....................Latex, Interior, Institutional Low Odor VOC, (MPI

Gloss Level 2)

145 ....................Latex, Interior, Institutional Low Odor VOC, (MPI

Gloss Level 3)

146 ....................Latex, Interior, Institutional Low Odor VOC, (MPI

Gloss Level 4)

151 ....................Light Industrial Coating, Interior, Water-based,

(MPI Gloss Level 3)

153 ....................Light Industrial Coating, Interior, Water-based,

(MPI Gloss Level 4)

163 ....................Exterior Water Based Semi-Gloss Light Industrial

Coating, MPI Gloss Level 5

164 ....................Exterior, Water Based, Gloss, Light Industrial

Coating, MPI Gloss Level 6

    - Society for Protective Coatings (SSPC): SSPC SP 1-82(R2004) ....Solvent Cleaning SSPC SP 2-82(R2004) ....Hand Tool Cleaning SSPC SP 3-28(R2004) ....Power Tool Cleaning

SSPC SP 10NACE No.2 ....Near-White Blast Cleaning

SSPC PA Guide 10 .......Guide to Safety and Health Requirements

    - Maple Flooring Manufacturer’s Association (MFMA):

    - U.S. National Archives and Records Administration (NARA):

29 CFR 1910.1000 .......Air Contaminants

    - Underwriter’s Laboratory (UL)

PART 2 - PRODUCTS

  - MATERIALS:

    - Conform to the coating specifications and standards referenced in PART 3. Submit manufacturer’s technical data sheets for specified coatings and solvents.

  - PAINT PROPERTIES:

    - Use ready-mixed (including colors), except two component epoxies, polyurethanes, polyesters, paints having metallic powders packaged separately and paints requiring specified additives.

    - Where no requirements are given in the referenced specifications for primers, use primers with pigment and vehicle, compatible with substrate and finish coats specified.

    - Provide undercoat paint produced by the same manufacturer as the finish coats. Use only thinners approved by the paint manufacturer and use only to recommended limits.

    - VOC Content: For field applications that are inside the weatherproofing system, paints and coating to comply with VOC content limits of authorities having jurisdiction and the following VOC content limits:

      - Flat Paints and Coatings: 50 gramliter.

      - Non-flat Paints and Coatings: 150 gramliter.

      - Dry-Fog Coatings: 400 gramliter.

      - Primers, Sealers, and Undercoaters: 200 gramliter.

      - Anticorrosive and Antirust Paints applied to Ferrous Metals: 250 gramliter.

      - Zinc-Rich Industrial Maintenance Primers: 340 gramliter.

      - Pretreatment Wash Primers: 420 gramliter.

      - Shellacs, Clear: 730 gramliter.

      - Shellacs, Pigmented: 550 gramliter.

    - VOC test method for paints and coatings is to be in accordance with

40 CFR 59 (EPA Method 24). Part 60, Appendix A with the exempt compounds’ content determined by Method 303 (Determination of Exempt Compounds) in the South Coast Air Quality Management District’s (SCAQMD) “Laboratory Methods of Analysis for Enforcement Samples” manual.

  - PLASTIC TAPE:

    - Pigmented vinyl plastic film in colors as specified in Section 09 06 00, SCHEDULE FOR FINISHES or specified.

    - Pressure sensitive adhesive back.

    - Snap on coil plastic markers.

    - Widths as shown on construction documents.

  - BIOBASED CONTENT

    - Paint products shall comply with following bio-based standards for biobased materials:

| Material Type | Percent by Weight |
| --- | --- |
| Interior Paint | 20 percent biobased material |
| Interior Paint- Oil Based and Solvent Alkyd | 67 percent biobased material |
| Exterior Paint | 20 percent biobased material |
| Wood & Concrete Stain | 39 percent biobased content |
| Polyurethane Coatings | 25 percent biobased content |
| Water Tank Coatings | 59 percent biobased content |
| Wood & Concrete Sealer- Membrane Concrete Sealers | 11 percent biobased content |
| Wood & Concrete Sealer- Penetrating Liquid | 79 percent biobased content |

    - The minimum-content standards are based on the weight (not the volume) of the material.

PART 3 - EXECUTION

  - JOB CONDITIONS:

    - Safety: Observe required safety regulations and manufacturer's warning and instructions for storage, handling and application of painting materials.

      - Take necessary precautions to protect personnel and property from hazards due to falls, injuries, toxic fumes, fire, explosion, or other harm.

      - Deposit soiled cleaning rags and waste materials in metal containers approved for that purpose. Dispose of such items off the site at end of each day’s work.

    - Atmospheric and Surface Conditions:

      - Do not apply coating when air or substrate conditions are:

        - Less than 3 degrees C (5 degrees F) above dew point.

        - Below 10 degrees C (50 degrees F) or over 35 degrees C

(95 degrees F), unless specifically pre-approved by the COR and the product manufacturer. Under no circumstances are application conditions to exceed manufacturer recommendations.

        - When the relative humidity exceeds 85 percent; or to damp or wet surfaces; unless otherwise permitted by the paint manufacturer’s printed instructions.

      - Maintain interior temperatures until paint dries hard.

      - Do no exterior painting when it is windy and dusty.

      - Do not paint in direct sunlight or on surfaces that the sun will warm.

      - Apply only on clean, dry and frost-free surfaces except as follows:

        - Apply water thinned acrylic and cementitious paints to damp (not wet) surfaces only when allowed by manufacturer's printed instructions.

        - Concrete and masonry when permitted by manufacturer’s recommendations, dampen surfaces to which water thinned acrylic and cementitious paints are applied with a fine mist of water on hot dry days to prevent excessive suction and to cool surface.

      - Varnishing:

        - Apply in clean areas and in still air.

        - Before varnishing vacuum and dust area.

        - Immediately before varnishing wipe down surfaces with a tack rag.

  - INSPECTION:

    - Examine the areas and conditions where painting and finishing are to be applied and correct any conditions detrimental to the proper and timely completion of the work. Do not proceed with the work until unsatisfactory conditions are corrected to permit proper installation of the work.

  - GENERAL WORKMANSHIP REQUIREMENTS:

    - Application may be by brush or roller. Spray application only upon acceptance from the COR in writing.

    - Furnish to the COR a painting schedule indicating when the respective coats of paint for the various areas and surfaces will be completed. This schedule is to be kept current as the job progresses.

    - Protect work at all times. Protect all adjacent work and materials by suitable covering or other method during progress of work. Upon completion of the work, remove all paint and varnish spots from floors, glass and other surfaces. Remove from the premises all rubbish and accumulated materials of whatever nature not caused by others and leave work in a clean condition.

    - Remove and protect hardware, accessories, device plates, lighting fixtures, and factory finished work, and similar items, or provide in place protection. Upon completion of each space, carefully replace all removed items by workmen skilled in the trades involved.

    - When indicated to be painted, remove electrical panel box covers and doors before painting walls. Paint separately and re-install after all paint is dry.

    - Materials are to be applied under adequate illumination, evenly spread and flowed on smoothly to avoid runs, sags, holidays, brush marks, air bubbles and excessive roller stipple.

    - Apply materials with a coverage to hide substrate completely. When color, stain, dirt or undercoats show through final coat of paint, the surface is to be covered by additional coats until the paint film is of uniform finish, color, appearance and coverage, at no additional cost to the Government.

    - All coats are to be dry to manufacturer’s recommendations before applying succeeding coats.

    - All suction spots or “hot spots” in plaster after the application of the first coat are to be touched up before applying the second coat.

    - Do not apply paint behind frameless mirrors that use mastic for adhering to wall surface.

  - SURFACE PREPARATION:

    - General:

      - The Contractor shall be held wholly responsible for the finished appearance and satisfactory completion of painting work. Properly prepare all surfaces to receive paint, which includes cleaning, sanding, and touching-up of all prime coats applied under other Sections of the work. Broom clean all spaces before painting is started. All surfaces to be painted or finished are to be completely dry, clean and smooth.

      - See other sections of specifications for specified surface conditions and prime coat.

      - Perform preparation and cleaning procedures in strict accordance with the paint manufacturer’s instructions and as herein specified, for each particular substrate condition.

      - Clean surfaces before applying paint or surface treatments with materials and methods compatible with substrate and specified finish. Remove any residue remaining from cleaning agents used. Do not use solvents, acid, or steam on concrete and masonry. Schedule the cleaning and painting so that dust and other contaminants from the cleaning process will not fall in wet, newly painted surfaces.

      - Maximum Moisture Content of Substrates: When measured with an electronic moisture meter as follows:

        - Concrete: 12 percent.

        - Fiber-Cement Board: 12 percent.

        - Masonry (Clay and CMU’s): 12 percent.

        - Wood: 15 percent.

        - Gypsum Board: 12 percent.

        - Plaster: 12 percent.

    - Wood:

      - Sand to a smooth even surface and then dust off.

      - Sand surfaces showing raised grain smooth between each coat.

      - Wipe surface with a tack rag prior to applying finish.

      - Surface painted with an opaque finish:

        - Coat knots, sap and pitch streaks with MPI 36 (Knot Sealer) before applying paint.

        - Apply two coats of MPI 36 (Knot Sealer) over large knots.

      - After application of prime or first coat of stain, fill cracks, nail and screw holes, depressions and similar defects with wood filler paste. Sand the surface to make smooth and finish flush with adjacent surface.

      - Before applying finish coat, reapply wood filler paste if required, and sand surface to remove surface blemishes. Finish flush with adjacent surfaces.

      - Fill open grained wood such as oak, walnut, ash and mahogany with MPI 91 (Wood Filler Paste), colored to match wood color.

        - Thin filler in accordance with manufacturer's instructions for application.

        - Remove excess filler, wipe as clean as possible, dry, and sand as specified.

    - Ferrous Metals:

      - Remove oil, grease, soil, drawing and cutting compounds, flux and other detrimental foreign matter in accordance with SSPC-SP 1 (Solvent Cleaning).

      - Remove loose mill scale, rust, and paint, by hand or power tool cleaning, as defined in SSPC-SP 2 (Hand Tool Cleaning) and SSPC-SP 3 (Power Tool Cleaning).

      - Fill dents, holes and similar voids and depressions in flat exposed surfaces of hollow steel doors and frames, access panels, roll-up steel doors and similar items specified to have semi-gloss or gloss finish with TT-F-322D (Filler, Two-Component Type, For Dents, Small Holes and Blow-Holes). Finish flush with adjacent surfaces.

        - Fill flat head countersunk screws used for permanent anchors.

        - Do not fill screws of item intended for removal such as glazing beads.

      - Spot prime abraded and damaged areas in shop prime coat which expose bare metal with same type of paint used for prime coat. Feather edge of spot prime to produce smooth finish coat.

      - Spot prime abraded and damaged areas which expose bare metal of factory finished items with paint as recommended by manufacturer of item.

    - Zinc-Coated (Galvanized) Metal Surfaces Specified Painted:

      - Clean surfaces to remove grease, oil and other deterrents to paint adhesion in accordance with SSPC-SP 1 (Solvent Cleaning).

      - Spot coat abraded and damaged areas of zinc-coating which expose base metal on hot-dip zinc-coated items with MPI 18 (Organic Zinc Rich Coating). Prime or spot prime with MPI 134 (Waterborne Galvanized Primer) or MPI 135 (Non-Cementitious Galvanized Primer) depending on finish coat compatibility.

    - Masonry, Concrete, Cement Board, Cement Plaster and Stucco:

      - Clean and remove dust, dirt, oil, grease efflorescence, form release agents, laitance, and other deterrents to paint adhesion.

      - Use emulsion type cleaning agents to remove oil, grease, paint and similar products. Use of solvents, acid, or steam is not permitted.

      - Remove loose mortar in masonry work.

      - Replace mortar and fill open joints, holes, cracks and depressions with new mortar specified in Section 04 05 13, MASONRY MORTARING Section 04

05 16, MASONRY GROUTING. Do not fill weep holes. Finish to match adjacent surfaces.

      - Neutralize Concrete floors to be painted by washing with a solution of

1.4 Kg (3 pounds) of zinc sulfate crystals to 3.8 L (1 gallon) of water, allow to dry three (3) days and brush thoroughly free of crystals.

      - Repair broken and spalled concrete edges with concrete patching compound to match adjacent surfaces as specified in

Division 03, CONCRETE Sections. Remove projections to level of adjacent surface by grinding or similar methods.

    - Gypsum Plaster and Gypsum Board:

      - Remove efflorescence, loose and chalking plaster or finishing materials.

      - Remove dust, dirt, and other deterrents to paint adhesion.

      - Fill holes, cracks, and other depressions with CID-A-A-1272A finished flush with adjacent surface, with texture to match texture of adjacent surface. Patch holes over 25 mm (1-inch) in diameter as specified in Section for plaster or gypsum board.

  - PAINT PREPARATION:

    - Thoroughly mix painting materials to ensure uniformity of color, complete dispersion of pigment and uniform composition.

    - Do not thin unless necessary for application and when finish paint is used for body and prime coats. Use materials and quantities for thinning as specified in manufacturer's printed instructions.

    - Remove paint skins, then strain paint through commercial paint strainer to remove lumps and other particles.

    - Mix two (2) component and two (2) part paint and those requiring additives in such a manner as to uniformly blend as specified in manufacturer's printed instructions unless specified otherwise.

    - For tinting required to produce exact shades specified, use color pigment recommended by the paint manufacturer.

  - APPLICATION:

    - Start of surface preparation or painting will be construed as acceptance of the surface as satisfactory for the application of materials.

    - Unless otherwise specified, apply paint in three (3) coats; prime, body, and finish. When two (2) coats applied to prime coat are the same, first coat applied over primer is body coat and second coat is finish coat.

    - Apply each coat evenly and cover substrate completely.

    - Allow not less than 48 hours between application of succeeding coats, except as allowed by manufacturer's printed instructions, and approved by COR.

    - Apply by brush or roller. Spray application for new or existing occupied spaces only upon approval by acceptance from COR in writing.

      - Apply painting materials specifically required by manufacturer to be applied by spraying.

      - In new construction and in existing occupied spaces, where paint is applied by spray, mask or enclose with polyethylene, or similar air tight material with edges and seams continuously sealed including items specified in “Building and Structural Work Field Painting”; “Work not Painted”; motors, controls, telephone, and electrical equipment, fronts of sterilizes and other recessed equipment and similar prefinished items.

    - Do not paint in closed position operable items such as access doors and panels, window sashes, overhead doors, and similar items except overhead roll-up doors and shutters.

  - PRIME PAINTING:

    - After surface preparation, prime surfaces before application of body and finish coats, except as otherwise specified.

    - Spot prime and apply body coat to damaged and abraded painted surfaces before applying succeeding coats.

    - Additional field applied prime coats over shop or factory applied prime coats are not required except for exterior exposed steel apply an additional prime coat.

    - Prime rabbets for stop and face glazing of wood, and for face glazing of steel.

    - Wood and Wood Particleboard:

      - Use same kind of primer specified for exposed face surface.

        - Exterior wood: MPI 7 (Exterior Oil Wood Primer) for new construction and MPI 5(Exterior Alkyd Wood Primer) for repainting bare wood

primer except where MPI 90 (Interior Wood Stain, Semi-Transparent) is scheduled.

        - Interior wood except for transparent finish: MPI 45 (Interior Primer Sealer) or MPI 46 (Interior Enamel Undercoat), thinned if recommended by manufacturer.

        - Transparent finishes as specified under “Transparent Finishes on Wood Except Floors Article” and “Finish for Wood Floors Article” .

      - Apply two (2) coats of primer MPI 7 (Exterior Oil Wood Primer) or MPI 5 (Exterior Alkyd Wood Primer) or sealer MPI 45 (Interior Primer Sealer) or MPI 46 (Interior Enamel Undercoat) to surfaces of wood doors, including top and bottom edges, which are cut for fitting or for other reason.

      - Apply one (1) coat of primer MPI 7 (Exterior Oil Wood Primer) or MPI 5 (Exterior Alkyd Wood Primer) or sealer MPI 45 (Interior Primer Sealer) or MPI 46 (Interior Enamel Undercoat) as soon as delivered to site to surfaces of unfinished woodwork, except concealed surfaces of shop fabricated or assembled millwork and surfaces specified to have varnish, stain or natural finish.

      - Back prime and seal ends of exterior woodwork, and edges of exterior plywood specified to be finished.

      - Apply MPI 67 (Interior Latex Fire Retardant, Top-Coat (UL Approved) to wood for fire retardant finish.

    - Metals except boilers, incinerator stacks, and engine exhaust pipes:

      - Steel and iron: MPI 79 (Marine Alkyd Metal Primer) finish is specified.

      - Zinc-coated steel and iron: MPI 134 (Waterborne Galvanized Primer)	MPI 135 (Non-Cementitious Galvanized Primer) .

      - Aluminum scheduled to be painted: MPI 95 (Fast Drying Metal Primer).

      - Terne Metal: MPI 79 (Marine Alkyd Metal Primer).

      - Copper and copper alloys scheduled to be painted: MPI 95 (Fast Drying Metal Primer).

      - Machinery not factory finished: MPI 9 (Exterior Alkyd Enamel).

      - Asphalt coated metal: MPI 1 (Aluminum Paint).

      - Metal over 94 degrees C (201 degrees F), Boilers, Incinerator Stacks, and Engine Exhaust Pipes: MPI 22 (High Heat Resistant Coating).

    - Gypsum Board and Hardboard:

      - Surfaces scheduled to have MPI 10 (Exterior Latex, Flat, MPI 11 (Exterior Latex, Semi-Gloss, MPI 119 (Exterior Latex, High Gloss (acrylic)), MPI 53 (Interior Latex, Flat), MPI Gloss Level 1, MPI 52 (Interior Latex, MPI Gloss Level 3) MPI 54 (Interior Latex, Semi-Gloss, MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss) finish: Use MPI

10 (Exterior Latex, Flat)	MPI 11 (Exterior Latex, Semi-Gloss)	MPI

119 (Exterior Latex, High Gloss (acrylic))	MPI 53 (Interior Latex, MPI Gloss Level 3)	MPI 52 (Interior Latex, MPI Gloss Level 3)	MPI

54 (Interior Latex, Semi-Gloss, MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss) respectively .

      - Primer: MPI 50 (Interior Latex Primer Sealer) except use MPI 45 (Interior Primer Sealer), MPI 46 (Interior Enamel Undercoat), in shower and bathrooms.

      - Surfaces scheduled to receive vinyl coated fabric wall covering:

        - Use MPI 45 (Interior Primer Sealer)	MPI 46 (Interior Enamel Undercoat) .

        - Use MPI 101 (Cold Curing Epoxy Primer) for surfaces scheduled to receive MPI 77 (Epoxy Cold Cured, Gloss)	MPI 98 (High Build Epoxy Coating)	MPI 108 (High Build Epoxy Marine Coating) finish .

    - Gypsum Plaster and Veneer Plaster:

      - Surfaces scheduled to receive vinyl coated fabric wall covering: Use MPI 45 (Interior Primer Sealer).

      - MPI 45 (Interior Primer Sealer), except use MPI 50 (Interior Latex Primer Sealer) when an alkyd flat finish is specified.

      - Surfaces scheduled to have MPI 10 (Exterior Latex, Flat)	MPI 11 (Exterior Latex, Semi-Gloss)	MPI 119 (Exterior Latex, High Gloss (acrylic))	MPI 53 (Interior Latex, Flat, MPI Gloss Level 1)	MPI 52 (Interior Latex, MPI Gloss Level 3)	MPI 54 (Interior Latex, Semi- Gloss, MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss) finish: Use MPI 10 (Exterior Latex, Flat) MPI 11 (Exterior Latex, Semi-Gloss) MPI 119 (Exterior Latex, High Gloss (acrylic))	MPI 53 (Interior Latex, Flat, MPI Gloss Level 1)	MPI 52 Latex, MPI Gloss Level 3)

MPI 54 (Interior Latex, Semi-Gloss, MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss) respectively.

      - Use MPI 101 (Cold Curing Epoxy Primer) for surfaces scheduled to receive	MPI 77 (Epoxy Cold Cured, Gloss)	MPI 108 (High Build Epoxy Marine Coating)	finish.

    - Concrete Masonry Units except glazed or integrally colored and decorative units:

      - MPI 4 (Block Filler) on interior surfaces.

      - Prime exterior surface as specified for exterior finishes.

    - Cement Plaster or stucco Concrete Masonry, Brick Masonry and Cement board Interior Surfaces of Ceilings and Walls:

      - MPI 53 (Interior Latex, Flat, MPI Gloss Level 1)	MPI 52 (Interior Latex, MPI Gloss Level 3)	MPI 54 (Interior Latex, Semi-Gloss,

MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss) except use two

(2) coats where substrate has aged less than six (6) months.

      - Use MPI 138 (Interior High Performance Latex, MPI Gloss Level 2)	MPI

139 (Interior High Performance Latex, MPI Gloss level 3)		MPI 140 (Interior High Performance latex, MPI Gloss Level 4)	MPI 141 (Interior High Performance Latex, MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss)		TT-P-1411A (Paint, Copolymer Resin, Cementitious) Type II	MPI 77 (Epoxy Cold Cured, Gloss	MPI 98 (High Build Epoxy Coating) MPI 108 (High Build Epoxy Marine Coating) as scheduled.

    - Concrete Floors: MPI 68 (Interior Exterior Latex Porch & Floor Paint, Gloss)	MPI 60 (Interior Exterior Latex Porch & Floor Paint, Low Gloss) . MPI 99 (Water-based Acrylic Curing and Sealing Compound).

  - EXTERIOR FINISHES:

    - Apply following finish coats to match existing.

    - Wood:

      - Do not apply finish coats on surfaces concealed after installation, top and bottom edges of wood doors and sash, or on edges of wood framed insect screens.

      - Two (2) coats of MPI 10 Exterior Latex, Flat)	MPI 11 (Exterior Latex, Semi-Gloss)	MPI 119 (Exterior Latex, High Gloss (acrylic)) on exposed surfaces, except where transparent finish is specified.

      - Two (2) coats of MPI 31 (Polyurethane, Moisture Cured, Clear Gloss) MPI 71 (Polyurethane, Moisture Cured, Clear Flat) for transparent finish.

    - Steel and Ferrous Metal , Including Tern :

      - Two (2) coats of MPI 8 (Exterior Alkyd, Flat)	MPI 9 (Exterior Alkyd Enamel)	MPI 94 (Exterior Alkyd, Semi-Gloss) on exposed surfaces, except on surfaces over 94 degrees C (201 degrees F).

      - One (1) coat of MPI 22 (High Heat Resistant Coating) on surfaces over

94 degrees K (290 degrees F) and on surfaces of boiler , incinerator

, stacks engine exhaust pipes.

    - Machinery without factory finish except for primer: One (1) coat MPI 8 (Exterior Alkyd, Flat)	MPI 9 (Exterior Alkyd Enamel)	MPI 94 (Exterior Alkyd, Semi-Gloss) .

    - Concrete Masonry Units Brick	Cement Plaster	Concrete :

      - General:

        - Where specified in Section 09 06 00, SCHEDULE FOR FINISHES or shown.

        - Mix as specified in manufacturer's printed directions.

        - Do not mix more paint than can be used within four (4) hours after mixing. Discard paint that has started to set.

        - Dampen warm surfaces above 24 degrees C (75 degrees F) with fine mist of water before application of paint. Do not leave free water on surface.

        - Cure paint with a fine mist of water as specified in manufacturer's printed instructions.

      - Use two (2) coats of TT-P-1411 (Paint, Co-polymer-Resin, Cementitious), unless specified otherwise.

  - INTERIOR FINISHES:

    - Apply following finish coats over prime coats in spaces or on surfaces to match existing.

    - Metal Work:

      - Apply to exposed surfaces.

      - Omit body and finish coats on surfaces concealed after installation except electrical conduit containing conductors over 600 volts.

      - Ferrous Metal, Galvanized Metal, and Other Metals Scheduled:

        - Apply two (2) coats of MPI 47 (Interior Alkyd, Semi-Gloss) unless specified otherwise.

        - Two (2) coats of MPI 48 (Interior Alkyd Gloss)	MPI 51 (Interior Alkyd, Eggshell) .

        - One (1) coat of MPI 46 (Interior Enamel Undercoat) plus one coat of MPI 47 (Interior Alkyd, Semi-Gloss) on exposed interior surfaces of alkyd-amine enamel prime finished windows.

        - One (1) coat of MPI 101 primer over two (2) coats of waterborne light industrial coating MPI 163 on exposed surfaces in battery rooms	pool area	chlorinator rooms . Steel is to be blast cleaned to SSPC 10NACE No. 2.

        - Machinery: One (1) coat MPI 9 (Exterior Alkyd Enamel).

        - Asphalt Coated Metal: One (1) coat MPI 1 (Aluminum Paint ).

        - Ferrous Metal over 94 degrees K (290 degrees F): Boilers, Incinerator Stacks, and Engine Exhaust Pipes: One (1) coat MPI 22 (High Heat Resistant Coating.

    - Gypsum Board:

      - One (1) coat of MPI 45 (Interior Primer Sealer)	MPI 46 (Interior Enamel Undercoat) plus one (1) coat of MPI 139 (Interior High Performance Latex, MPI Gloss level 3).

      - Two (2) coats of MPI 138 (Interior High Performance Latex, MPI Gloss Level 2).

      - One (1) coat of MPI 45 (Interior Primer Sealer)	MPI 46 (Interior Enamel Undercoat) plus one (1) coat of MPI 54 (Interior Latex, Semi- Gloss, MPI Gloss Level 5) or MPI 114 (Interior Latex, Gloss).

      - One (1) coat of MPI 45 (Interior Primer Sealer) MPI 46 (Interior Enamel Undercoat) plus one (1) coat of MPI 48 (Interior Alkyd Gloss).

    - Plaster:

      - One (1) coat of MPI 45 (Interior Primer Sealer) MPI 46 (Interior Enamel Undercoat) MPI 50 (Interior Latex Primer Sealer) plus one (1) coat of MPI 139 (Interior High Performance Latex, MPI Gloss level 3).

      - Two (2) coats of MPI 51 (Interior Alkyd, Eggshell).

      - One (1) coat of MPI 45 (Interior Primer Sealer)	MPI 46 (Interior Enamel Undercoat) or MPI 50 (Interior Latex Primer Sealer) plus one

(1) coat of 139 (Interior High Performance Latex, MPI Gloss level 3).

      - One (1) coat MPI 101 (Cold Curing Epoxy Prime).

    - Masonry and Concrete Walls:

      - Over MPI 4 (InteriorExterior Latex Block Filler) on CMU surfaces.

      - Two (2) coats of MPI 53 (Interior Latex, Flat, MPI Gloss Level

1)	MPI 52 (Interior Latex, MPI Gloss Level 3)	MPI 54 (Interior

Latex, Semi-Gloss, MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss)

.

      - Two (2) coats of MPI 138 (Interior High Performance Latex, MPI Gloss Level 2)	MPI 139 (Interior High Performance Latex, MPI Gloss Level 3) MPI 140 (Interior High Performance Latex MPI Gloss Level 4)	MPI 141 (Interior High Performance Latex MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss) .

    - Wood:

      - Sanding:

        - Use 220-grit sandpaper.

        - Sand sealers and varnish between coats.

        - Sand enough to scarify surface to assure good adhesion of subsequent coats, to level roughly applied sealer and varnish, and to knock off "whiskers" of any raised grain as well as dust particles.

      - Sealers:

        - MPI 31 (gloss) or MPI 71 (flat) thinned as recommended by manufacturer at rate of one (1) part of thinner to four (4) parts of varnish.

        - Apply sealers specified except sealer may be omitted where pigmented, penetrating, or wiping stains containing resins are used.

        - Allow manufacturer's recommended drying time before sanding, but not less than 24 hours or 36 hours in damp or muggy weather.

        - Sand as specified.

      - Paint Finish:

        - One (1) coat of MPI 45 (Interior Primer Sealer)	MPI 46 (Interior Enamel Undercoat) plus one (1) coat of MPI 47 (Interior Alkyd, Semi-Gloss.

        - One (1) coat MPI 66 (Interior Alkyd Fire retardant, Clear Top-Coat (UL Approved) MPI 67 (Interior Latex Fire Retardant, Top-Coat (UL Approved), intumescent type, on exposed wood in attics with floors used for mechanical equipment  and above ceilings where shown .

        - One (1) coat of MPI 45 Interior Primer Sealer)	MPI 46 (Interior Enamel Undercoat) plus one (1) coat of MPI 48 (Interior Alkyd Gloss).

        - Two (2) coats of MPI 51 (Interior Alkyd, Eggshell).

      - Transparent Finishes on Wood Except Floors.

        - Natural Finish:

One (1) coat of sealer MPI 31 (gloss)	MPI 71 (flat) thinned with thinner recommended by manufacturer at rate of one (1) part of thinner to four (4) parts of varnish.

Two (2) coats of MPI 71 (Polyurethane, Moisture Cured, Clear Flat MPI 31 (Polyurethane, Moisture Cured, Clear Gloss.

        - Stain Finish:

One (1) coat of MPI 90 (Interior Wood Stain, Semi-Transparent).

Use wood stain of type and color required to achieve finish specified. Do not use varnish type stains.

One (1) coat of sealer MPI 31 (gloss)	MPI 71 (flat) thinned as recommended by manufacturer at rate of one (1) part of thinner to four (4) parts of varnish.

Two (2) coats of MPI 71 (Polyurethane, Moisture Cured, Clear Flat)	MPI 31 (Polyurethane Moisture Cured, Clear Gloss) .

        - Varnish Finish:

One (1) coat of sealer MPI 31 (gloss)	MPI 71 (flat) thinned as recommended by manufacturer at rate of one (1) part of thinner to four (4) parts of varnish.

Two (2) coats of MPI 71 (Polyurethane, Moisture Cured, Clear Flat)	MPI 31 (Polyurethane Moisture Cured, Clear Gloss) .

        - Fire Retardant Intumescent Varnish:

MPI 66 (Interior Alkyd Fire Retardant, Clear Top-Coat (UL Approved)) Intumescent Type, Fire Retardant Coating where scheduled: Two (2) coats.

      - Finish for Wood Floors:

        - Hardwood Flooring:

Apply MPI 91 (Wood Filler Paste) to open grained wood. Remove surplus filler and wipe clean.

Sand lightly when dry. Remove dust.

Apply two (2) coats of CID-A-A-2335 (Sealer, Surface).

Apply two (2) thin coats of P-W-155 (Wax Floor, Water Emulsion) and machine buff to uniform luster.

        - Stage Floor: Sand only. No filling, sealing, or waxing is required.

        - Exercise Area	Recreation Hall , Gymnasium , Handball Boards in Exercise Area Floor Finish:

Floor-Sealer Formulation: Pliable, penetrating type, MFMA Group I, Sealers.

Finish-Coat Formulation: Formulated for gloss finish and multicoat application.

Type: MFMA Group 5, Water-Based Finishes. Allow 48 hours between coats.

Apply in one (1) continuous operation with squeegee or lamb’s wool applicator with application free from streaks in accordance with plastic coating manufacturer's directions.

        - Striping:

Where striping is shown on construction documents for wood floors, apply pressure sensitive adhesive back vinyl plastic tape stripes in widths shown in construction documents.

Do striping when floor coating is dry.

Install stripes to straight lines and true curves.

Provide colors as specified in Section 09 06 00, SCHEDULE FOR FINISHES or indicated in construction documents.

    - Cement Board: One (1) coat of MPI 138 (Interior High Performance Latex, MPI Gloss Level 2) MPI 139 (Interior High Performance Latex, MPI Gloss Level 3)  MPI 140 (Interior High Performance Latex MPI Gloss

Level 4) MPI 141 (Interior High Performance Latex, MPI Gloss Level 5  MPI 114 (Interior Latex, Gloss) .

    - Concrete Floors: One (1) coat of MPI 68 (Interior Exterior Latex Porch & Floor Paint, Gloss).

    - Miscellaneous:

      - Apply where specified in Section 09 06 00, SCHEDULE FOR FINISHES.

      - MPI 1 (Aluminum Paint): Two (2) coats of aluminum paint.

      - Existing acoustical units scheduled to be repainted except acoustical units with a vinyl finish:

        - Clean units free of dust, dirt, grease, and other deterrents to paint adhesion.

        - Mineral fiber units: One (1) coat of MPI 53 (Interior Latex, Flat, MPI Gloss Level 1)	MPI 52 (Interior Latex, MPI Gloss

Level 3)	MPI 54 (Interior Latex, Semi-Gloss, MPI Gloss Level 5) MPI 114 (Interior Latex, Gloss) .

        - Units of organic fiber or other material not having a class A rating: One (1) coat of MPI 66 (Interior Alkyd Fire Retardant, Clear Top-Coat (UL Approved))	MPI 67 (Interior Latex Fire Retardant, Top-Coat (UL Approved)) fire retardant paint.

      - Interstitial floor markings: One (1) coat MPI 27 (Exterior Interior Alkyd Floor Enamel, Gloss)		MPI 59 ((Interior Exterior Alkyd Porch & Floor Enamel, Low Gloss)	MPI 68 (Interior Exterior Latex Porch & Floor Paint, Gloss)	MPI 60 (interior Exterior Latex Porch & Floor Paint, Low Gloss) .

  - REFINISHING EXISTING PAINTED SURFACES:

    - Clean, patch and repair existing surfaces as specified under “Surface Preparation”. No “telegraphing” of lines, ridges, flakes, etc., through new surfacing is permitted. Where this occurs, sand smooth and re-finish until surface meets with COR’s approval.

    - Remove and reinstall items as specified under “General Workmanship Requirements”.

    - Remove existing finishes or apply separation coats to prevent non compatible coatings from having contact.

    - Patched or Replaced Areas in Surfaces and Components: Apply spot prime and body coats as specified for new work to repaired areas or replaced components.

    - Except where scheduled for complete painting apply finish coat over plane surface to nearest break in plane, such as corner, reveal, or frame.

    - In existing rooms and areas where alterations occur, clean existing stained and natural finished wood retouch abraded surfaces and then give entire surface one (1) coat of MPI 31 (Polyurethane, Moisture Cured, Clear Gloss)	MPI 71 (Polyurethane, Moisture Cured, Clear Flat) .

    - Refinish areas as specified for new work to match adjoining work unless specified or scheduled otherwise.

    - Coat knots and pitch streaks showing through old finish with MPI 36 (Knot Sealer) before refinishing.

    - Sand or dull glossy surfaces prior to painting.

    - Sand existing coatings to a feather edge so that transition between new and existing finish will not show in finished work.

  - PAINT COLOR:

    - Color and gloss of finish coats is specified in Section 09 06 00, SCHEDULE FOR FINISHES.

    - For additional requirements regarding color see Articles, “REFINISHING EXISTING PAINTED SURFACE” and “MECHANICAL AND ELECTRICAL FIELD PAINTING SCHEDULE”.

    - Coat Colors:

      - Color of priming coat: Lighter than body coat.

      - Color of body coat: Lighter than finish coat.

      - Color prime and body coats to not show through the finish coat and to mask surface imperfections or contrasts.

    - Painting, Caulking, Closures, and Fillers Adjacent to Casework:

      - Paint to match color of casework where casework has a paint finish.

      - Paint to match color of wall where casework is stainless steel, plastic laminate, or varnished wood.

  - MECHANICAL AND ELECTRICAL WORK FIELD PAINTING SCHEDULE:

    - Field painting of mechanical and electrical consists of cleaning, touching-up abraded shop prime coats, and applying prime, body and finish coats to materials and equipment if not factory finished in space scheduled to be finished.

    - In spaces not scheduled to be finish painted in Section 09 06 00, SCHEDULE FOR FINISHES paint as specified below.

    - Paint various systems specified in Division 02 – EXISTING CONDITIONS, Division 21 – FIRE SUPPRESSION, Division 22 - PLUMBING, Division 23 – HEATING, VENTILATION AND AIR-CONDITIONING, Division 26 - ELECTRICAL, Division 27 - COMMUNICATIONS, and Division 28 – ELECTRONIC SAFETY AND SECURITY.

    - Paint after tests have been completed.

    - Omit prime coat from factory prime-coated items.

    - Finish painting of mechanical and electrical equipment is not required when located in interstitial spaces, above suspended ceilings, in concealed areas such as pipe and electric closets, pipe basements, pipe tunnels, trenches, attics, roof spaces, shafts and furred spaces except on electrical conduit containing feeders 600 volts or more.

    - Omit field painting of items specified in “BUILDING AND STRUCTURAL WORK FIELD PAINTING”; “Building and Structural Work not Painted”.

    - Color:

      - Paint items having no color specified in Section 09 06 00, SCHEDULE FOR FINISHES to match surrounding surfaces.

      - Paint colors as specified in Section 09 06 00, SCHEDULE FOR FINISHES except for following:

        - White: Exterior unfinished surfaces of enameled plumbing fixtures. Insulation coverings on breeching and uptake inside boiler house, drums and drum-heads, oil heaters, condensate tanks and condensate piping.

        - Gray: Heating, ventilating, air conditioning and refrigeration equipment (except as required to match surrounding surfaces), and water and sewage treatment equipment and sewage ejection equipment.

        - Aluminum Color: Ferrous metal on outside of boilers and in connection with boiler settings including supporting doors and door frames and fuel oil burning equipment, and steam generation system (bare piping, fittings, hangers, supports, valves, traps and miscellaneous iron work in contact with pipe).

        - Federal Safety Red: Exposed fire protection piping, hydrants, post indicators, electrical conducts containing fire alarm control wiring, and fire alarm equipment.

        - Federal Safety Orange: Entire lengths of electrical conduits containing feeders 600 volts or more.

        - Color to match brickwork sheet metal covering on breeching outside of exterior wall of boiler house.

    - Apply paint systems on properly prepared and primed surface as follows:

      - Exterior Locations:

        - Apply two (2) coats of MPI 8 (Exterior Alkyd, Flat)	MPI 94 (Exterior Alkyd, Semi-gloss)	MPI 9 (Exterior Alkyd Enamel) to the following ferrous metal items:

Vent and exhaust pipes with temperatures under 94 degrees C(201 degrees F), roof drains, fire hydrants, post indicators, yard hydrants, exposed piping and similar items.

        - Apply two (2) coats of MPI 10 (Exterior Latex, Flat)	MPI 11 (Exterior Latex, Semi-Gloss)	MPI 119 (Exterior Latex, High Gloss (acrylic)) to galvanized and zinc-copper alloy metal.

        - Apply one (1) coat of MPI 22 (High Heat Resistant Coating),

650 degrees C (1200 degrees F) to incinerator stacks, boiler stacks, and engine generator exhaust.

      - Interior Locations:

        - Apply two (2) coats of MPI 47 (Interior Alkyd, Semi-Gloss) to following items:

Metal under 94 degrees C (201 degrees F) of items such as bare piping, fittings, hangers and supports.

Equipment and systems such as hinged covers and frames for control cabinets and boxes, cast-iron radiators, electric conduits and panel boards.

Heating, ventilating, air conditioning, plumbing equipment, and machinery having shop prime coat and not factory finished.

        - Ferrous metal exposed in hydrotherapy equipment room and chlorinator room of water and sewerage treatment plants: One (1) coat of MPI 101 (Cold Curing Epoxy Primer) and one (1) coat of MPI 77 (Epoxy Cold Cured, Gloss	MPI 98 (High Build Epoxy Coating))	MPI 108 (High Build Epoxy Marine coating) .

        - Apply one (1) coat of MPI 50 (Interior Latex Primer Sealer) and one (1) coat of MPI 53 (Interior Latex, Flat, MPI Gloss Level 1) MPI 44 (Interior Low Sheen Latex)	MPI 52 (Interior Latex, MPI Gloss Level 3) MPI 43 (Interior Satin Latex)	MPI 54 (Interior Latex, Semi-Gloss, MPI Gloss Level 5)	MPI 114 (Interior Latex, Gloss) on finish of insulation on boiler breeching and uptakes inside boiler house, drums, drumheads, oil heaters, feed water heaters, tanks and piping.

        - Apply two (2) coats of MPI 22 (High Heat Resistant Coating) to ferrous metal surface over 94 degrees K (290 degrees F) of following items:

Garbage and trash incinerator. Medical waste incinerator.

Exterior of boilers and ferrous metal in connection with boiler settings including supporting members, doors and door frames and fuel oil burning equipment.

Steam line flanges, bare pipe, fittings, valves, hangers and supports over 94 degrees K (290 degrees F).

Engine generator exhaust piping and muffler.

        - Paint electrical conduits containing cables rated 600 volts or more using two (2) coats of MPI 9 (Exterior Alkyd Enamel)	MPI 8 (Exterior Alkyd, Flat)	MPI 94 (Exterior Alkyd, Semi-gloss) in the Federal Safety Orange color in exposed and concealed spaces full length of conduit.

      - Other exposed locations:

        - Metal surfaces, except aluminum, of cooling towers exposed to view, including connected pipes, rails, and ladders: Two (2) coats of

MPI 1 (Aluminum Paint).

        - Cloth jackets of insulation of ducts and pipes in connection with plumbing, air conditioning, ventilating refrigeration and heating systems: One (1) coat of MPI 50 (Interior Latex Primer Sealer) and one (1) coat of MPI 10 (Exterior Latex, Flat)	MPI 11 (Exterior Latex Semi-Gloss	MPI 119 (Exterior Latex, High Gloss (acrylic)) .

  - BUILDING AND STRUCTURAL WORK FIELD PAINTING:

    - Painting and finishing of interior and exterior work except as specified here-in-after.

      - Painting and finishing of new and existing work including colors and gloss of finish selected is specified in Finish Schedule, Section 09 06 00, SCHEDULE FOR FINISHES.

      - Painting of disturbed, damaged and repaired or patched surfaces when entire space is not scheduled for complete repainting or refinishing.

      - Painting of ferrous metal and galvanized metal.

      - Painting of wood with fire retardant paint exposed in attics, when used as mechanical equipment space (except shingles).

      - Identity painting and safety painting.

    - Building and Structural Work not Painted:

      - Prefinished items:

        - Casework, doors, elevator entrances and cabs, metal panels, wall covering, and similar items specified factory finished under other sections.

        - Factory finished equipment and pre-engineered metal building components such as metal roof and wall panels.

      - Finished surfaces:

        - Hardware except ferrous metal.

        - Anodized aluminum, stainless steel, chromium plating, copper, and brass, except as otherwise specified.

        - Signs, fixtures, and other similar items integrally finished.

      - Concealed surfaces:

        - Inside dumbwaiter, elevator and duct shafts, interstitial spaces, pipe basements, crawl spaces, pipe tunnels, above ceilings, attics, except as otherwise specified.

        - Inside walls or other spaces behind access doors or panels.

        - Surfaces concealed behind permanently installed casework and equipment.

      - Moving and operating parts:

        - Shafts, chains, gears, mechanical and electrical operators, linkages, and sprinkler heads, and sensing devices.

        - Tracks for overhead or coiling doors, shutters, and grilles.

      - Labels:

        - Code required label, such as Underwriters Laboratories Inc., Intertek Testing Service or Factory Mutual Research Corporation.

        - Identification plates, instruction plates, performance rating, and nomenclature.

      - Galvanized metal:

        - Exterior chain link fence and gates, corrugated metal areaways, and gratings.

        - Gas Storage Racks.

        - Except where specifically specified to be painted.

      - Metal safety treads and nosings.

      - Gaskets.

      - Concrete curbs, gutters, pavements, retaining walls, exterior exposed foundations walls and interior walls in pipe basements.

      - Face brick.

      - Structural steel encased in concrete, masonry, or other enclosure.

      - Structural steel to receive sprayed-on fire proofing.

      - Ceilings, walls, columns in interstitial spaces.

      - Ceilings, walls, and columns in pipe basements.

      - Wood Shingles.

  - PROTECTION CLEAN UP, AND TOUCH-UP:

    - Protect work from paint droppings and spattering by use of masking, drop cloths, removal of items or by other approved methods.

    - Upon completion, clean paint from hardware, glass and other surfaces and items not required to be painted of paint drops or smears.

    - Before final inspection, touch-up or refinished in a manner to produce solid even color and finish texture, free from defects in work which was damaged or discolored.

- - - E N D - - -

SECTION 27 05 11

REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS

PART 1 - GENERAL

  - DESCRIPTION

    - This section includes common requirements to communications installations and applies to all sections of Division 27 and Division 28.

    - Provide completely functioning communications systems.

    - Comply with VAAR 852.236.91 and FAR clause 52.236-21 in circumstance of a need for additional detail or conflict between drawings, specifications, reference standards or code.

  - REFERENCES

    - Abbreviations and Acronyms

      - Refer to http://www.cfm.va.gov/til/sdetail.asp for Division 00, ARCHITECTURAL ABBREVIATIONS.

      - Additional Abbreviations and Acronyms:

| A | Ampere |
| --- | --- |
| AC | Alternating Current |
| AE | Architect and Engineer |
| AFF | Above Finished Floor |
| AHJ | Authority Having Jurisdiction |
| ANSI | American National Standards Institute |
| AWG | American Wire Gauge (refer to STP and UTP) |
| AWS | Advanced Wireless Services |
| BCT | Bonding Conductor for Telecommunications (also Telecommunications Bonding Conductor (TBC)) |
| BDA | Bi-Directional Amplifier |
| BICSI | Building Industry Consulting Service International |
| BIM | Building Information Modeling |
| BOM | Bill of Materials |
| BTU | British Thermal Units |
| BUCR | Back-up Computer Room |
| BTS | Base Transceiver Station |
| CAD | AutoCAD |
| CBOPC | Community Based Out Patient Clinic |

| CBC | Coupled Bonding Conductor |
| --- | --- |
| CBOC | Community Based Out Patient Clinic (refer to CBOPC, OPC, VAMC) |
| CCS | TIP's Cross Connection System (refer to VCCS and HCCS) |
| CFE | Contractor Furnished Equipment |
| CFM | US Department of Veterans Affairs Office of Construction and Facilities Management |
| CFR | Consolidated Federal Regulations |
| CIO | Communication Information Officer (Facility, VISN or Region) |
| cm | Centimeters |
| CO | Central Office |
| COR | Contracting Officer Representative |
| CPU | Central Processing Unit |
| CSU | Customer Service Unit |
| CUP | Conditional Use Permit(s) – Federal/GSA for VA |
| dB | Decibel |
| dBm | Decibel Measured |
| dBmV | Decibel per milli-Volt |
| DC | Direct Current |
| DEA | United States Drug Enforcement Administration |
| DSU | Data Service Unit |
| EBC | Equipment Bonding Conductor |
| ECC | Engineering Control Center (refer to DCR, EMCR) |
| EDGE | Enhanced Data (Rates) for GSM Evolution |
| EDM | Electrical Design Manual |
| EMCR | Emergency Management Control Room (refer to DCR, ECC) |
| EMI | Electromagnetic Interference (refer to RFI) |
| EMS | Emergency Medical Service |
| EMT | Electrical Metallic Tubing or thin wall conduit |
| ENTR | Utilities Entrance Location (refer to DEMARC, POTS, LEC) |

| EPBX | Electronic Digital Private Branch Exchange |
| --- | --- |
| ESR | Vendor’s Engineering Service Report |
| FA | Fire Alarm |
| FAR | Federal Acquisition Regulations in Chapter 1 of Title 48 of Code of Federal Regulations |
| FMS | VA’s Headquarters or Medical Center Facility’s Management Service |
| FR | Frequency (refer to RF) |
| FTS | Federal Telephone Service |
| GFE | Government Furnished Equipment |
| GPS | Global Positioning System |
| GRC | Galvanized Rigid Metal Conduit |
| GSM | Global System (Station) for Mobile |
| HCCS | TIP’s Horizontal Cross Connection System (refer to CCS & VCCS) |
| HDPE | High Density Polyethylene Conduit |
| HDTV | Advanced Television Standards Committee High- Definition Digital Television |
| HEC | Head End Cabinets(refer to HEIC, PA) |
| HEIC | Head End Interface Cabinets(refer to HEC, PA) |
| HF | High Frequency (Radio Band; Re FR, RF, VHF & UHF) |
| HSPA | High Speed Packet Access |
| HZ | Hertz |
| IBT | Intersystem Bonding Termination (NEC 250.94) |
| IC | Intercom |
| ICRA | Infectious Control Risk Assessment |
| IDEN | Integrated Digital Enhanced Network |
| IDC | Insulation Displacement Contact |
| IDF | Intermediate Distribution Frame |
| ILSM | Interim Life Safety Measures |
| IMC | Rigid Intermediate Steel Conduit |
| IRM | Department of Veterans Affairs Office of Information Resources Management |

| ISDN | Integrated Services Digital Network |
| --- | --- |
| ISM | Industrial, Scientific, Medical |
| IWS | Intra-Building Wireless System |
| LAN | Local Area Network |
| LBS | Location Based Services, Leased Based Systems |
| LEC | Local Exchange Carrier (refer to DEMARC, PBX & POTS) |
| LED | Light Emitting Diode |
| LMR | Land Mobile Radio |
| LTE | Long Term Evolution, or 4G Standard for Wireless Data Communications Technology |
| M | Meter |
| MAS | Medical Administration Service |
| MATV | Master Antenna Television |
| MCR | Main Computer Room |
| MCOR | Main Computer Operators Room |
| MDF | Main Distribution Frame |
| MH | Manholes or Maintenance Holes |
| MHz | Megaherts (106 Hz) |
| mm | Millimeter |
| MOU | Memorandum of Understanding |
| MW | Microwave (RF Band, Equipment or Services) |
| NID | Network Interface Device (refer to DEMARC) |
| NEC | National Electric Code |
| NOR | Network Operations Room |
| NRTL | OSHA Nationally Recognized Testing Laboratory |
| NS | Nurse Stations |
| NTIA | U.S. Department of Commerce National Telecommunications and Information Administration |
| OEM | Original Equipment Manufacturer |
| OI&T | Office of Information and Technology |
| OPC | VA’s Outpatient Clinic (refer to CBOC, VAMC) |
| OSH | Department of Veterans Affairs Office of Occupational Safety and Health |

| OSHA | United States Department of Labor Occupational Safety and Health Administration |
| --- | --- |
| OTDR | Optical Time-Domain Reflectometer |
| PA | Public Address System (refer to HE, HEIC, RPEC) |
| PBX | Private Branch Exchange (refer to DEMARC, LEC, POTS) |
| PCR | Police Control Room (refer to SPCC, could be designated SCC) |
| PCS | Personal Communications Service (refer to UPCS) |
| PE | Professional Engineer |
| PM | Project Manager |
| PoE | Power over Ethernet |
| POTS | Plain Old Telephone Service (refer to DEMARC, LEC, PBX) |
| PSTN | Public Switched Telephone Network |
| PSRAS | Public Safety Radio Amplification Systems |
| PTS | Pay Telephone Station |
| PVC | Poly-Vinyl Chloride |
| PWR | Power (in Watts) |
| RAN | Radio Access Network |
| RBB | Rack Bonding Busbar |
| RE | Resident Engineer or Senior Resident Engineer |
| RF | Radio Frequency (refer to FR) |
| RFI | Radio Frequency Interference (refer to EMI) |
| RFID | RF Identification (Equipment, System or Personnel) |
| RMC | Rigid Metal Conduit |
| RMU | Rack Mounting Unit |
| RPEC | Radio Paging Equipment Cabinets(refer to HEC, HEIC, PA) |
| RTLS | Real Time Location Service or System |
| RUS | Rural Utilities Service |
| SCC | Security Control Console (refer to PCR, SPCC) |
| SMCS | Spectrum Management and Communications Security (COMSEC) |

| SFO | Solicitation for Offers |
| --- | --- |
| SME | Subject Matter Experts (refer to AHJ) |
| SMR | Specialized Mobile Radio |
| SMS | Security Management System |
| SNMP | Simple Network Management Protocol |
| SPCC | Security Police Control Center (refer to PCR, SMS) |
| STP | Shielded Balanced Twisted Pair (refer to UTP) |
| STR | Stacked Telecommunications Room |
| TAC | VA’s Technology Acquisition Center, Austin, Texas |
| TCO | Telecommunications Outlet |
| TER | Telephone Equipment Room |
| TGB | Telecommunications Grounding Busbar (also Secondary Bonding Busbar (SBB)) |
| TIP | Telecommunications Infrastructure Plant |
| TMGB | Telecommunications Main Grounding Busbar (also Primary Bonding Busbar (PBB)) |
| TMS | Traffic Management System |
| TOR | Telephone Operators Room |
| TP | Balanced Twisted Pair (refer to STP and UTP) |
| TR | Telecommunications Room (refer to STR) |
| TWP | Twisted Pair |
| UHF | Ultra High Frequency (Radio) |
| UMTS | Universal Mobile Telecommunications System |
| UPCS | Unlicensed Personal Communications Service (refer to PCS) |
| UPS | Uninterruptible Power Supply |
| USC | United States Code |
| UTP | Unshielded Balanced Twisted Pair (refer to TP and STP) |
| UV | Ultraviolet |
| V | Volts |
| VAAR | Veterans Affairs Acquisition Regulation |
| VACO | Veterans Affairs Central Office |

| VAMC | VA Medical Center (refer to CBOC, OPC, VACO) |
| --- | --- |
| VCCS | TIP’s Vertical Cross Connection System (refer to CCS and HCCS) |
| VHF | Very High Frequency (Radio) |
| VISN | Veterans Integrated Services Network (refers to geographical region) |
| VSWR | Voltage Standing Wave Radio |
| W | Watts |
| WEB | World Electronic Broadcast |
| WiMAX | Worldwide Interoperability (for MW Access) |
| WI-FI | Wireless Fidelity |
| WMTS | Wireless Medical Telemetry Service |
| WSP | Wireless Service Providers |

    - Definitions:

      - Access Floor: Pathway system of removable floor panels supported on adjustable pedestals to allow cable placement in area below.

      - BNC Connector (BNC): United States Military Standard MIL-C-39012/21 bayonet-type coaxial connector with quick twist mating/unmating, and two lugs preventing accidental disconnection from pulling forces on cable.

      - Bond: Permanent joining of metallic parts to form an electrically conductive path to ensure electrical continuity and capacity to safely conduct any currents likely to be imposed to earth ground.

      - Bundled Microducts: All forms of jacketed microducts.

      - Conduit: Includes all raceway types specified.

      - Conveniently Accessible: Capable of being reached without use of ladders, or without climbing or crawling under or over obstacles such as, motors, pumps, belt guards, transformers, piping, ductwork, conduit and raceways.

      - Distributed (in house) Antenna System (DAS): An Emergency Radio Communications System installed for Emergency Responder (or first responders and Government personnel) use while inside facility to maintain contact with each respective control point;

      - DEMARC, Extended DMARC or ENTR: Service provider's main point of demarcation owned by LEC or service provider and establishes a

physical point where service provider's responsibilities for service and maintenance end. This point is called NID, in data networks.

      - Effectively Grounded: Intentionally bonded to earth through connections of low impedance having current carrying capacity to prevent buildup of currents and voltages resulting in hazard to equipment or persons.

      - Electrical Supervision: Analyzing a system’s function and components (i.e. cable breaks / shorts, inoperative stations, lights, LEDs and states of change, from primary to backup) on a 24/7/365 basis; provide aural and visual emergency notification signals to minimum two remote designated or accepted monitoring stations.

      - Electrostatic Interference (ESI) or Electrostatic Discharge Interference: Refer to EMI and RFI.

      - Emergency Call Systems: Wall units (in parking garages and stairwells) and pedestal mounts (in parking lots) typically provided with a strobe, camera and two-way audio communication functions. Additional units are typically provided in facility’s emergency room, designated nurses stations, director’s office, Disaster Control Center, SCC, ECC.

      - Project 25 (2014) (P25 (TIA-102 Series)): Set of standards for local, state and Federal public safety organizations and agencies digital LMR services. P25 is applicable to LMR equipment authorized or licensed under the US Department of Commerce National Telecommunications and Information Administration or FCC rules and regulations and is a required standard capability for all LMR equipment and systems.

      - Grounding Electrode Conductor: (GEC) Conductor connected to earth grounding electrode.

      - Grounding Electrode System: Electrodes through which an effective connection to earth is established, including supplementary communications system grounding electrodes and GEC.

      - Grounding Equalizer or Backbone Bonding Conductor (BBC): Conductor that interconnects elements of telecommunications grounding infrastructure.

      - Head End (HE): Equipment, hardware and software, or a master facility at originating point in a communications system designed for centralized communications control, signal processing, and

distribution that acts as a common point of connection between equipment and devices connected to a network of interconnected equipment, possessing greatest authority for allowing information to be exchanged, with whom other equipment is subordinate.

      - Microducts: All forms of air blown fiber pathways.

      - Ohm: A unit of restive measurement.

      - Received Signal Strength Indication (RSSI): A measurement of power present in a received RF signal.

      - Service Provider Demarcation Point (SPDP): Not owned by LEC or service provider but designated by Government as point within facility considered the DEMARC.

      - Sound (SND): Changing air pressure to audible signals over given time span.

      - System: Specific hardware, firmware, and software, functioning together as a unit, performing task for which it was designed.

      - Telecommunications Bonding Backbone (TBB): Conductors of appropriate size (minimum 53.49 mm2 [1/0 AWG]) stranded copper wire, that connect to Grounding Electrode System and route to telecommunications main grounding busbar (TMGB) and circulate to interconnect various TGBs and other locations shown on drawings.

      - Voice over Internet Protocol (VoIP): A telephone system in which voice signals are converted to packets and transmitted over LAN network using Transmission Control Protocol (TCP)/Internet Protocol (IP). VA’S VoIP is not listed or coded for life and public safety, critical, emergency or other protection functions. When VoIP system or equipment is provided instead of PBX system or equipment, each TR (STR) and DEMARC requires increased AC power provided to compensate for loss of PBX’s telephone instrument line power; and, to compensate for absence of PBX’s UPS capability.

      - Wide Area Network (WAN): A digital network that transcends localized LANs within a given geographic location. VA’S WAN/LAN is not nationally listed or coded for life and public safety, critical, emergency or other safety functions.

  - APPLICABLE PUBLICATIONS

    - Applicability of Standards: Unless documents include more stringent requirements, applicable construction industry standards have same force and effect as if bound or copied directly into the documents to

extent referenced. Such standards are made a part of these documents by reference.

      - Each entity engaged in construction must be familiar with industry standards applicable to its construction activity.

      - Obtain standards directly from publication source, where copies of standards are needed to perform the required construction activity.

    - Government Codes, Standards and Executive Orders: Refer to http://www.cfm.va.gov/TIL/cPro.asp:

      - Federal Communications Commission, (FCC) CFR, Title 47:

Part 15	Restrictions of use for Part 15 listed RF Equipment in Safety of Life Emergency Functions and Equipment Locations

Part 47	Chapter A, Paragraphs 6.1-6.23, Access to Telecommunications Service, Telecommunications Equipment and Customer Premises Equipment

Part 90	Rules and Regulations, Appendix C

Chapter XXIII	National Telecommunications and Information

Administration (NTIA, P/O Commerce, Chapter XXIII) the ‘Red Book’– Chapters 7, 8 & 9 compliments CFR, Title 47, FCC Part 15, RF Restriction of Use and Compliance in “Safety of Life” Functions & Locations

      - US Department of Agriculture, (Title 7, USC, Chapter 55, Sections 2201, 2202 & 2203:RUS 1755 Telecommunications Standards and Specifications for Materials, Equipment and Construction:

RUS Bull 1751F-640	Design of Buried Cable Plant, Physical

Considerations

RUS Bull 1751F-643	Underground Plant Design

RUS Bull 1751F-815	Electrical Protection of Outside Plants,

RUS Bull 1753F-201	Acceptance Tests of Telecommunications Plants

(PC-4)

RUS Bull 345-65	Shield Bonding Connectors (PE-65)

      - US Department of Commerce/National Institute of Standards Technology,(NIST):

FIPS 175	Federal Building Standard for Telecommunications Pathway and Spaces

| FIPS | 191 | Guideline for the Analysis of Local Area Network Security |
| --- | --- | --- |
| FIPS | 197 | Advanced Encryption Standard (AES) |
| FIPS | 199 | Standards for Security Categorization of |
|  |  | Federal Information and Information Systems |

      - US Department of Defense, (DoD):

MIL-STD-188-110	Interoperability and Performance Standards for

Data Modems

MIL-STD-188-114	Electrical Characteristics of Digital Interface

Circuits

MIL-STD-188-115	Communications Timing and Synchronizations

Subsystems

MIL-C-39012/21	Connectors, Receptacle, Electrical, Coaxial,

Radio Frequency, (Series BNC (Uncabled), Socket Contact, Jam Nut Mounted, Class 2)

      - US Department of Health and Human Services:

The Health Insurance Portability and Accountability Act of 1996 (HIPAA) Privacy, Security and Breach Notification Rules

      - US Department of Justice:

2010 Americans with Disabilities Act Standards for Accessible Design (ADAAD).

      - US Department of Labor, (DoL) - Public Law 426-62 – CFR, Title 29, Part 1910, Chapter XVII - Occupational Safety and Health Administration (OSHA), Occupational Safety and Health Standards):

Subpart 7	Approved NRTLs; obtain a copy at https://www.osha.gov/dts/otpca/nrtl/nrtllist.ht ml

Subpart 35	Compliance with NFPA 101, Life Safety Code Subpart 36	Design and Construction Requirements for Exit

Routes

Subpart 268	Telecommunications

Subpart 305	Wiring Methods, Components, and Equipment for

General Use

Subpart 508	Americans with Disabilities Act Accessibility

Guidelines; technical requirement for accessibility to buildings and facilities by individuals with disabilities

      - US Department of Veterans Affairs (VA): Office of Telecommunications (OI&T), MP-6, PART VIII, TELECOMMUNICATIONS, CHAPTER 5, AUDIO, RADIO AND TELEVISION (and COMSEC) COMMUNICATIONS SYSTEMS: Spectrum

Management and COMSEC Service (SMCS), AHJ for:

        - CoG, “Continuance of Government” communications guidelines and compliance.

        - COMSEC,“VA wide coordination and control of security classified communication assets.”

        - COOP, “Continuance of Operations” emergency communications guidelines and compliance.

        - FAA, FCC, and US Department of Commerce National Telecommunications and Information Administration, “VA wide RF Co-ordination, Compliance and Licensing.”

        - Handbook 6100 – Telecommunications: Cyber and Information Security Office of Cyber and Information Security, and Handbook 6500 – Information Security Program.

        - Low Voltage Special Communications Systems “Design, Engineering, Construction Contract Specifications and Drawings Conformity, Proof of Performance Testing, VA Compliance and Life Safety Certifications for CFM and VA Facility Low Voltage Special Communications Projects (except Fire Alarm, Telephone and Data Systems).”

        - VA’s CEOSH, concurrence with warning identified in VA Directive 7700.

        - Office of Security and Law Enforcement: VA Directive 0730 and Health Special Presidential Directive (HSPD)-12.

    - NRTL Standards: Refer to https://www.osha.gov/laws- regs/regulations/standardnumber/1926

      - Canadian Standards Association (CSA); same tests as presented by UL

      - Communications Certifications Laboratory (CEL); same tests as presented by UL.

      - Intertek Testing Services NA, Inc., (ITSNA), formerly Edison Testing Laboratory (ETL) same tests as presented by UL).

      - Underwriters Laboratory (UL):

1-2005	Flexible Metal Conduit

5-2011	Surface Metal Raceway and Fittings

6-2007	Rigid Metal Conduit

44-010	Thermoset-Insulated Wires and Cables

50-1995	Enclosures for Electrical Equipment

65-2010	Wired Cabinets

83-2008	Thermoplastic-Insulated Wires and Cables

96-2005	Lightning Protection Components

96A-2007	Installation Requirements for Lightning Protection Systems

360-2013	Liquid-Tight Flexible Steel Conduit

444-2008	Communications Cables

467-2013	Grounding and Bonding Equipment 486A-486B-2013	Wire Connectors

486C-2013	Splicing Wire Connectors

486D-2005	Sealed Wire Connector Systems

486E-2009	Standard for Equipment Wiring Terminals for Use

with Aluminum and/or Copper Conductors

493-2007	Thermoplastic-Insulated Underground Feeder and

Branch Circuit Cable

510-2005	Polyvinyl Chloride, Polyethylene and Rubber Insulating Tape

514A-2013	Metallic Outlet Boxes

514B-2012	Fittings for Cable and Conduit

651-2011	Schedule 40 and 80 Rigid PVC Conduit

797-2007	Electrical Metallic Tubing

1242-2006	Intermediate Metal Conduit

1449-2006	Standard for Transient Voltage Surge Suppressors

1479-2003	Fire Tests of Through-Penetration Fire Stops 1480-2003	Speaker Standards for Fire Alarm, Emergency,

Commercial and Professional use

1666-2007	Standard for Wire/Cable Vertical (Riser) Tray

Flame Tests

1685-2007	Vertical Tray Fire Protection and Smoke Release

Test for Electrical and Fiber Optic Cables

1861-2012	Communication Circuit Accessories

1863-2013	Standard for Safety, communications Circuits

Accessories

1865-2007	Standard for Safety for Vertical-Tray Fire

Protection and Smoke-Release Test for Electrical and Optical-Fiber Cables

2024-2014	Standard for Cable Routing Assemblies and

Communications Raceways

60950-1 ed. 2-2014	Information Technology Equipment Safety

    - Industry Standards:

      - American Institute of Architects (AIA): 2006 Guidelines for Design & Construction of Health Care Facilities.

      - American Society for Testing and Materials (ASTM):

B1 (2001)	Standard Specification for Hard-Drawn Copper

Wire

B8 (2004)	Standard Specification for Concentric-Lay-

Stranded Copper Conductors, Hard, Medium-Hard, or Soft

D1557 (2012)	Standard Test Methods for Laboratory Compaction

Characteristics of Soil Using Modified Effort 56,000 ft-lbf/ft3 (2,700 kN-m/m3)

D2301 (2004)	Standard Specification for Vinyl Chloride

Plastic Pressure Sensitive Electrical Insulating Tape

B258-02 (2008)	Standard Specification for Standard Nominal

Diameters and Cross-Sectional Areas of AWG Sizes of Solid Round Wires Used as Electrical Conductors

D709-01(2007)	Standard Specification for Laminated

Thermosetting Materials

D4566 (2008)	Standard Test Methods for Electrical

Performance Properties of Insulations and Jackets for Telecommunications Wire and Cable

      - Building Industry Consulting Service International(BICSI): ANSI/BICSI 004-2012 Information Technology Systems Design and

Implementation Best Practices for Healthcare Institutions and Facilities

ANSI/NECA/BICSI

568-2006	Standard for Installing Commercial Building Telecommunications Cabling

| NECA/BICSI | 607-2011 | Standard for Telecommunications Bonding and |
| --- | --- | --- |
|  |  | Grounding Planning and Installation Methods for |
|  |  | Commercial Buildings |
| ANSI/BICSI | 005-2013 | Electronic Safety and Security (ESS) System |
|  |  | Design and Implementation Best Practices |

      - Electronic Components Assemblies and Materials Association,(ECA). ECA EIA/RS-270 (1973)Tools, Crimping, Solderless Wiring Devices –

Recommended Procedures for User Certification EIA/ECA 310-E (2005) Cabinets, and Associated Equipment

      - Facility Guidelines Institute: 2010 Guidelines for Design and Construction of Health Care Facilities.

      - Insulated Cable Engineers Association (ICEA):ANSI/ICEA,ICEA S-102- 700 (2004)Category 6 Individually Unshielded Twisted Pair Indoor Cables (With or Without an Overall Shield) for use in Communications Wiring Systems Technical Requirements

      - Institute of Electrical and Electronics Engineers (IEEE): IEEE C2-2012	National Electrical Safety Code (NESC) C62.41.2-2002/

Cor 1-2012 IEEE	Recommended Practice on Characterization of

Surges in Low-Voltage (1000 V and Less) AC Power Circuits 4)

C62.45-2002	IEEE Recommended Practice on Surge Testing for

Equipment Connected to Low-Voltage (1000 V and Less) AC Power Circuits

81-2012 IEEE	Guide for Measuring Earth Resistivity, Ground

Impedance, and Earth Surface Potentials of a Grounding System

100-1992	IEEE the New IEEE Standards Dictionary of Electrical and Electronics Terms

602-2007	IEEE Recommended Practice for Electric Systems in Health Care Facilities

1100-2005	IEEE Recommended Practice for Powering and

Grounding Electronic Equipment

      - International Code Council:

AC193 (2014)	Mechanical Anchors in Concrete Elements

      - National Electrical Manufacturers Association (NEMA):

NEMA 250 (2008)	Enclosures for Electrical Equipment (1,000V

Maximum)

ANSI/NEMA FB 1 (2012)Fittings, Cast Metal Boxes and Conduit Bodies

for Conduit, Electrical Metallic Tubing EMT) and Cable

ANSI/NEMA OS 1 (2009)Sheet-Steel Outlet Boxes, Device Boxes, Covers,

and Box Supports

TC 3 (2004)	Polyvinyl Chloride (PVC) Fittings for Use with

Rigid PVC Conduit and Tubing

NEMA VE 2 (2006)	Cable Tray Installation Guidelines

      - National Fire Protection Association (NFPA):

70E-2015	Standard for Electrical Safety in the Workplace 70-2014	National Electrical Code (NEC)

72-2013	National Fire Alarm Code

77-2014	Recommended Practice on Static Electricity

99-2015	Health Care Facilities Code

101-2015	Life Safety Code

241	Safeguarding construction, alternation and Demolition Operations

255-2006	Standard Method of Test of Surface Burning Characteristics of Building Materials

262 - 2011	Standard Method of Test for Flame Travel and

Smoke of Wires and Cables for Use in Air- Handling Spaces

780-2014	Standard for the Installation of Lightning Protection Systems

1221-2013	Standard for the Installation, Maintenance, and

Use of Emergency Services Communications Systems

5000-2015	Building Construction and Safety Code

      - Telecommunications Industry Association (TIA):

TIA-120 Series	Telecommunications Land Mobile communications

(APCO/Project 25) (January 2014)

TIA-155	Guidelines for the Assessment and Mitigation of Installed Category 6 Cabling to Support

10GBASE-T (2010)

TIA/EIA-423-B	Electrical Characteristics of Unbalanced

Voltage Digital Interface Circuits (2012) TIA-472D000-B	Fiber Optic Communications Cable for Outside

Plant Use (July 2007)

TIA-492CAAA	Detail Specification for Class IVa Dispersion-

Unshifted Single-Mode Optical Fibers (September 2002)

TIA-492E000	Sectional Specification for Class IVd Nonzero-

Dispersion Single-Mode Optical Fibers for the 1,550 nm Window (September 2002)

TIA-526-7-B	Measurement of Optical Power Loss of Installed

Single-Mode Fiber Cable Plant – OFSTP-7 (December 2008)

TIA-568	Revision/Edition: C Commercial Building Telecommunications Cabling Standard Set: (TIA- 568-C.0-2 Generic Telecommunications Cabling for Customer Premises (2012), TIA-568-C.1-1 Commercial Building Telecommunications Cabling Standard Part 1: General Requirements (2012), TIA-568-C.2 Commercial Building Telecommunications Cabling Standard—Part 2: Balanced Twisted Pair Cabling Components (2009), TIA-568-C.3-1 Optical Fiber Cabling Components Standard, (2011) AND TIA-568-C.4 Broadband Coaxial Cabling and Components Standard (2011) with addendums and erratas

TIA-569	Revision/Edition C Telecommunications Pathways and Spaces (March 2013)

TIA-574	Position Non-Synchronous Interface between Data Terminal equipment and Data Circuit Terminating Equipment Employing Serial Binary Interchange (May 2003)

TIA/EIA-590-A	Standard for Physical Location and Protection

of Below Ground Fiber Optic Cable Plant (July 2001)

TIA-598-D	Optical Fiber Cable Color Coding (January 2005)

TIA-604-10-B	Fiber Optic Connector Intermateablility

Standard (August 2008)

ANSI/TIA-606-B	Administration Standard for Telecommunications

Infrastructure (2012)

TIA-607-B	Generic Telecommunications Bonding and Grounding (Earthing) For Customer Premises (January 2013)

TIA-613	High Speed Serial Interface for Data Terminal Equipment and Data Circuit Terminal Equipment (September 2005)

ANSI/TIA-758-B    Customer-owned Outside Plant Telecommunications

Infrastructure Standard (April 2012)

ANSI/TIA-854	A Full Duplex Ethernet Specification for 1000

Mb/s (1000BASE-TX) Operating over Category 6 Balanced Twisted-Pair Cabling (2001)

TIA-1152	Requirements for Field Testing Instruments and

Measurements for Balanced Twisted Pair Cabling (September 2009)

TIA-1179	Healthcare Facility Telecommunications Infrastructure Standard (July 2010)

  - SINGULAR NUMBER

    - Where any device or part of equipment is referred in singular number (such as " rack"), reference applies to as many such devices as are required to complete installation.

  - RELATED WORK

    - Specification Order of Precedence: FAR Clause 52.236-21, VAAR Clause 852.236-71.

      - Field Cutting and Patching: Section 09 91 00, PAINTING.

      - Additional submittal requirements: Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA AND SAMPLES.

      - Availability and source of references and standards specified in applicable publications: Section 01 42 19, REFERENCE STANDARDS.

      - Control of environmental pollution and damage for air, water, and land resources: Section 01 57 19, TEMPORARY ENVIRONMENTAL CONTROLS.

      - Requirements for non-hazardous building construction and demolition waste: Section 01 74 19, CONSTRUCTION WASTE MANAGEMENT.

      - General requirements and procedures to comply with various federal mandates and U.S. Department of Veterans Affairs (VA) policies for sustainable design: Section 01 81 13,SUSTAINABLE DESIGN REQUIREMENTS.

      - Closures of openings in walls, floors, and roof decks against penetration of flame, heat, and smoke or gases in fire resistant rated construction: Section 07 84 00, FIRESTOPPING.

      - Sealant and caulking materials and their application: Section 07 92 00, JOINT SEALANTS.

      - General requirements common to more than one section in Division 28: Section 28 05 00, COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND SECURITY.

      - Conductors and cables for electronic safety and security systems: Section 28 05 13, CONDUCTORS AND CABLES FOR ELECTRONIC SAFETY AND SECURITY.

      - Low impedance path to ground for electronic safety and security system ground fault currents: Section 28 05 26, GROUNDING AND BONDING FOR SECURITY SYSTEMS.

      - Conduits and partitioned telecommunications raceways for Electronic Safety and Security systems: Section 28 05 28.33, CONDUITS AND BACK BOXES FOR ELECTRONIC SAFETY AND SECURITY.

      - Video surveillance system cameras, data transmission wiring, and control stations with associated equipment: Section 28 23 00, VIDEO SURVEILLANCE EQUIPMENT AND SYSTEMS.

  - ADMINISTRATIVE REQUIREMENTS

    - Assign a single communications project manager to serve as point of contact for Government, contractor, and design professional.

    - Be proactive in scheduling work.

      - Use of premises is restricted at times directed by COR.

      - Movement of materials: Unload materials and equipment delivered to site. Pay costs for rigging, hoisting, lowering and moving equipment on and around site, in building or on roof.

      - Coordinate installation of required supporting devices and sleeves to be set in poured-in-place concrete and other structural components, as they are constructed.

      - Sequence, coordinate, and integrate installations of materials and equipment for efficient flow of Work.

      - Coordinate connection of materials, equipment, and systems with exterior underground and overhead utilities and services. Comply with requirements of governing regulations, franchised service companies, and controlling agencies; provide required connection for each service.

      - Initiate and maintain discussion regarding schedule for ceiling construction and install cables to meet that schedule.

    - Contact the Office of Telecommunications, Special Communications Team (005OP2H3) (202)461-5310 to have a Government-accepted Telecommunications COR assigned to project for telecommunications review, equipment and system approval and coordination with other VA personnel.

    - Communications Project Manager Responsibilities:

      - Assume responsibility for overall telecommunications system integration and coordination of work among trades, subcontractors, and authorized system installers.

      - Coordinate with related work indicated on drawings or specified.

      - Manage work related to telecommunications system installation in a manner approved by manufacturer.

  - SUBMITTALS

    - Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

    - Provide parts list including quantity of spare parts.

    - Provide manufacturer product information. Government reserves the right to require a list of installations where products have been in operation.

    - Provide Source Quality Control Submittal:

      - Submit written certification from OEM indicating that proposed supervisor of installation and proposed provider of warranty maintenance are authorized representatives of OEM. Include individual's legal name, contact information and OEM credentials in certification.

      - Submit written certification from OEM that wiring and connection diagrams meet Government Life Safety Guidelines, NFPA, NEC, NRTL, these specifications, and Joint Commission requirements and instructions, requirements, recommendations, and guidance set forth by OEM for the proper performance of system.

      - Pre-acceptance Certification: Certification in accordance with procedure outlined in Section 01 00 00, GENERAL REQUIREMENTS and specific Division 27 qualification documentation.

    - Installer Qualifications: Submit three installations of similar size and complexity furnished and installed by installer; include:

      - Installation location and name.

      - Owner’s name and contact information including, address, telephone and email.

      - Date of project start and date of final acceptance.

      - System project number.

      - Three paragraph description of each system related to this project; include function, operation, and installation.

    - Provide delegated design submittals (e.g. seismic support design).

    - Submittals are required for all equipment anchors and supports. Include weights, dimensions, center of gravity, standard connections, manufacturer's recommendations and behavior problems (e.g., vibration, thermal expansion,) associated with equipment or conduit. Anchors and supports to resist seismic load based on seismic design categories per section 4.0 of VA seismic design requirements H-18-8 dated August, 2013.

    - Test Equipment List:

      - Supply test equipment of accuracy better than parameters to be tested.

      - Submit test equipment list including make and model number:

        - ANSI/TIA-1152 Level IV twisted pair cabling test instrument.

        - Fiber optic insertion loss power meter with light source.

        - Optical time domain reflectometer (OTDR).

        - Volt-Ohm meter.

        - Digital camera.

        - Bit Error Test Set (BERT).

        - Signal level meter.

        - Time domain reflectometer (TDR) with strip chart recorder (Data and Optical Measuring).

        - Spectrum analyzer.

        - Color video monitor with audio capability.

        - Video waveform monitor.

        - Video vector scope

        - 100 MHz oscilloscope with video adapters.

      - Supply only test equipment with a calibration tag from Government- accepted calibration service dated not more than 12 months prior to test.

      - Provide sample test and evaluation reports.

    - Submittal Drawings:

      - Telecommunications Space Plans/Elevations: Provide enlarged floor plans of telecommunication spaces indicating layout of equipment and devices, including receptacles and grounding provisions. Submit detailed plan views and elevations of telecommunication spaces showing racks, termination blocks, and cable paths. Include following rooms:

        - Telecommunications rooms.

        - Building Entrance Facility/Demarcation rooms.

      - Logical Drawings: Provide logical riser or schematic drawings for all systems.

        - Provide riser diagrams systems and interconnection drawings for equipment assemblies; show termination points and identify wiring connections.

      - Access Panel Schedule on Submittal Drawings: Coordinate and prepare a location, size, and function schedule of access panels required to fully service equipment.

    - Provide sustainable design submittals.

    - Furnish electronic certified test reports to COR prior to final inspection and not more than 90 days after completion of tests.

  - CLOSEOUT SUBMITTALS

    - Provide following closeout submittals prior to project closeout date:

      - Warranty certificate.

      - Evidence of compliance with requirements such as low voltage certificate of inspection.

      - Project record documents.

      - Instruction manuals and software that are a part of system.

    - Maintenance and Operation Manuals: Submit in accordance with Section 01 00 00, GENERAL REQUIREMENTS.

      - Prepare a manual for each system and equipment specified.

      - Furnish on portable storage drive in PDF format or equivalent accepted by COR.

      - Furnish complete manual as specified in specification section, fifteen days prior to performance of systems or equipment test.

      - Furnish remaining manuals prior to final completion.

      - Identify storage drive "MAINTENANCE AND OPERATION MANUAL" and system name.

      - Include name, contact information and emergency service numbers of each subcontractor installing system or equipment and local representatives for system or equipment.

      - Provide a Table of Contents and assemble files to conform to Table of Contents.

      - Operation and Maintenance Data includes:

        - Approved shop drawing for each item of equipment.

        - Internal and interconnecting wiring and control diagrams with data to explain detailed operation and control of equipment.

        - A control sequence describing start-up, operation, and shutdown.

        - Description of function of each principal item of equipment.

        - Installation and maintenance instructions.

        - Safety precautions.

        - Diagrams and illustrations.

        - Test Results and testing methods.

        - Performance data.

        - Pictorial "exploded" parts list with part numbers. Emphasis to be placed on use of special tools and instruments. Indicate sources of supply, recommended spare parts, and name of servicing organization.

        - Warranty documentation indicating end date and equipment protected under warranty.

        - Appendix; list qualified permanent servicing organizations for support of equipment, including addresses and certified personnel qualifications.

    - Record Wiring Diagrams:

      - Red Line Drawings: Keep one E size 91.44 cm x 121.92 cm (36 inches x 48 inches) set of floor plans, on site during work hours, showing installation progress marked and backbone cable labels noted. Make these drawings available for examination during construction meetings or field inspections.

      - General Drawing Specifications: Detail and elevation drawings to be D size 61 cm x 91.44 cm (24 inches x 36 inches) with a minimum scale of 0.635 cm = 30.48 cm (1/4 inch = 12 inches). ER, TR and other enlarged detail floor plan drawings to be D size 61 cm x 91.44 cm (24” x 36”) with a minimum scale of 0.635 cm = 30.48 cm (1/4 inch = 12 inches). Building composite floor plan drawings to be D size 61 cm x 91.44 cm (24 inches x 36 inches) with a minimum scale of 3.175 mm = 30.48 cm (1/8 inch = 1’ 0 inch).

      - Building Composite Floor Plans: Provide building floor plans showing work area outlet locations and configuration, types of jacks, distance for each cable, and cable routing locations.

      - Floor plans to include:

        - Final room numbers and actual backbone cabling and pathway locations and labeling.

        - Inputs and outputs of equipment identified according to labels installed on cables and equipment

        - Device locations with labels.

        - Conduit.

        - Head-end equipment.

        - Wiring diagram.

        - Labeling and administration documentation.

      - Submit Record Wiring Diagrams within five business days after final cable testing.

      - Deliver Record Wiring Diagrams as CAD files in .dwg formats as determined by COR.

      - Deliver four complete sets of electronic record wiring diagrams to COR on portable storage drive.

    - Service Qualifications: Submit name and contact information of service organizations providing service to this installation within // four hours of receipt of notification service is needed.

  - MAINTENANCE MATERIAL SUBMITTALS

    - After approval and prior to installation, furnish COR with the following:

      - A 300 mm (12 inch) length of each type and size of wire and cable along with tag from coils of reels from which samples were taken.

      - One coupling, bushing and termination fitting for each type of conduit.

      - Samples of each hanger, clamp and supports for conduit and pathways.

      - Duct sealing compound.

  - QUALITY ASSURANCE

    - Manufacturer’s Qualifications: Manufacturer must produce, as a principal product, the equipment and material specified for this project and have manufactured item for at least three years.

    - Product and System Qualification:

      - OEM must have three installations of equipment submitted presently in operation of similar size and type as this project, that have continuously operated for a minimum of three years.

      - Government reserves the right to require a list of installations where products have been in operation before approval.

      - Authorized representative of OEM must be responsible for design, satisfactory operation of installed system, and certification.

    - Trade Contractor Qualifications: Trade contractor must have completed three or more installations of similar systems of comparable size and complexity with regards to coordinating, engineering, testing, certifying, supervising, training, and documentation. Identify these installations as a part of submittal.

    - System Supplier Qualifications: System supplier must be authorized by OEM to warranty installed equipment.

    - Telecommunications technicians assigned to system must be trained and certified by OEM on installation and testing of system; provide written evidence of current OEM certifications for installers.

    - Manufactured Products:

      - Comply with FAR clause 52.236-5 for material and workmanship.

      - When more than one unit of same class of equipment is required, units must be product of a single manufacturer.

      - Equipment Assemblies and Components:

        - Components of an assembled unit need not be products of same manufacturer.

        - Manufacturers of equipment assemblies, which include components made by others, to assume complete responsibility for final assembled unit.

        - Provide compatible components for assembly and intended service.

        - Constituent parts which are similar must be product of a single manufacturer.

      - Identify factory wiring on equipment being furnished and on wiring diagrams.

    - Testing Agencies: Government reserves the option of witnessing factory tests. Notify COR minimum 15 working days prior to manufacturer performing the factory tests.

      - When equipment fails to meet factory test and re-inspection is required, contractor is liable for additional expenses, including expenses of Government.

  - DELIVERY, STORAGE, AND HANDLING

    - Delivery and Acceptance Requirements:

      - Government's approval of submittals must be obtained for equipment and material before delivery to job site.

      - Deliver and store materials to job site in OEM's original unopened containers, clearly labeled with OEM's name and equipment catalog numbers, model and serial identification numbers for COR to inventory cable, patch panels, and related equipment.

    - Storage and Handling Requirements:

      - Equipment and materials must be protected during shipment and storage against physical damage, dirt, moisture, cold and rain:

        - Store and protect equipment in a manner that precludes damage or loss, including theft.

        - Protect painted surfaces with factory installed removable heavy kraft paper, sheet vinyl or equivalent.

        - Protect enclosures, equipment, controls, controllers, circuit protective devices, and other like items, against entry of foreign matter during installation; vacuum clean both inside and outside before testing and operating.

    - Coordinate storage.

  - FIELD CONDITIONS

    - Where variations from documents are requested in accordance with GENERAL CONDITIONS and Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA,

AND SAMPLES, connecting work and related components must include additions or changes to branch circuits, circuit protective devices, conduits, wire, feeders, controls, panels and installation methods.

    - A contract adjustment or additional time will not be granted because of field conditions pursuant to FAR 52.236-2 and FAR 52.236-3; a contract adjustment or additional time will not be granted for additional work

required for complete and usable construction and systems pursuant to FAR 52.246-12.

  - WARRANTY

    - Comply with FAR clause 52.246-21, except as follows:

      - Warranty material and equipment to be free from defects, workmanship, and remain so for a period of one year for Emergency Systems from date of final acceptance of system by Government; provide OEM’s equipment warranty document to COR.

      - Government maintenance personnel must have ability to contact OEM for emergency maintenance and logistic assistance, remote diagnostic testing, and assistance in resolving technical problems at any time; contractor and OEM must provide this capability.

      - Provide five (5) year extended maintenance plan and service agreement for support of the closed-circuit television (TVSS) in accordance with Government request.

PART 2 - PRODUCTS

  - PERFORMANCE AND DESIGN CRITERIA

    - Provide communications spaces and pathways conforming to TIA 569, at a minimum.

    - In cases of renovations in historic or otherwise restrictive buildings, where it has been determined as impossible to follow above stated guidelines, exceptions must not modify maximum distances set forth in TIA 568 and 569; and exceptions must not in any way effect performance of entire TIP system.

    - Modification to administrative issues requires written approvals from COR with concurrence from SMCS 005OP2H3, OEM, contractor, and local authorities.

  - EQUIPMENT IDENTIFICATION

    - Provide laminated black phenolic resin with a white core nameplates with minimum 6 mm (1/4 inch) high engraved lettering.

    - Nameplates furnished by manufacturer as standard catalog items, unless other method of identification is indicated.

  - UNDERGROUND WARNING TAPE

    - Underground Warning: Standard 4-Mil polyethylene 76 mm (3 inch) wide tape detectable type; red with black letters imprinted with “CAUTION BURIED ELECTRIC LINE BELOW”, orange with black letters imprinted with

“CAUTION BURIED TELEPHONE LINE BELOW” or orange with black letters imprinted with “CAUTION BURIED FIBER OPTIC LINE BELOW”, as applicable.

  - WIRE LUBRICATING COMPOUND

    - Provide non-hardening or forming adhesive coating cable lubricants suitable for cable jacket material and raceway.

  - FIREPROOFING TAPE

    - Provide flexible, conformable fabric tape of organic composition and coated one side with flame-retardant elastomer.

    - Tape must be self-extinguishing and cannot support combustion; arc- proof and fireproof.

    - Tape cannot deteriorate when subjected to water, gases, salt water, sewage, or fungus; and tape must be resistant to sunlight and ultraviolet light.

    - Application must withstand a 200-ampere arc for minimum 30 seconds.

    - Securing Tape: Glass cloth electrical tape minimum 0.18 mm (7 mils) thick and 19 mm (3/4 inch) wide.

  - ACCESS PANELS

    - Panels: 304 mm x 304 mm (12 inches by 12 inches), or size allowed by location to provide optimum access to equipment for maintenance and service.

    - Provide access panels and doors as required to allow service of materials and equipment that require inspection, replacement, repair or service.

    - Provide access panels where items installed require access and are concealed in floor, wall, furred space or above ceiling; ceilings consisting of lay-in or removable splined tiles do not require access panels.

    - Provide access panels with same fire rating classification as surface penetrated.

PART 3 - EXECUTION

  - PREPARATION

    - Penetrations and Sleeves:

      - Lay out penetration and sleeve openings in advance, to permit provision in work.

      - Provide sleeves and packing materials at penetrations of foundations, walls, slabs, partitions, and floors.

      - Make sleeves that penetrate outside walls, basement slabs, footings, and beams waterproof.

      - Fill slots, sleeves and other openings in floors or walls if not used.

        - Fill spaces in openings after installation of conduit or cable.

        - Provide fill for floor penetrations to prevent passage of water, smoke, fire, and fumes.

        - Provide fire resistant fill in rated floors and walls, to prevent passage of air, smoke and fumes.

      - Match and set sleeves flush with adjoining floor, ceiling, and wall finishes where raceways passing through openings are exposed in finished rooms.

      - Annular space between conduit and sleeve must be minimum 6 mm (1/4 inch).

      - Comply with requirements for firestopping, for sleeves through rated fire walls and smoke partitions.

      - Do not support piping risers or conduit on sleeves.

      - Identify unused sleeves and slots for future installation.

      - Provide core drilling if walls are poured or otherwise constructed without sleeves and wall penetration is required; do not penetrate structural members.

    - Core Drilling:

      - Avoid core drilling whenever possible.

      - Coordinate openings with other trades and utilities and prevent damage to structural reinforcement.

      - Investigate existing conditions in vicinity of required opening prior to coring, including an x-ray of floor if determined necessary by competent person or COR.

      - Protect areas from damage.

    - Verification of In-Place Conditions:

      - Verify location, use and status of all material, equipment, and utilities that are specified, indicated, or determined necessary for removal.

        - Verify materials, equipment, and utilities to be removed are inactive, not required, or in use after completion of project.

        - Replace with equivalent any material, equipment and utilities that were removed by contractor that are required to be left in place.

      - Existing Utilities: Do not interrupt utilities serving facilities occupied by Government or others unless permitted under following conditions and then only after arranging to provide temporary utility services, according to requirements indicated:

        - Notify COR in writing at least 14 days in advance of proposed utility interruptions.

        - Do not proceed with utility interruptions without Government’s written permission.

    - Provide suspended platforms, strap hangers, brackets, shelves, stands or legs for floor, wall and ceiling mounting of equipment as required.

    - Provide steel supports and hardware for installation of hangers, anchors, guides, and other support hardware.

    - Obtain and analyze catalog data, weights, and other pertinent data required for coordination of equipment support provisions and installation.

    - Verify site conditions and dimensions of equipment to ensure access for proper installation of equipment without disassembly that would void warranty.

  - INSTALLATION - GENERAL

    - Coordinate systems, equipment, and materials installation with other building components.

    - Install systems, materials, and equipment to conform with approved submittal data, including coordination drawings.

    - Conform to VAAR 852.236.91 arrangements indicated, recognizing that work may be shown in diagrammatic form or have been impracticable to detail all items because of variances in manufacturers’ methods of achieving specified results.

    - Install systems, materials, and equipment level and plumb, parallel and perpendicular to other building systems and components, where installed in both exposed and un-exposed spaces.

    - Install equipment according to manufacturers' written instructions.

    - Install wiring and cabling between equipment and related devices.

    - Install cabling, wiring, and equipment to facilitate servicing, maintenance, and repair or replacement of equipment components. Connect

equipment for ease of disconnecting, with minimum interference of adjacent other installations.

    - Provide access panel or doors where units are concealed behind finished surfaces.

    - Arrange for chases, slots, and openings in other building components during progress of construction, to allow for wiring, cabling, and equipment installations.

    - Where mounting heights are not detailed or dimensioned, install systems, materials, and equipment to provide maximum headroom and access for service and maintenance as possible.

    - Install systems, materials, and equipment giving priority to systems required to be installed at a specified slope.

    - Avoid interference with structure and with work or other trades, preserving adequate headroom and clearing doors and passageways to satisfaction of COR and code requirements.

    - Install equipment and cabling to distribute equipment loads on building structural members provided for equipment support under other sections; install and support roof-mounted equipment on structural steel or roof curbs as appropriate.

    - Provide supplementary or miscellaneous items, appurtenances, devices and materials for a complete installation.

  - EQUIPMENT INSTALLATION

    - Locate equipment as close as practical to locations shown on drawings.

    - Note locations of equipment requiring access on record drawings.

    - Access and Access Panels: Verify access panel locations and construction with COR.

    - Inaccessible Equipment:

      - Where Government determines that contractor has installed equipment not conveniently accessible for operation and maintenance, equipment must be removed and reinstalled as directed and without additional cost to Government.

  - EQUIPMENT IDENTIFICATION

    - Install an identification sign which clearly indicates information required for use and maintenance of equipment.

    - Secure identification signs with screws.

  - CUTTING AND PATCHING

    - Perform cutting and patching according to contract general requirements and as follows:

      - Remove samples of installed work as specified for testing.

      - Perform cutting, fitting, and patching of equipment and materials required to uncover existing infrastructure in order to provide access for correction of improperly installed existing or new work.

      - Remove and replace defective work.

    - Cut, remove, and legally dispose of selected equipment, components, and materials, including removal of material, equipment, devices, and other items indicated to be removed and items made obsolete by new work.

    - Provide and maintain temporary partitions or dust barriers adequate to prevent spread of dust and dirt to adjacent areas.

    - Protect adjacent installations during cutting and patching operations.

    - Protect structure, furnishings, finishes, and adjacent materials not indicated or scheduled to be removed.

    - Patch finished surfaces and building components using new materials specified for original installation and experienced installers.

  - FIELD QUALITY CONTROL

    - Provide work according to VAAR 852.236.91 and FAR clause 52.236-5.

    - Provide minimum clearances and work required for compliance with NFPA 70, National Electrical Code (NEC), and manufacturers' instructions; comply with additional requirements indicated for access and clearances.

    - Verify all field conditions and dimensions that affect selection and provision of materials and equipment, and provide any disassembly, reassembly, relocation, demolition, cutting and patching required to provide work specified or indicated, including relocation and reinstallation of existing wiring and equipment.

      - Protect facility, equipment, and wiring from damage.

    - Submit written notice that:

      - Project has been inspected for compliance with documents.

      - Work has been completed in accordance with documents.

    - Non-Conforming Work: Conduct project acceptance inspections, final completion inspections, substantial completion inspections, and acceptance testing and demonstrations after verification of system operation and completeness by Contractor.

    - For project acceptance inspections, final completion inspections, substantial completion inspections, and testing/demonstrations that require more than one site visit by COR or design professional to verify project compliance for same material or equipment, Government reserves right to obtain compensation from contractor to defray cost of additional site visits that result from project construction or testing deficiencies and incompleteness, incorrect information, or non- compliance with project provisions.

      - COR will notify contractor, of hourly rates and travel expenses for additional site visits and will issue an invoice to Contractor for additional site visits.

      - Contractor is not eligible for extensions of project schedule or additional charges resulting from additional site visits that result from project construction or testing deficiencies/incompleteness, incorrect information, or non-compliance with Project provisions.

    - Tests:

      - Interim inspection is required at approximately 50 percent of installation.

      - Request inspection ten working days prior to interim inspection start date by notifying COR in writing; this inspection must verify equipment and system being provided adheres to installation, mechanical and technical requirements of construction documents.

      - Inspection to be conducted by OEM and factory-certified contractor representative, and witnessed by COR, facility and SMCS 0050P2H3 representatives.

      - Check each item of installed equipment to ensure appropriate NRTL listing labels and markings are fixed in place.

      - Verify cabling terminations in MCR, TRs and head end rooms, workstation locations and TCO adhere to color code for // T568B pin assignments and cabling connections are in compliance with TIA standards.

      - Visually confirm minimum Category 6A cable marking at TCOs, CCSs locations, patch cords and origination locations.

      - Review entire communications circulating ground system, each TGB and grounding connection, grounding electrode and outside lightning protection system.

      - Review cable tray, conduit and path/wire way installation practice.

      - OEM and contractor to perform:

        - Fiber optical cable field inspection tests via attenuation measurements on factory reels; provide results along with OEM certification for factory reel tests.

        - Baseband cable field inspection tests via attenuation measurements on factory reels and provide results along with OEM certification for factory reel tests.

      - Relocate failed cable reels to a secured location for inventory, as directed by COR, and then remove from project site within two working days; provide COR with written confirmation of defective cable reels removal from project site.

      - Provide results of interim inspections to COR.

      - If major or multiple deficiencies are discovered, additional interim inspections could be required until deficiencies are corrected, before permitting further system installation.

        - Additional inspections are scheduled at direction of COR.

        - Re-inspection of deficiencies noted during interim inspections must be part of system’s Final Acceptance Proof of Performance Test.

        - The interim inspection cannot affect the system’s completion date unless directed by COR.

      - Facility COR will ensure test documents become a part of system’s official documentation package.

    - Pretesting: Re-align, re-balance, sweep, re-adjust and clean entire system and leave system working for a “break-in” period, upon completing installation of system and prior to Final Acceptance Proof of Performance Test. System RF transmitting equipment must not be connected to keying or control lines during “break-in” period.

      - Pretesting Procedure:

        - Verify systems are fully operational and meet performance requirements, utilizing accepted test equipment and spectrum analyzer.

        - Pretest and verify system functions and performance requirements conform to construction documents and, that no unwanted physical, aural and electronic effects, such as signal distortion, noise pulses, glitches, audio hum, poling noise are present.

    - Acceptance Test:

      - Schedule an acceptance test date after system has been pretested, and pretest results and certification submitted to COR.

      - Give COR fifteen working days written notice prior to date test is expected to begin; include expected duration of time for test in notification.

      - Test in the presence of the following:

        - COR.

        - OEM representatives.

        - VACO:

          - CFM representative.

          - AHJ–SMCS 005OP2H3, (202)461-5310.

        - VISN–CIO, Network Officer and VISN representatives.

        - Facility:

          - FMS Service Chief, Bio-Medical Engineering and facility representatives.

          - OI&T Service Chief and OI&T representatives.

          - Safety Officer, Police Chief and facility safety representatives.

        - Local Community Safety Personnel:

          - EMS Representatives: Police, Sherriff, City, County or State representatives.

      - Test system utilizing accepted test equipment to certify proof of performance and Life and Public Safety compliance, FCC, NRTL, NFPA and OSHA compliance.

        - Rate system as acceptable or unacceptable at conclusion of test; make only minor adjustments and connections required to show proof of performance.

          - Demonstrate and verify that system complies with performance requirements under operating conditions.

          - Failure of any part of system that precludes completion of system testing, and which cannot be repaired within four hours, terminates acceptance test of that portion of system.

          - Repeated failures that result in a cumulative time of eight hours to affect repairs is cause for entire system to be declared unacceptable.

          - If system is declared unacceptable, retesting must be rescheduled at convenience of Government and costs borne by the contractor.

    - Acceptance Test Procedure:

      - Physical and Mechanical Inspection: The test team representatives must tour major areas to determine system and sub-systems are completely and properly installed and are ready for acceptance testing.

      - A system inventory including available spare parts must be taken at this time.

      - Each item of installed equipment must be re-checked to ensure appropriate NRTL (i.e. UL) certification listing labels are affixed.

      - Confirm that deficiencies reported during Interim Inspections and Pretesting are corrected prior to start of Acceptance Test.

      - Inventory system diagrams, record drawings, equipment manuals, pretest results.

      - Failure of system to meet installation requirements of specifications is grounds for terminating testing and to schedule re-testing.

    - Operational Test:

      - Government’s Condition of Acceptance of System Language:

        - Without Acceptance: Until system fully meets conditions of construction documents, system’s ownership, use, operation and warranty commences at Government’s final acceptance date.

        - With Conditional Acceptance: Stating conditions that need to be addressed by contractor or OEM and stating system’s use and operation to commence immediately while its warranty commences only at Government’s agreed final extended acceptance date.

        - With Full Acceptance: Stating system’s ownership, use, operation and warranty to immediately commence at Government’s agreed to date of final acceptance.

    - Acceptance Test Conclusion: Reschedule testing on deficiencies and shortages with COR, after COR and SMCS AHJ jointly agree to results of the test, using the generated punch list or discrepancy list. Perform retesting to comply with these specifications at contractor's expense.

    - Proof of Performance Certification:

      - If system is declared acceptable, AHJ (SMCS 005OP2H3) provides COR notice stating system processes to required operating standards and functions and is Government accepted for use by facility.

      - Validate items with COR needing to be provided to complete project contract (i.e. charts & diagrams, manuals, spare parts, system warranty documents executed, etc.). Once items have been provided, COR contacts FMS service chief to turn over system from CFM oversight for beneficial use by facility.

      - If system is declared unacceptable without conditions, rescheduled testing expenses are to be borne by contractor.

  - CLEANING

    - Remove debris, rubbish, waste material, tools, construction equipment, machinery and surplus materials from project site and clean work area, prior to final inspection and acceptance of work.

    - Put building and premises in neat and clean condition.

    - Remove debris on a daily basis.

    - Remove unused material, during progress of work.

    - Perform cleaning and washing required to provide acceptable appearance and operation of equipment to satisfaction of COR.

    - Clean exterior surface of all equipment, including concrete residue, dirt, and paint residue, after completion of project.

    - Perform final cleaning prior to project acceptance by COR.

    - Remove paint splatters and other spots, dirt, and debris; touch up scratches and mars of finish to match original finish.

    - Clean devices internally using methods and materials recommended by manufacturer.

    - Tighten wiring connectors, terminals, bus joints, and mountings, to include lugs, screws and bolts according to equipment manufacturer’s published torque tightening values for equipment connectors. In absence of published connection or terminal torque values, comply with torque values specified in UL 486A-486B.

  - TRAINING

    - Provide training in accordance with subsection, INSTRUCTIONS, of Section 01 00 00, GENERAL REQUIREMENTS.

    - Provide training for equipment or system as required in each associated specification.

    - Develop and submit training schedule for approval by COR, at least 30 days prior to planned training.

  - PROTECTION

    - Protection of Fireproofing:

      - Install clips, hangers, clamps, supports and other attachments to surfaces to be fireproofed, if possible, prior to start of spray fireproofing work.

      - Install conduits and other items that would interfere with proper application of fireproofing after completion of spray fire proofing work.

      - Patch and repair fireproofing damaged due to cutting or course of work must be performed by installer of fireproofing and paid for by trade responsible for damage.

    - Maintain equipment and systems until final acceptance.

    - Ensure adequate protection of equipment and material during installation and shutdown and during delays pending final test of systems and equipment because of seasonal conditions.

- - - E N D - - -

SECTION 27 05 26

GROUNDING AND BONDING FOR COMMUNICATIONS SYSTEMS

PART 1 - GENERAL

  - DESCRIPTION

## This section specifies grounding and bonding requirements of communications installations based on the requirements of ANSI/TIA-607-D, Telecommunications Bonding and Grounding (Earthing) for Customer Premises. Work covered by this Section shall consist of furnishing supplies, labor, materials, equipment, labeling, and tools. Testing is required unless otherwise specified. An operable grounding and bonding infrastructure is required as described on the Drawings and/or required by these specifications. All materials shall be listed by a nationally recognized testing laboratory (NRTL).

  - SUMMARY

## Section Includes:

## Required Bonding Busbars.

## Telecommunications Bonding Conductors.

## Joining Requirements.

## Overvoltage Surge Protectors.

  - REFERENCES

## VA Infrastructure Standard for Telecommunications Spaces.

## ANSI/TIA-607-D, Telecommunications Bonding and Grounding (Earthing) for Customer Premises.

## NFPA 70, National Electrical Code (NEC).

## International Annealed Copper Standard (IACS).

## BICSI Information Technology Systems Installation Methods Manual (ITSIMM), 8th Edition, Recommended Testing Procedures and Criteria.

## UL 497 & UL 497A, UL Standards for Primary & Secondary Safety Protectors for Paired-Conductor Communications Circuits.

  - RELATED WORK

## Sealing around penetrations to maintain integrity of fire rated construction: Section 07 84 00, FIRESTOPPING.

## Fabrications for deflection of water away from building envelope at penetrations: Section 07 60 00, FLASHING AND SHEET METAL.

## Sealing around conduit penetrations through building envelope to prevent moisture migration into building: Section 07 92 00, JOINT SEALANTS.

## Identification and painting of conduit and other devices: Section 09 91 00, PAINTING.

## Requirements for Communications Installations: Section 27 05 11, REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS.

## Cable trays: Section 27 05 36, CABLE TRAYS FOR COMMUNICATIONS SYSTEMS.

## Excavation: Section 31 20 00, EARTH MOVING.

  - SUBMITTALS

## Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

## Provide riser diagram indicating location of communications grounding system connections indicating routing of grounding conductors.

## Closeout Submittals: Provide test reports of ground resistance to each primary or secondary bonding busbar (PBB/SBB) located in each telecommunications space impacted by the work.

PART 2 - PRODUCTS

  - BONDING BUSBARS.

## Bonding busbars are located in each telecommunications space and in each network rack/cabinet. Bonding busbars provide common locations in the telecommunications space for the connection of the telecommunications bonding conductors.

## Common Requirements.

## Provided with holes for use with correctly matched UL Listed two-hole lugs and hardware.

## Constructed of copper or copper alloy with a minimum of 95% conductivity when annealed.

## Annealed as specified by the International Annealed Copper Standard (IACS).

## Installation resulting in a maximum 4.0Ω to ground resistance measured from any point in the system.

## Installation is insulated from the mounting surface through the use of appropriate insulators.

## UL Listed.

## Primary Bonding Busbar (PBB). The PBB is a dedicated extension of the building grounding electrode system for the telecommunications infrastructure. The PBB also serves as the central attachment point for Secondary Bonding Busbars (SBB) via Telecommunications Bonding Backbone (TBB).

## Pre-drilled copper with holes to accommodate lug mounting holes.

## Sized for current applications and future growth.

## Insulated from its supports.

## Electro-tin plated is acceptable.

## Maintain a 2” min clearance between busbar and finished wall.

## Size must be 0.25” thick by 4” wide by 20” length.

## Secondary Bonding Busbar (SBB). The SBB is a common point of connection for telecommunications system and equipment bonding to a ground located in each Telecommunications Room.

## Pre-drilled holes to accommodate dual lug mounting holes.

## 0.25” thick x 2” wide with varying length to be sized for current applications and future growth.

## Maintain a 2” min clearance between the finished wall and busbar.

## Copper or tin annealed copper.

## Rack Bonding Busbar (RBB). The RBB is a busbar located in a cabinet, rack, or frame.

## Mounting. Horizontal mounting to an EIA-310-D 19” equipment rack is specified.

## Capacity: 10 Double-hole lugs.

## Size & material 0.75” wide x 19” length x 0.25” thick – Copper or tin annealed copper.

  - TELECOMMUNICATIONS BONDING BACKBONE (TBB).

## The TBB bonds the facility Primary Bonding Busbar (PBB) to telecommunications space Secondary Bonding Busbars (SBBs).

## Material. Stranded copper wire with a green jacket (or per NEC depending on size), run as a continuous conductor.

## Size. The TBB shall be sized to meet the requirements of ANSI/TIA-607-D and will be as straight as practicable avoiding bends.

## Bonding the TBB to the PBB and each SBB will require a UL Listed irreversible compression (crimp) dual-lug connector.

  - BONDING CONDUCTORS.

## Telecommunications Equipment Bonding Conductor (TEBC). The TEBC connects the cabinets and racks in the

## telecommunications space to the space’s bonding busbar (PBB or SBB).

## Material. Stranded copper wire with a green jacket (or per NEC depending on size), run as a continuous conductor.

## Size. The TBB shall be sized to meet the requirements of ANSI/TIA-607-D. The minimum size for the TEBC shall be AWG 6.

## Bonding. Bonded to the telecommunications space bonding busbar (PBB or SBB) via a UL Listed two-hole compression lug. Rack Bonding Conductors (RBCs) are connected to the TEBC using UL Listed irreversible compression (crimp) connectors.

## Rack Bonding Conductor (RBC). The RBC is a bonding conductor from the cabinet or Rack Bonding Busbar (RBB) to the Telecommunications Equipment Bonding Conductor (TEBC).

## Material. Stranded copper wire with a green jacket run as a continuous conductor.

## Size. The minimum size for the RBC shall be AWG 6.

## Bonding. Bonded to the Telecommunications Equipment Bonding Conductor (TEBC) using UL Listed irreversible compression (crimp) connectors.

## Where connected to a server cabinet, the RBC extends to the bottom of the server cabinet allowing Equipment Bonding Conductors to be attached at any point in the cabinet.

## Where connected to a network rack/cabinet, the Rack Bonding Conductor (RBC) is bonded to the Rack Bonding Busbar (RBB) via a UL Listed two-hole compression lug.

## Equipment/Unit Bonding Conductor (EBC/UBC). The Equipment/Unit Bonding Conductor connects individual

## equipment in a cabinet or rack to the Rack Bonding Conductor (RBC) or Rack Bonding Busbar (RBB). Equipment Bonding conductors are also used as cable tray bonding conductors to bond cable tray sections to the Telecommunications Equipment Bonding Conductor (TEBC).

## Material. Stranded copper wire with a green jacket run as a continuous conductor.

## Size. The minimum size for the RBC shall be AWG 6.

## Bonding.

## Where used in a server cabinet, bonded to the Rack Bonding Connector (RBC) using UL Listed irreversible compression (crimp) connectors and to IT equipment via a UL Listed two-hole compression lug. (Some IT equipment may require one-hole lugs.)

## Where used in a network cabinet/rack, bonded to the Rack Bonding Busbar (RBB) via a UL Listed two-hole compression lug and to IT equipment via a UL Listed two-hole compression lug. (Some IT equipment may require one-hole lugs.)

## Where used as a cable tray bonding conductor connecting cable tray sections, bonded to each adjoining section of the cable tray using UL Listed two-hole compression lugs.

## Where used as a cable tray bonding conductor connecting cable tray sections to the Telecommunications Equipment Bonding Conductor (TEBC), bonded to the TEBC using UL Listed irreversible compression (crimp) connectors and to the cable tray via a UL Listed two-hole compression lug.

## Contractor shall furnish a minimum of ten (10) EBCs for each RBB. Five (5) EBCs shall be outfitted as

## described here and shall be six (6) feet in length. Five (5) EBCs shall be outfitted as decried here and shall be nine (9) feet in length. Contractor shall use field measurements to determine EBC cable length when directed by VA project managers.

  - OVERVOLTAGE SURGE PROTECTORS.

## Protectors are voltage-limiting devices intended to protect equipment, wiring, and personnel against the effects of excessive potentials and currents in communications lines caused by lightning, contacts with power conductors, power induction, and rises in ground potential.

## Compliance. Protectors shall be compliant with UL 497 and/or UL 497A, as applicable.

## Performance. Protectors shall be rated to support copper UTP performance Category 5e at 100MHz.

## Protection. Voltage suppression shall be via low capacitance solid state protectors only, rated at 18V for copper backbone applications or 65V for VOIP or PoE applications.

## Construction. Provide protection for each pair.

## Termination shall be insulation-displacement contact.

## Mounting. Protectors shall be wall mounted.

PART 3 - EXECUTION

3.1 IMPLEMENTATION

## Components of the telecommunications bonding system will be installed and connected using materials and techniques required by ANSI/TIA-607-D. The use of antioxidant joint compound is required for all connections excluding protector 110 block connections.

## Testing.

## Perform tests per BICSI Information Technology Systems Installation Methods Manual (ITSIMM), 8TH Edition, Recommended Testing Procedures and Criteria.

## Perform two-point bond test using trained installers qualified to use test equipment.

## Conduct continuity tests to verify that metallic pathways in telecommunications spaces are bonded to PBB or SBB.

## Conduct electrical continuity test to verify that PBB is effectively bonded to the facility grounding electrode conductor.

## Perform resistance tests to ensure rack and cabinet bonding connection resistance measures less than 4Ω to PBB or SBB.

## - - - E N D - - -

SECTION 27 05 33

CONDUITS AND BACKBOXES FOR COMMUNICATIONS SYSTEMS

PART 1 - GENERAL

  - DESCRIPTION

## This section specifies conduit, fittings, and boxes to form raceway systems for communications cabling.

  - RELATED WORK

## Sealing around penetrations to maintain integrity of fire rated construction: Section 07 84 00, FIRESTOPPING.

## Fabrications for deflection of water away from building envelope at penetrations: Section 07 60 00, FLASHING AND SHEET METAL.

## Sealing around conduit penetrations through building envelope to prevent moisture migration into building: Section 07 92 00, JOINT SEALANTS.

## Identification and painting of conduit and other devices: Section 09 91 00, PAINTING.

## Requirements for personnel safety and to provide a low impedance path for possible ground fault currents: Section

## 27 05 26, GROUNDING AND BONDING FOR COMMUNICATIONS SYSTEMS.

  - SUBMITTALS

## In accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS, submit the following:

## Size and location of cabinets, splice boxes, and pull boxes.

## Layout of required conduit penetrations through structural elements.

## Catalog cuts marked with specific item proposed and area of application identified.

## Certification: Provide letter prior to final inspection, certifying material is in accordance with construction documents and properly installed.

PART 2 - PRODUCTS

2.1 MATERIAL

## Minimum Conduit Size: 19 mm (3/4 inch).

## Conduit:

## Rigid Galvanized Steel: Conform to UL 6, ANSI C80.1.

## Rigid Aluminum: Conform to UL 6A, ANSI C80.5.

## Rigid Intermediate Steel Conduit (IMC): Conform to UL 1242, ANSI C80.6.

## Electrical Metallic Tubing (EMT):

## Maximum Size: 105 mm (4 inches).

## Install only for cable rated 600 volts or less.

## Conform to UL 797, ANSI C80.3.

## Flexible Galvanized Steel Conduit: Conform to UL 1.

## Liquid-tight Flexible Metal Conduit: Conform to UL 360.

## Direct Burial Plastic Conduit: Conform to UL 651 and UL 651A, heavy wall PVC, or high density polyethylene (HDPE).

## Surface Metal Raceway: Conform to UL 5.

## Conduit Fittings:

## Rigid Galvanized Steel and Rigid Intermediate Steel Conduit Fittings:

## Provide fittings meeting requirements of UL 514B and ANSI/ NEMA FB 1.

## Sealing: Provide threaded cast iron type. Use continuous drain type sealing fittings to prevent passage of water and vapor. In concealed work, install sealing fittings in flush steel boxes with blank cover

## plates having same finishes as other electrical plates in room.

## Standard Threaded Couplings, Locknuts, Bushings, and Elbows: Only steel or malleable iron materials are acceptable. Integral retractable type IMC couplings are also acceptable.

## Locknuts: Bonding type with sharp edges for digging into metal wall of an enclosure.

## Bushings: Metallic insulating type, consisting of an insulating insert molded or locked into metallic body of fitting. Bushings made entirely of metal or nonmetallic material are not permitted.

## Erickson (union-type) and Set Screw Type Couplings:

## Couplings listed for use in concrete are permitted for use to complete a conduit run where conduit is installed in concrete.

## Use set screws of case hardened steel with hex head and cup point to seat in conduit wall for positive ground.

## Provide OEM approved fittings.

## Rigid Aluminum Conduit Fittings:

## Standard Threaded Couplings, Locknuts, Bushings, and Elbows: Malleable iron, steel or aluminum alloy materials; Zinc or cadmium plate iron or steel fittings. Aluminum fittings containing more than 0.4 percent copper are not permitted.

## Locknuts and Bushings: As specified for rigid steel and IMC conduit.

## Set Screw Fittings: Not permitted for use with aluminum conduit.

## Electrical Metallic Tubing Fittings:

## Conform to UL 514B and ANSI/ NEMA FB1; only steel or malleable iron materials are acceptable.

## Couplings and Connectors: Concrete tight and rain tight, with connectors having insulated throats.

## Use gland and ring compression type couplings and connectors for conduit sizes 50 mm (2 inches) and smaller.

## Use set screw type couplings with four set screws each for conduit sizes over 50 mm (2 inches).

## Use set screws of case-hardened steel with hex head and cup point to seat in wall of conduit for positive grounding.

## Indent type connectors or couplings are not permitted.

## Die-cast or pressure-cast zinc-alloy fittings or fittings made of "pot metal" are not permitted.

## Provide OEM approved fittings.

## Flexible Steel Conduit Fittings:

## Conform to UL 514B; only steel or malleable iron materials are acceptable.

## Provide clamp type, with insulated throat.

## Provide OEM approved fittings.

## Liquid-tight Flexible Metal Conduit Fittings:

## Conform to UL 514B and ANSI/ NEMA FB1; only steel or malleable iron materials are acceptable.

## Fittings must incorporate a threaded grounding cone, a steel or plastic compression ring, and a gland for tightening.

## Provide connectors with insulated throats to prevent damage to cable jacket.

## Provide OEM approved fittings.

## Direct Burial Plastic Conduit Fittings: Provide fittings meeting requirements of UL 514C and NEMA TC3, and as recommended by conduit manufacturer.

## Expansion and Deflection Couplings:

## Conform to UL 467 and UL 514B.

## Accommodate 19 mm (3/4 inch) deflection, expansion, or contraction in any direction, and allow 30-degree angular deflections.

## Include internal flexible metal braid sized to ensure conduit ground continuity and fault currents in accordance with UL 467, and NEC code tables for ground conductors.

## Jacket: Flexible, corrosion-resistant, watertight, moisture and heat resistant molded rubber material with stainless steel jacket clamps.

## Conduit Supports:

## Parts and Hardware: Provide zinc-coat or equivalent corrosion protection.

## Individual Conduit Hangers: Designed for the purpose, having a pre-assembled closure bolt and nut, and provisions for receiving a hanger rod.

## Multiple Conduit (Trapeze) Hangers: Minimum 38 mm by 38 mm (1-1/2 by 1-1/2 inch), 2.78 mm (12 gage) steel, cold formed, lipped channels; with minimum 9 mm (3/8 inch) diameter steel hanger rods.

## Solid Masonry and Concrete Anchors: Self-drilling expansion shields, or machine bolt expansion.

## Outlet, Splice, and Pull Boxes:

## Conform to UL-50 and UL-514A.

## Cast metal where required by NEC or shown and equipped with rustproof boxes.

## Sheet Metal Boxes: Galvanized steel, except where otherwise shown.

## Install flush mounted wall or ceiling boxes with raised covers so that front face of raised cover is flush with wall.

## Install surface mounted wall or ceiling boxes with surface style flat or raised covers.

## Warning Tape: Standard, 4-Mil polyethylene 76 mm (3 inch) wide tape detectable type, red with black letters, and imprinted with “CAUTION BURIED COMMUNICATIONS CABLE BELOW”.

## Flexible Nonmetallic Communications Raceway (Innerduct) and Fittings: Interior Installations

## General: Provide UL 910 listed plenum, riser, and general purpose corrugated pliable communications raceway.

## Provide Communications Raceway with a factory installed

## 567 kg (1250 lb.) tensile pre-lubricated pull tape.

## Use only metallic straps, hangers and fittings to support raceway from building structure. Cable ties are not permitted for securing raceway to building structure.

## Provide fittings to be installed in spaces used for environmental air made of materials that do not exceed flammability, smoke generation, ignitibility, and toxicity requirements of environmental air space.

## Size: Metric Designator 53 (trade size 2) or smaller.

## Outside Plant: Plenum-rated where each innerduct is 75 mm (3 inches) and larger.

## Inside Plant: Listed and marked for installation in plenum airspaces and minimum 25 mm (1 inch) inside diameter.

## Plenum: Non-metallic communications raceway.

## Constructed of low smoke emission, flame retardant PVC with corrugated construction.

## UL 94 V-O rating for flame spreading limitation.

## Provide innerduct reel lengths as necessary to ensure ducts are continuous.

## Provide pulling accessories used for innerduct including but not limited to, inner duct lubricants, spreaders, applicators, grips, swivels, harnesses, and line missiles (blown air) compatible with materials being pulled.

## Flexible Textile Fabric Innerduct – Exterior Installations

## General

## Material: White polyester and nylon resin polymer.

## Labeled and/or listed as acceptable to the authority having jurisdiction as suitable for the intended use.

## Flexible optical fiber/communication raceway.

## A non-metallic pathway, usually circular, placed within a larger non flexible raceway.

## Description and Application

## Outdoor Locations:

## Detectable Outdoor Textile Innerduct Micro 2 inch, 3 inch and 4 inch single or multi-cell polyester/nylon textile innerduct containing 1,250 lb. polyester flat woven pull tape, and a solid copper, polyvinyl color coated conductor (19 AWG minimum) for tracing and rated for a minimum of 6 amps and 600 volts. Conductor shall be placed in the sidewall edge fold of the textile sleeve.

## Refer to drawings for quantity and location of raceways requiring textile innerduct and diameter/number of cells per raceway.

## Textile Innerduct Fittings

## Conduit Plugs: compression-type conduit plugs with locking nuts for sealing and securing one or more textile innerducts within a 4-inch inside diameter conduit, e.g.:

## 4-inch plug with nine holes for cables in a 3 pack (9-cell) configuration

## Termination Bags: Inflation-type bags for sealing and securing around one or more textile innerducts and cables within 2-inch outside diameter or larger conduit.

## Pull Tape

## Measuring and pulling tape constructed of synthetic fiber, printed with accurate sequential footage marks. Color-coded.

## Penetration Sealing Materials

## Duct Water Seal: Products suitable for closing underground and entrance conduit openings where innerduct or cable is installed to prevent entry of gases, liquids, or rodents into the structure.

## Outlet Boxes:

## Flush wall mounted minimum 11.9 cm (4-11/16 inches) square, 9.2 cm (3-5/8 inches) deep pressed galvanized steel.

## 2-Gang Tile Box:

## Flush backbox type for installation in block walls.

## Minimum 92 mm (3-5/8 inches) deep.

## Weatherproof Outlet Boxes: Surface mount two gang, 67 mm (2-5/8 inches) deep weatherproof cast aluminum with powder coated finish internal threads on hubs 19 mm (3/4 inch) minimum.

PART 3 - EXECUTION

  - EQUIPMENT INSTALLATION AND REQUIREMENTS

## Penetrations:

## Cutting or Holes:

## Locate holes in advance of installation. Where proposed in structural sections, obtain approval of structural engineer and COR prior to drilling through structural sections.

## Make holes through concrete and masonry in existing structures with a diamond core drill or concrete saw. Pneumatic hammer, impact electric, hand or manual hammer type drills are not permitted; COR may grant limited permission by request, in condition of limited working space.

## Fire Stop: Where conduits, wireways, and other communications raceways pass through fire partitions, fire walls, smoke partitions, or floors, install a fire stop that provides an effective barrier against spread of fire, smoke and gases as specified in Section 07 84 00, FIRESTOPPING.

## Fill and seal clearances between raceways and openings with fire stop material.

## Install only retrofittable, non-hardening, and reusable firestop material that can be removed and reinstalled to seal around cables inside conduits.

## Waterproofing at Floor, Exterior Wall, and Roof Conduit Penetrations: Seal clearances around conduit and make watertight as specified in Section 07 92 00, JOINT SEALANTS.

## Conduit Installation:

## Minimum conduit size of 19 mm (3/4 inch), but not less than size required for 40 percent fill.

## Install insulated bushings on all conduit ends.

## Install pull boxes after every 180 degrees of bends (two 90-degree bends) or every 100ft. Size boxes per TIA 569.

## Extend vertical conduits/sleeves through floors minimum

## 75 mm (3 inches) above floor and minimum 75 mm (3 inches) below ceiling of floor below.

## Exterior conduit penetrations through building ceilings, floors and walls shall be made of metallic conduit (e.g. RGS, IMC); interior conduit through building floors and walls shall be made of metallic conduit (e.g. RGS, IMC, EMT);	non-metallic conduit is not permitted for exterior or interior ceiling, floor or wall penetrations.

## Exterior conduit turn ups from concrete slab, macadam and/or landscaping areas shall be made of metallic conduit (e.g. RGS, IMC); non-metallic conduit is not permitted.

## Terminate conduit runs to and from a backboard in a TR or interstitial space at top or bottom of backboard. Install conduits to enter telecommunication rooms next to wall and flush with backboard.

## Where drilling is necessary for vertical conduits, locate holes so as not to affect structural sections.

## Seal empty conduits located in telecommunications rooms or on backboards to prevent entrance of moisture and gases and to meet fire resistance requirements.

## Provide nylon pull wire in all empty conduits; sleeves through floor are exceptions.

## Complete each entire conduit run installation before pulling in cables.

## Flattened, dented, or deformed conduit is not permitted.

## Ensure conduit installation does not encroach into ceiling height head room, walkways, or doorways.

## Cut conduit square with a hacksaw, ream, remove burrs, and draw tight.

## Install conduit mechanically continuous.

## Independently support conduit at 2.44 m (8 feet) on center; do not use other supports (i.e., suspended ceilings, suspended ceiling supporting members, luminaires, conduits, mechanical piping, or mechanical ducts).

## Support conduit within 300 mm (1 foot) of changes of direction, and within 300 mm (1 foot) of each enclosure to which connected.

## Close ends of empty conduit with plugs or caps to prevent entry of debris, until cables are pulled in.

## Attach conduits to cabinets, splice cases, pull boxes and outlet boxes with bonding type locknuts. For rigid and IMC conduit installations, provide a locknut on inside of enclosure, made up wrench tight. Do not make conduit connections to box covers.

## Do not use aluminum conduits in wet locations.

## Unless otherwise indicated on drawings or specified herein, conceal conduits within finished walls, floors and ceilings.

## Conduit Bends:

## Make bends with standard conduit bending machines; observe minimum bend radius for cable type and outside diameter.

## Conduit hickey is permitted only for slight offsets, and for straightening stubbed conduits.

## Bending of conduits with a pipe tee or vise is not permitted.

## Minimum radius of communication conduit bends:

| Sizes of Conduit Trade Size | Radius of Conduit Bends mm, Inches |
| --- | --- |
| 3/4 | 150 (6) |
| 1 | 230 (9) |
| 1-1/4 | 350 (14) |
| 1-1/2 | 430 (17) |
| 2 | 525 (21) |
| 2-1/2 | 635 (25) |
| 3 | 775 (31) |
| 3-1/2 | 900 (36) |
| 4 | 1125 (45) |

## Layout and Homeruns - Deviations: Make only where necessary to avoid interferences and only after drawings showing proposed deviations have been submitted and approved by COR.

## Concealed Work Installation:

## In Concrete:

## Conduit: Schedule 40 PVC, Rigid steel or IMC.

## Align and run conduit in direct lines.

## Install conduit through concrete beams only when the following occurs:

## Where shown on structural drawings.

## As accepted by COR prior to construction, and after submittal of drawing showing location, size, and position of each penetration.

## Installation of conduit in concrete that is less than

## 75 mm (3 inches) thick is prohibited.

## Conduit outside diameter larger than 1/3 of slab thickness is prohibited.

## Space between Conduits in Slabs: Approximately six conduit diameters apart, except one conduit diameter at conduit crossings.

## Install conduits approximately in center of slab to ensure a minimum of 19 mm (3/4 inch) of concrete around conduits.

## Make couplings and connections watertight. Use thread compounds that are NRTL listed conductive type to ensure low resistance ground continuity through conduits. Tightening set screws with pliers is not permitted.

## Furred or Suspended Ceilings and in Walls:

## Rigid steel, IMC or rigid aluminum. Different type conduits mixed indiscriminately in same system is not permitted.

## Align and run conduit parallel or perpendicular to building lines.

## Tightening set screws with pliers is not permitted.

## Exposed Work Installation:

## Unless otherwise indicated on drawings, exposed conduit is only permitted in telecommunications rooms.

## Provide rigid steel, IMC or rigid aluminum.

## Different type of conduits mixed indiscriminately in system is not permitted.

## Align and run conduit parallel or perpendicular to building lines.

## Install horizontal runs close to ceiling or beams and secure with conduit straps.

## Support horizontal or vertical runs at not over 2400 mm (96 inches) intervals.

## Painting:

## Paint exposed conduit as specified in Section 09 91 00, PAINTING.

## Refer to Section 09 91 00, PAINTING for preparation, paint type, and exact color.

## Provide labels where conduits pass through walls and floors and at maximum 6000 mm (20 foot) intervals in between.

## Expansion Joints:

## Conduits 75 mm (3 inches) and larger, that are secured to building structure on opposite sides of a building expansion joint, require expansion and deflection couplings. Install couplings in accordance with manufacturer's recommendations.

## Provide conduits smaller than 75 mm (3 inches) with pull boxes on both sides of expansion joint. Connect conduits to expansion and deflection couplings as specified.

## Install expansion and deflection couplings where shown.

## Seismic Areas:

## In seismic areas, follow H-18-8 Seismic Design Requirements.

## Rigidly secure conduit to building structure on opposite sides of a building expansion joint with pull boxes on both sides of joint.

## Connect conduits to pull boxes with 375 mm (15 inches) of slack flexible conduit.

## Install green copper wire minimum #6 AWG in flexible conduit for bonding jumper.

## Conduit Supports, Installation:

## Select AC193 code listed mechanical anchors or fastening devices with safe working load not to exceed 1/4 of proof test load.

## Use pipe straps or individual conduit hangers for supporting individual conduits. Maximum distance between supports is 2.5 m (8 foot) on center.

## Support multiple conduit runs with trapeze hangers. Use trapeze hangers designed to support a load equal or greater than sum of the weights of the conduits, wires, hanger itself, and 90 kg (200 pounds). Attach each conduit with U-bolts or other accepted fasteners.

## Support conduit independent of pull boxes, luminaires, suspended ceiling components, angle supports, duct work, and similar items.

## Fastenings and Supports in Solid Masonry and Concrete:

## Existing Construction:

## Code AC193 listed wedge type steel expansion anchors minimum 6 mm (1/4 inch) bolt size and minimum 28 mm (1-1/8 inch) embedment.

## Power set fasteners minimum 6 mm (1/4 inch) diameter with depth of penetration minimum 75 mm (3 inches).

## Use vibration and shock resistant anchors and fasteners for attaching to concrete ceilings.

## Fastening to Hollow Masonry: Toggle bolts are permitted.

## Fastening to Metal Structures: Use machine screw fasteners or other devices designed and accepted for application.

## Bolts supported only by plaster or gypsum wallboard are not acceptable.

## Attachment by wood plugs, rawl plug, plastic, lead or soft metal anchors, or wood blocking and bolts supported only by plaster is prohibited.

## Do not support conduit from chain, wire, or perforated strap.

## Spring steel type supports or fasteners are not permitted except horizontal and vertical supports/fasteners within walls.

## Vertical Supports:

## Install riser clamps and supports for vertical conduit runs in accordance with NEC.

## Provide supports for cable and wire with fittings that include internal wedges and retaining collars.

## Box Installation:

## Boxes for Concealed Conduits:

## Flush mounted.

## Provide raised covers for boxes to suit wall or ceiling, construction and finish. In spaces not controlled by VA (i.e., common hallways) covers must be lockable.

## In addition to boxes shown, install additional boxes where needed to prevent damage to cables during pulling.

## Remove only knockouts as required and plug unused openings. Use threaded plugs for cast metal boxes and snap-in metal covers for sheet metal boxes.

## Stencil or install phenolic nameplates on covers of boxes identified on riser diagrams; for example "SIG-FA JB No. 1".

## Outlet boxes mounted back-to-back in same wall are not permitted. A minimum 600 mm (24 inches) center-to-center lateral spacing must be maintained between boxes.

## Flexible Nonmetallic Communications Raceway (Innerduct), Installation:

## Install Innerduct in cable tray. Innerduct may not be free-hung.

## Install only in accessible spaces not subject to physical damage or corrosive influences.

## Make bends manually to assure internal diameter of tubing is not effectively reduced.

## Extend each segment of innerduct minimum 300 mm (12 inches) beyond end of service conduit tie or cable tray. Restrain innerduct ends with wall mount clamps and seal when cable is installed.

  - TESTING

## Examine fittings and locknuts for secureness.

## Test RMC, IMC and EMT systems for electrical continuity and resistance to ground.

## - - - E N D - - -

SECTION 27 05 36

CABLE TRAYS FOR COMMUNICATIONS SYSTEMS

PART 1 - GENERAL

  - DESCRIPTION:

This section specifies requirements for telecommunications cabling cable tray and raceway equipment.

  - SUMMARY

Section Includes:

    - Cable Tray.

  - REFERENCES

    - VA Infrastructure Standard for Telecommunications Spaces.

  - RELATED WORK:

    - Grounding and bonding: Section 27 05 26, GROUNDING AND BONDING FOR COMMUNICATIONS SYSTEMS.

  - SUBMITTALS:

    - Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

PART 2 - PRODUCTS

2.1 CABLE TRAY.

- Design. Wire basket with tray insert. Maximum 2” x 4” wire mesh construction. Constructed of round, smooth wire with continuous top side to minimize cable sheath damage.

- Finish. Coated to prevent rust.

- Size. Cable tray shall be sized to hold the maximum expected cable load at not more than 40% fill and not more than 6” maximum cable depth.

- Accessories. Provide and install the following components and accessories as necessary to achieve the design:

  - Overhead mounting equipment (thread-rod, unistrut, nuts, washers, etc.) suitable for the supporting structural elements.

  - Tray section splicing hardware.

  - Tray insert.

  - Cable waterfalls.

  - Ground strap kits.

  - Bend radius limiters.

PART 3 - EXECUTION

3.1 IMPLEMENTION:

- Cable tray shall be used in horizontal applications.

- Cable tray and ladder rack sections shall be bonded together with bonding conductors and the system bonded to the bonding busbar in the space.

- Support horizontal cable tray not less than every 5’ (shorter spans if recommended by the equipment manufacturer).

- - - E N D - - -

Richmond, VA	Issued for Bids: 10/17/25

SECTION 27 05 53 IDENTIFICATION FOR COMMUNICATIONS SYSTEMS

PART 1 - GENERAL

  - DESCRIPTION:

This section specifies labeling and identification requirements for information technology (IT) equipment cabinets, racks, and cabling.

  - SUMMARY

Section Includes:

    - Equipment and component labels.

    - Labeling implementation requirements.

  - REFERENCES

    - VA Infrastructure Standard for Telecommunications Spaces.

  - SUBMITTALS:

    - Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

PART 2 - PRODUCTS

  - EQUIPMENT AND COMPONENT LABELS.

    - Materials. Materials used for labeling equipment, components, and telecommunications cabling shall be appropriate for the installation environment, durable and permanent, and heat-resistant if necessary for labeling in high-temperature environments.

PART 3 - EXECUTION

3.1 IMPLEMENTION:

- Governing Standard. Labeling and identification of equipment, components, and telecommunications cabling shall be based on ANSI/TIA- 606-C, Administration Standard for Telecommunications Infrastructure, and NFPA 70, National Electrical Code, as modified by guidance in the VA Infrastructure Standard for Telecommunications Spaces.

- All passive infrastructure equipment, components, and telecommunications cabling installed shall be labeled at the time of installation.

- Telecommunications cable labeling shall include delivery of complete and accurate connection documentation (where each cable terminates at each end) matching the installed labels.

- Label locations shall be as specified in the VA Infrastructure Standard for Telecommunications Spaces.

- - - E N D - - -

SECTION 27 10 00 STRUCTURED CABLING

PART 1 - GENERAL

  - DESCRIPTION:

This section specifies requirements for telecommunications structured cabling systems.

  - SUMMARY

Section Includes:

    - Facility Horizontal Structured Cabling.

  - REFERENCES

    - VA Infrastructure Standard for Telecommunications Spaces.

  - RELATED WORK:

    - Cabling labeling and identification: Section 27 05 53, IDENTIFICATION FOR COMMUNICATIONS SYSTEMS.

    - Cable termination locations and equipment: Section 27 11 19, COMMUNICATIONS TERMINATION BLOCKS AND PATCH PANELS.

  - SUBMITTALS:

    - Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

PART 2 - PRODUCTS

  - FACILITY HORIZONTAL STRUCTURED CABLING.

Facility horizontal structured cabling (horizontal distribution) connects the Telecommunications Room (TR) to each end-user Work Area Outlet (WAO).

    - Interior to each TR, install horizontal distribution structured cabling in overhead cable tray systems.

    - All horizontal distribution structured cabling shall have a minimum of

2 cables per WAO.

- CCTV cameras shall have a minimum of 1 cable per WAO.

    - Horizontal distribution structured cabling may be field-terminated.

    - In each TR install sufficient UTP patch panels to support the quantity of WAOs in the TR’s serving zone.

      - Plan network racks such that patch panels and horizontal cable managers are located in the top 1/3 (RU31-45), switching equipment in the middle 1/3 (RU16-30), and power distribution and other services in the bottom 1/3 (RU1-15).

    - Install a minimum of 2 UTP cables between the TR UTP patch panels and each work area faceplate.

    - Each typical end-user receptacle shall be constructed of a two-gang workbox with one connector chassis, a minimum of two non-proprietary Category 6A 8P8C media interface connectors (RJ-45), and a four- position keystone faceplate.

- Modular plug terminated links (MPTL) are permitted to service wireless access points (WAPs), cameras, and other Power over Ethernet (PoE) devices where mating will be very infrequent.

    - For WAO that exceed the maximum manufacturer’s recommendations for unshielded twisted pair (UTP) linear cable length of 295 feet (90M), provide PoE Extender System consisting of the following components for each WAO:

- Indoor/Outdoor rated hybrid fiber optic/DC power cable consisting of multi-strand single-mode, 8.3/125 micron (SMF) type OS2 and #12 American Wire Gauge (AWG) copper conductors. Sheath color is black when cable is not provided with interlocking armor assembly.

- Head end (source) combination UTP to fiber optic media converter and power supply extender module.

  - Head end (source) module may consist of a 1-port device for single end device applications or power chassis allowing for up to six (6) 4-port media modules in a 2 rack-unit (RU) chassis suitable for mounting in a standard 19 inch rack for multiple end device applications.

- Remote End Device (Receiver) combination fiber optic to UTP media converter and power input module.

- Fiber optic cabling for hybrid cable shall use LC-LC terminations for connection to source and remote end unit modules. Number of fiber pairs shall be as required to support the number of end devices.

- Fiber optic cables within hybrid cable shall be tight buffered construction type when serving 1-port remote devices. When cable is serving 2 or more end devices (ports), cable shall be loose tube construction.

- Hybrid cable installed in interior applications above accessible ceiling shall have plenum rated sheathing. Where cable is

installed in open ceilings, within interstitial spaces, warehouses, loading docks and where subject to physical damage, the cable shall have an interlocking armor assembly or installed within metallic pathways. Hybrid cable installed in outdoor locations within conduit shall have riser rated sheathing.

- Remote end device shall be suitable for number of WAO ports served. Device shall be suitable for 1, 2 or 4-port configurations and installed within WAO outlet box or within separate junction box as noted on the drawings (e.g. site light poles).

- Refer to the drawing details for specific device applications based on project and WAO requirements.

PART 3 - EXECUTION

            - IMPLEMENTION:

              - 100% construction drawing sets shall include drawings detailing the computer room and facility/campus structured cabling systems, including:

                - Cable media performance categories for each type of run.

                - Cabling and equipment quantities.

                - Elevation drawings showing equipment placement in individual enclosures as coordinated with VA OIT.

                - Full interconnection diagram for all structured cabling.

                - Port map and cable label matrices.

              - All cabling and equipment shall be labeled per the requirements of the VA Infrastructure Standard for Telecommunications Spaces.

- - - E N D - - -

SECTION 27 11 19

COMMUNICATIONS TERMINATION BLOCKS AND PATCH PANELS

PART 1 - GENERAL

  - DESCRIPTION:

This section specifies cable termination and management equipment to be mounted in information technology (IT) equipment cabinets and racks.

  - SUMMARY

Section Includes:

    - Copper UTP Patch Panels.

    - Horizontal Cable Managers.

    - Blanking Panels.

  - REFERENCES

    - VA Infrastructure Standard for Telecommunications Spaces.

  - RELATED WORK:

    - Labeling and identification requirements: Section 27 05 53, IDENTIFICATION FOR COMMUNICATIONS SYSTEMS.

  - SUBMITTALS:

    - Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

PART 2 - PRODUCTS

  - COPPER (UTP) PATCH PANELS.

    - Form Factor. 1U, 19” rack-mountable. Default form factor for patch panels shall be angled to extend not less than 4” (104mm) forward from the mounting rail.

    - Capacity. 24 or 48 copper 8P8C ports in groupings of 6 or as needed based on quantity of WAO and spare capacity for future growth.

    - Interface. Copper (UTP) patch panels shall accept pre-terminated single 8P8C keystone jacks and 6-jack cassettes. Jacks shall be rated for Category 6a minimum communications as required to support the CCTV system.

    - Accessories. Provide each patch panel installation with the following accessories.

      - Angled panel cover. Specify angled panel covers at the top and bottom of each stack of angled patch panels. Covers shall mount to the same RU rail positions as the top and bottom patch panels.

      - Rear cable manager tray. Specify one rear cable manager tray per patch panel. Trays shall mount to the same RU rail positions as the patch panel.

  - HORIZONTAL CABLE MANAGERS.

    - Form Factor. 2U, 19” rack-mountable.

    - Door. Horizontal cable managers shall have a double-hinged front cover to protect installed cables.

    - Fingers. 6-port spacing (five fingers).

  - BLANKING PANELS.

    - Form Factor. 1U or 2U 19” rack-mountable, angled to extend 4” (104mm) forward from the mounting rail.

    - Transition. Blanking panel shall have a transition cover from angled front to flat front.

    - Quantity. Provide blanking panels to fill 75% of all RUs in all server cabinets and network cabinets.

PART 3 - EXECUTION

3.1 INSTALLATION:

A. Patch panels, horizontal wire managers, and associated blanking panels shall be installed within existing spaces within existing racks in the telecommunication rooms as directed by OIT.

- - - E N D - - -

SECTION 27 13 13.13

COMMUNICATIONS COPPER CABLE SPLICING AND TERMINATIONS

PART 1 - GENERAL

  - DESCRIPTION:

This section specifies requirements for terminations of copper (UTP) cabling.

  - SUMMARY

Section Includes:

    - Termination Requirements.

    - Splicing.

  - REFERENCES

    - VA Infrastructure Standard for Telecommunications Spaces, V4.0.

  - RELATED WORK:

    - Termination equipment: Section 27 11 19, COMMUNICATIONS TERMINATION BLOCKS AND PATCH PANELS.

    - Copper (UTP) cabling requirements: Section 27 15 13, COMMUNICATIONS COPPER HORIZONTAL CABLING.

  - SUBMITTALS:

    - Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

PART 2 - PRODUCTS

Not used.

PART 3 - EXECUTION

  - TERMINATION REQUIREMENTS.

    - Terminate copper (UTP) cabling used for data communications per TIA 568B. All cables shall be terminated; no pairs shall be left unterminated.

    - Connections shall be made to equipment certified to performance category 6a.

    - Pre-terminated connections are preferred for computer room structured cabling applications. Field termination for non-computer room applications is acceptable.

  - SPLICING.

Splicing of copper (UTP) cabling is prohibited.

- - - E N D - - -

SECTION 27 15 13 COMMUNICATIONS COPPER HORIZONTAL CABLING

PART 1 - GENERAL

  - DESCRIPTION:

This section specifies requirements for telecommunications copper (UTP) horizontal distribution cabling outside of the computer room.

  - SUMMARY

Section Includes:

    - Copper (UTP) Horizontal Cables.

  - REFERENCES

    - VA Infrastructure Standard for Telecommunications Spaces.

  - RELATED WORK:

    - Termination equipment: Section 27 11 19, COMMUNICATIONS TERMINATION BLOCKS AND PATCH PANELS.

    - Cable labeling requirements: Section 27 05 53, IDENTIFICATION FOR COMMUNICATIONS SYSTEMS.

  - SUBMITTALS:

    - Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

PART 2 - PRODUCTS

  - COPPER (UTP) HORIZONTAL CABLES.

Copper (UTP) horizontal cables connect the Telecommunications Room (TR) to each end-user Work Area Outlet (WAO) (horizontal distribution).

    - Performance Category. Copper (UTP) horizontal cables shall meet the Category 6A performance requirements. Category 6A connectors are required.

    - Performance Specifications. Meets or exceeds TIA-EIA-568-C.2-10 and TSB-155.

    - Limited Power (LP) Certification. UL Listed as x-LP (0.5A).

    - Termination. Field terminated TIA 568B.

    - Testing. Following installation, each cable shall be field certified to meet performance category requirements per TIA 568-C.2.

    - Conductor Size. 22-24AWG.

    - Jacket Rating. Communications Multipurpose Cable, Plenum (CMP) shall be specified if any portion of the cable passes through an NEC-defined plenum. Communications Multipurpose Cable, Riser (CMR) shall be specified for all other applications. CMP may be used as a substitute for CMR.

    - Construction. Copper Clad Aluminum (CCA) cable is not permitted.

J. Length. The maximum distance for UTP horizontal cables is limited to

295 feet.

2.02 POWER OVER ETHERNET EXTENDED REACH CABLING AND INFRASTRUCTURE

For WAO that exceed the maximum manufacturer’s recommendations for unshielded twisted pair (UTP) linear cable length of 295 feet (90M), provide PoE Extender System consisting of the following components for each WAO:

- Indoor/Outdoor rated hybrid fiber optic/DC power cable consisting of multi-strand single-mode, 8.3/125 micron (SMF) type OS2 and #12 American Wire Gauge (AWG) copper conductors. Sheath color is black when cable is not provided with interlocking armor assembly.

- Head end (source) combination UTP to fiber optic media converter and power supply extender module.

1. Head end (source) module may consist of a 1-port device for single end device applications or power chassis allowing for up to six (6) 4-port media modules in a 2 rack-unit (RU) chassis suitable for mounting in a standard 19 inch rack for multiple end device applications.

- Remote End Device (Receiver) combination fiber optic to UTP media converter and power input module.

- Fiber optic cabling for hybrid cable shall use LC-LC terminations for connection to source and remote end unit modules. Number of fiber pairs shall be as required to support the number of end devices.

- Fiber optic cables within hybrid cable shall be tight buffered construction type when serving 1-port remote devices. When cable is serving 2 or more end devices (ports), cable shall be loose tube construction.

- Hybrid cable installed in interior applications above accessible ceiling shall have plenum rated sheathing. Where cable is installed in open ceilings, within interstitial spaces, warehouses, loading docks and where subject to physical damage, the cable shall have an

interlocking armor assembly or in metallic pathways. Hybrid cable installed in outdoor locations within conduit shall have riser rated sheathing.

- Remote end device shall be suitable for number of WAO ports served. Device shall be suitable for 1, 2 or 4-port configurations and installed within WAO outlet box or within separate junction box as noted on the drawings (e.g. site light poles).

- Refer to the drawing details for specific device applications based on project and WAO requirements.

PART 3 - EXECUTION

3.1 IMPLEMENTATION.

- All cabling and equipment shall be labeled per the requirements of the VA Infrastructure Standard for Telecommunications Spaces.

- Interior to the TR, install horizontal copper (UTP) structured cabling in overhead cable tray.

- Installation of all cabling shall be coordinated with OIT.

- - - E N D - - -

SECTION 27 16 19

COMMUNICATIONS PATCH CORDS, STATION CORDS, AND CROSS CONNECT WIRE

PART 1 - GENERAL

  - DESCRIPTION:

This section specifies requirements for telecommunications patch cords.

  - SUMMARY

Section Includes:

    - Copper (UTP) Patch Cables.

  - REFERENCES

    - VA Infrastructure Standard for Telecommunications Spaces.

  - RELATED WORK:

    - Termination equipment: Section 27 11 19, COMMUNICATIONS TERMINATION BLOCKS AND PATCH PANELS.

    - Cable labeling requirements: Section 27 05 53, IDENTIFICATION FOR COMMUNICATIONS SYSTEMS.

  - SUBMITTALS:

    - Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

PART 2 - PRODUCTS

  - COPPER (UTP) PATCH CABLES.

    - Performance Category. Patch cables shall meet the Category 6A performance requirements. Category 6A connectors are required.

    - Termination Method. Factory pre-terminated TIA 568B.

    - Conductor Size. 22-28AWG. Where 28AWG patch cords are specified, the overall horizontal channel distance is reduced.

    - Length. Patch cords of the shortest appropriate length shall be used.

PART 3 - EXECUTION

3.1 IMPLEMENTATION.

- Patch cords for WAO at camera locations and data outlets shall be furnished and installed by the CCTV system installation contractor.

- Patch cords for installation within the TR rooms for CCTV and data outlet connections to the OIT active network switches shall be furnished by the CCTV system installation contractor; installed at the patch panel and into the active switch network port(s) by OIT.

- Patch cords shall not be used to connect equipment in different server cabinets.

- Patch cords shall be neatly installed using cable management equipment and following cable management principles.

- Upon installation patch cords shall be labeled in accordance with the requirements of the VA Infrastructure Standard for Telecommunications Spaces.

- - - E N D - - -

SECTION 28 05 00

COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND SECURITY

PART 1 - GENERAL

  - DESCRIPTION

    - This Section, Common Work Results for Electronic Safety and Security (ESS), applies to all sections of Division 28 as specifically related to the replacement of the existing campus video surveillance system. The existing access control, intrusion detection and other Division 28 systems are considered existing to remain and not be altered in any way. Refer to the scope of work section as indicated in specification section 280501.

    - Furnish and install fully functional electronic safety and security cabling system(s), equipment and approved accessories in accordance with the specification section(s), drawing(s), and referenced publications. Capacities and ratings of cable and other items and arrangements for the specified items are shown on each system’s required Bill of Materials (BOM) and verified on the approved system drawing(s). If there is a conflict between contract’s specification(s) and drawings(s), the contract’s specification requirements shall prevail.

    - The Contractor shall provide a fully functional and operating ESS (video surveillance system), programmed, configured, documented, and tested as required herein and the respective Safety and Security System Specification(s). The Contractor shall provide calculations and analysis to support design and engineering decisions as specified in submittals. The Contractor shall provide and pay all labor, materials, and equipment, sales and gross receipts and other taxes. The Contractor shall secure and pay for plan check fees, permits, other fees, and licenses necessary for the execution of work as applicable for the project. Give required notices; the Contractor will comply with codes, ordinances, regulations, and other legal requirements of public authorities, which bear on the performance of work.

    - The Contractor shall provide a video surveillance system, installed, programmed, configured, documented, and tested. The security system shall include but not limited to:, video assessment and surveillance, video recording and storage, , two (2) client PC workstations with

monitors as noted, and uninterruptible power supplies (UPS) interface. Operator training shall not be required as part of the Security Contractors scope and shall be provided by the Owner. The Security Contractor shall still be required to provide necessary maintenance and troubleshooting manuals as well as submittals as identified herein.

The work shall include the procurement and installation of electrical wire and cables, the installation and testing of all system components. Inspection, testing, demonstration, and acceptance of equipment, software, materials, installation, documentation, and workmanship, shall be as specified herein. The Contractor shall provide all associated installation support, including the provision of primary electrical input power circuits.

    - Repair Service Replacement Parts On-site service during the warranty period shall be provided as specified under “Emergency Service”. The Contractor shall guarantee all parts and labor for a term of five (5) years, unless dictated otherwise in this specification from the acceptance date of the system as described in Part 5 of this Specification. The Contractor shall be responsible for all equipment, software, shipping, transportation charges, and expenses associated with the service of the system for one (1) year. The Contractor shall provide 24-hour telephone support for the software program at no additional charge to the owner. Software support shall include all software updates that occur during the warranty period.

    - Section Includes:

      - Description of Work for Video Surveillance System ,

      - Electronic security equipment coordination with relating Divisions,

      - Submittal Requirements for Electronic Security,

      - Miscellaneous Supporting equipment and materials for Electronic Security,

      - Electronic security installation requirements.

  - RELATED WORK

    - Section 01 00 00 - GENERAL REQUIREMENTS. For General Requirements.

    - Sealing around penetrations to maintain integrity of fire rated construction: Section 07 84 00, FIRESTOPPING.

    - Fabrications for deflection of water away from building envelope at penetrations: Section 07 60 00, FLASHING AND SHEET METAL.

    - Sealing around conduit penetrations through building envelope to prevent moisture migration into building: Section 07 92 00, JOINT SEALANTS.

    - Identification and painting of conduit and other devices: Section 09 91 00, PAINTING.

    - Requirements for Communications Installations: Section 27 05 11, REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS.

    - Cable trays: Section 27 05 36, CABLE TRAYS FOR COMMUNICATIONS SYSTEMS.

    - Section 28 05 13 - CONDUCTORS AND CABLES FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for conductors and cables.

    - Section 28 05 26 - GROUNDING AND BONDING FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for grounding of equipment.

    - Section 28 05 28.33 - CONDUITS AND BOXES FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for infrastructure.

    - Section 28 23 00 - VIDEO SURVEILLANCE. Requirements for security camera systems.

    - Excavation: Section 31 20 00, EARTH MOVING.

  - DEFINITIONS

    - AGC: Automatic Gain Control.

    - Basket Cable Tray: A fabricated structure consisting of wire mesh bottom and side rails.

    - BICSI: Building Industry Consulting Service International.

    - CCD: Charge-coupled device.

    - Central Station: A PC with software designated as the main controlling PC of the security access system. Where this term is presented with initial capital letters, this definition applies.

    - Channel Cable Tray: A fabricated structure consisting of a one-piece, ventilated-bottom or solid-bottom channel section.

    - Controller: An intelligent peripheral control unit that uses a computer for controlling its operation. Where this term is presented with an initial capital letter, this definition applies.

    - CPU: Central processing unit.

    - Credential: Data assigned to an entity and used to identify that entity.

    - DGP: Data Gathering Panel – component of the Physical Access Control System capable to communicate, store and process information received

from readers, reader modules, input modules, output modules, and Security Management System.

    - DTS: Digital Termination Service: A microwave-based, line-of-sight communications provided directly to the end user.

    - EMI: Electromagnetic interference.

    - EMT: Electric Metallic Tubing.

    - ESS: Electronic Security System.

    - File Server: A PC in a network that stores the programs and data files shared by users.

    - GFI: Ground fault interrupter.

    - IDC: Insulation displacement connector.

    - Identifier: A credential card, keypad personal identification number or code, biometric characteristic, or other unique identification entered as data into the entry-control database for the purpose of identifying an individual. Where this term is presented with an initial capital letter, this definition applies.

    - I/O: Input/Output.

    - Intrusion Zone: A space or area for which an intrusion must be detected and uniquely identified, the sensor or group of sensors assigned to perform the detection, and any interface equipment between sensors and communication link to central-station control unit.

    - Ladder Cable Tray: A fabricated structure consisting of two longitudinal side rails connected by individual transverse members (rungs).

    - LAN: Local area network.

    - LCD: Liquid-crystal display.

    - LED: Light-emitting diode.

    - Location: A Location on the network having a PC-to-Controller communications link, with additional Controllers at the Location connected to the PC-to-Controller link with RS-485 communications loop. Where this term is presented with an initial capital letter, this definition applies.

    - Low Voltage: As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control and signaling power- limited circuits.

    - M-JPEG: Motion – Joint Photographic Experts Group.

    - MPEG: Moving picture experts group.

    - NEC: National Electric Code

    - NEMA: National Electrical Manufacturers Association

    - NFPA: National Fire Protection Association

    - NTSC: National Television System Committee.

    - NRTL: Nationally Recognized Testing Laboratory.

    - Open Cabling: Passing telecommunications cabling through open space (e.g., between the studs of a wall cavity).

II. PACS: Physical Access Control System; A system comprised of cards, readers, door controllers, servers and software to control the physical ingress and egress of people within a given space

- PC: Personal computer. This acronym applies to the Central Station, workstations, and file servers.

- PCI Bus: Peripheral component interconnect; a peripheral bus providing a high-speed data path between the CPU and peripheral devices (such as monitor, disk drive, or network).

- PDF: (Portable Document Format.) The file format used by the Acrobat document exchange system software from Adobe.

- RCDD: Registered Communications Distribution Designer.

- RFI: Radio-frequency interference.

- RIGID: Rigid conduit is galvanized steel tubing, with a tubing wall that is thick enough to allow it to be threaded.

- RS-232: An TIA/EIA standard for asynchronous serial data communications between terminal devices. This standard defines a 25- pin connector and certain signal characteristics for interfacing computer equipment.

- RS-485: An TIA/EIA standard for multipoint communications.

- Solid-Bottom or Non-ventilated Cable Tray: A fabricated structure consisting of integral or separate longitudinal side rails, and a bottom without ventilation openings.

- SMS: Security Management System – A SMS is software that incorporates multiple security subsystems (e.g., physical access control, intrusion detection, closed circuit television, intercom) into a single platform and graphical user interface.

- TCP/IP: Transport control protocol/Internet protocol incorporated into Microsoft Windows.

- Trough or Ventilated Cable Tray: A fabricated structure consisting of integral or separate longitudinal rails and a bottom having openings

sufficient for the passage of air and using 75 percent or less of the plan area of the surface to support cables.

VV. UPS: Uninterruptible Power Supply

WW. UTP: Unshielded Twisted Pair

XX. Workstation: A PC with software that is configured for specific limited security system functions.

  - QUALITY ASSURANCE

    - Manufacturers Qualifications: The manufacturer shall regularly and presently produce, as one of the manufacturer's principal products, the equipment and material specified for this project and shall have manufactured the item for at least three years.

    - Product Qualification:

      - Manufacturer's product shall have been in satisfactory operation, on three installations of similar size and type as this project, for approximately three years.

      - The Government reserves the right to require the Contractor to submit a list of installations where the products have been in operation before approval.

    - Contractor Qualification:

      - The Contractor or security sub-contractor shall be a licensed security Contractor with a minimum of five (5) years’ experience installing and servicing systems of similar scope and complexity. The Contractor shall be an authorized regional representative of the Security Management System’s (PACS) manufacturer. The Contractor shall provide four (4) current references from clients with systems of similar scope and complexity which became operational in the past three (3) years. At least three (3) of the references shall be utilizing the same system components, in a similar configuration as the proposed system. The references must include a current point of contact, company or agency name, address, telephone number, complete system description, date of completion, and approximate cost of the project. The owner reserves the option to visit the reference sites, with the site owner’s permission and representative, to verify the quality of installation and the references’ level of satisfaction with the system. The Contractor shall provide copies of system manufacturer certification for all technicians. The Contractor shall only utilize factory-trained technicians to

install, program, and service the PACS. The Contractor shall only utilize factory-trained technicians to install, terminate and service controller/field panels and reader modules. The technicians shall have a minimum of five (5) continuous years of technical experience in electronic security systems. The Contractor shall have a local service facility. The facility shall be located within

60 miles of the project site. The local facility shall include sufficient spare parts inventory to support the service requirements associated with this contract. The facility shall also include appropriate diagnostic equipment to perform diagnostic procedures. The Resident Engineer reserves the option of surveying the company’s facility to verify the service inventory and presence of a local service organization.

      - The Contractor shall provide proof project superintendent with BICSI Certified Commercial Installer Level 1, Level 2, or Technician to provide oversight of the project.

      - Cable installer must have on staff a Registered Communication Distribution Designer (RCDD) certified by Building Industry Consulting Service International. The staff member shall provide consistent oversight of the project cabling throughout design, layout, installation, termination and testing.

    - Service Qualifications: There shall be a permanent service organization maintained or trained by the manufacturer which will render satisfactory service to this installation within // four hours of receipt of notification that service is needed. Submit name and address of service organizations.

  - GENERAL ARANGEMENT OF CONTRACT DOCUMENTS

    - The Contract Documents supplement to this specification indicates approximate locations of equipment. The installation and/or locations of the equipment and devices shall be governed by the intent of the design; specification and Contract Documents, with due regard to actual site conditions, recommendations, ambient factors affecting the equipment and operations in the vicinity. The Contract Documents are diagrammatic and do not reveal all offsets, bends, elbows, components, materials, and other specific elements that may be required for proper installation. If any departure from the contract documents is deemed necessary, or in the event of conflicts, the Contractor shall submit

details of such departures or conflicts in writing to the owner or owner’s representative for his or her comment and/or approval before initiating work.

    - Anything called for by one of the Contract Documents and not called for by the others shall be of like effect as if required or called by all, except if a provision clearly designed to negate or alter a provision contained in one or more of the other Contract Documents shall have the intended effect. In the event of conflicts among the Contract Documents, the Contract Documents shall take precedence in the following order: the Form of Agreement; the Supplemental General Conditions; the Special Conditions; the Specifications with attachments; and the drawings.

  - SUBMITTALS

    - Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

    - The Government's approval shall be obtained for all equipment and material before delivery to the job site. Delivery, storage or installation of equipment or material which has not had prior approval will not be permitted at the job site.

    - Submittals for individual systems and equipment assemblies which consist of more than one item or component shall be made for the system or assembly as a whole. Partial submittals will not be considered for approval.

      - Mark the submittals, "SUBMITTED UNDER SECTION	".

      - Submittals shall be marked to show specification reference including the section and paragraph numbers.

      - Submit each section separately.

    - The submittals shall include the following:

      - Information that confirms compliance with contract requirements. Include the manufacturer's name, model or catalog numbers, catalog information, technical data sheets, shop drawings, pictures, nameplate data and test reports as required.

      - Submittals are required for all equipment anchors and supports. Submittals shall include weights, dimensions, center of gravity, standard connections, manufacturer's recommendations and behavior problems (e.g., vibration, thermal expansion,) associated with

equipment or piping so that the proposed installation can be properly reviewed.

      - Parts list which shall include those replacement parts recommended by the equipment manufacturer, quantity of parts, current price and availability of each part.

    - Submittals shall be in full compliance of the Contract Documents. All submittals shall be provided in accordance with this section. Submittals lacking the breath or depth these requirements will be considered incomplete and rejected. Submissions are considered multidisciplinary and shall require coordination with applicable divisions to provide a complete and comprehensive submission package. All submittals shall include adequate descriptive literature, catalog cuts, shop drawings and other data necessary for the Government to ascertain that the proposed equipment and materials comply with specification requirements. Catalog cuts submitted for approval shall be legible and clearly identify equipment being submitted. Additional general provisions are as follows:

      - The Contractor shall schedule submittals in order to maintain the project schedule. For coordination drawings refer to Specification Section 01 33 10 - Design Submittal Procedures, which outline basic submittal requirements and coordination. Section 01 33 10 shall be used in conjunction with this section.

      - The Contractor shall identify variations from requirements of Contract Documents and state product and system limitations, which may be detrimental to successful performance of the completed work or system.

      - Each package shall be submitted at one (1) time for each review and include components from applicable disciplines (e.g., electrical work, architectural finishes, door hardware, etc.) which are required to produce an accurate and detailed depiction of the project.

      - Manufacturer’s information used for submittal shall have pages with items for approval tagged, items on pages shall be identified, and capacities and performance parameters for review shall be clearly marked through use of an arrow or highlighting. Provide space for Resident Engineer and Contractor review stamps.

      - Technical Data Drawings shall be in the latest version of AutoCAD®, drawn accurately, and in accordance with VA CAD Standards CAD Standard Application Guide, and VA BIM Guide. FREEHAND SKETCHES OR COPIED VERSIONS OF THE CONSTRUCTION DOCUMENTS WILL NOT BE ACCEPTED.

The Contractor shall not reproduce Contract Documents or copy standard information as the basis of the Technical Data Drawings. If departures from the technical data drawings are subsequently deemed necessary by the Contractor, details of such departures and the reasons thereof shall be submitted in writing to the Resident Engineer for approval before the initiation of work.

      - Packaging: The Contractor shall organize the submissions according to the following packaging requirements.

        - Binders: For each manual, provide heavy duty, commercial quality, durable three (3) ring vinyl covered loose leaf binders, sized to receive 8.5 x 11 in paper, and appropriate capacity to accommodate the contents. Provide a clear plastic sleeve on the spine to hold labels describing the contents. Provide pockets in the covers to receive folded sheets.

          - Where two (2) or more binders are necessary to accommodate data, correlate data in each binder into related groupings according to the Project Manual table of contents. Cross- referencing other binders where necessary to provide essential information for communication of proper operation and/or maintenance of the component or system.

          - Identify each binder on the front and spine with printed binder title, Project title or name, and subject matter covered. Indicate the volume number if applicable.

        - Dividers: Provide heavy paper dividers with celluloid tabs for each Section. Mark each tab to indicate contents.

        - Protective Plastic Jackets: Provide protective transparent plastic jackets designed to enclose diagnostic software for computerized electronic equipment.

        - Text Material: Where written material is required as part of the manual use the manufacturer's standard printed material, or if not available, specially prepared data, neatly typewritten on 8.5 inches by 11 inches 20 pound white bond paper.

        - Drawings: Where drawings and/or diagrams are required as part of the manual, provide reinforced punched binder tabs on the drawings and bind them with the text.

          - Where oversized drawings are necessary, fold the drawings to the same size as the text pages and use as a foldout.

          - If drawings are too large to be used practically as a foldout, place the drawing, neatly folded, in the front or rear pocket of the binder. Insert a type written page indicating the drawing title, description of contents and drawing location at the appropriate location of the manual.

          - Drawings shall be sized to ensure details and text is of legible size. Text shall be no less than 1/16” tall.

        - Manual Content: Submit in accordance with Section 01 00 00, GENERAL REQUIREMENTS.

          - Maintenance and Operation Manuals: Submit as required for systems and equipment specified in the technical sections. Furnish four copies, bound in hardback binders, (manufacturer's standard binders) or an approved equivalent. Furnish one complete manual as specified in the technical section but in no case later than prior to performance of systems or equipment test and furnish the remaining manuals prior to contract completion.

          - Inscribe the following identification on the cover: the words "MAINTENANCE AND OPERATION MANUAL," the name and location of the system, equipment, building, name of Contractor, and contract number. Include in the manual the names, addresses, and telephone numbers of each subcontractor installing the system or equipment and the local representatives for the system or equipment.

          - The manuals shall include:

            - Internal and interconnecting wiring and control diagrams with data to explain detailed operation and control of the equipment.

            - A control sequence describing start-up, operation, and shutdown.

            - Description of the function of each principal item of equipment.

            - Installation and maintenance instructions.

            - Safety precautions.

            - Diagrams and illustrations.

            - Testing methods.

            - Performance data.

            - Pictorial "exploded" parts list with part numbers. Emphasis shall be placed on the use of special tools and instruments. The list shall indicate sources of supply, recommended spare parts, and name of servicing organization.

            - Appendix; list qualified permanent servicing organizations for support of the equipment, including addresses and certified qualifications.

        - Binder Organization: Organize each manual into separate sections for each piece of related equipment. At a minimum, each manual shall contain a title page, table of contents, copies of Product Data supplemented by drawings and written text, and copies of each warranty, bond, certifications, and service Contract issued. Refer to Group I through V Technical Data Package Submittal requirements for required section content.

        - Title Page: Provide a title page as the first sheet of each manual to include the following information; project name and address, subject matter covered by the manual, name and address of the Project, date of the submittal, name, address, and telephone number of the Contractor, and cross references to related systems in other operating and/or maintenance manuals.

        - Table of Contents: After the title page, include a type written table of contents for each volume, arranged systematically according to the Project Manual format. Provide a list of each product included, identified by product name or other appropriate identifying symbols and indexed to the content of the volume. Where more than one (1) volume is required to hold data for a particular system, provide a comprehensive table of contents for all volumes in each volume of the set.

        - General Information Section: Provide a general information section immediately following the table of contents, listing each product included in the manual, identified by product name.

Under each product, list the name, address, and telephone number of the installer and maintenance Contractor. In addition, list a local source for replacement parts and equipment.

        - Drawings: Provide specially prepared drawings where necessary to supplement the manufacturers printed data to illustrate the relationship between components of equipment or systems or provide control or flow diagrams. Coordinate these drawings with information contained in Project Record Drawings to assure correct illustration of the completed installation.

        - Manufacturer’s Data: Where manufacturer's standard printed data is included in the manuals, include only those sheets that are pertinent to the part or product installed. Mark each sheet to identify each part or product included in the installation. Where more than one (1) item in tabular format is included, identify each item, using appropriate references from the Contract Documents. Identify data that is applicable to the installation and delete references to information which is not applicable.

        - Where manufacturer's standard printed data is not available and the information is necessary for proper operation and maintenance of equipment or systems, or it is necessary to provide additional information to supplement the data included in the manual, prepare written text to provide the necessary information. Organize the text in a consistent format under a separate heading for different procedures. Where necessary, provide a logical sequence of instruction for each operating or maintenance procedure. Where similar or more than one product is listed on the submittal the Contractor shall differentiate by highlighting the specific product to be utilized.

        - Calculations: Provide a section for circuit and panel calculations.

        - Loading Sheets:	Provide a section for DGP Loading Sheets.

        - Certifications: Provide section for Contractor’s manufacturer certifications.

      - Contractor Review: Review submittals prior to transmittal. Determine and verify field measurements and field construction criteria. Verify manufacturer’s catalog numbers and conformance of

submittal with requirements of contract documents. Return non- conforming or incomplete submittals with requirements of the work and contract documents. Apply Contractor’s stamp with signature certifying the review and verification of products occurred, and the field dimensions, adjacent construction, and coordination of information is in accordance with the requirements of the contract documents.

      - Resubmission: Revise and resubmit submittals as required within 15 calendar days of return of submittal. Make resubmissions under procedures specified for initial submittals. Identify all changes made since previous submittal.

      - Product Data: Within 15 calendar days after execution of the contract, the Contractor shall submit for approval a complete list of all of major products proposed for use. The data shall include name of manufacturer, trade name, model number, the associated contract document section number, paragraph number, and the referenced standards for each listed product.

    - Group 1 Technical Data Package: Group I Technical Data Package shall be one submittal consisting of the following content and organization. Refer to VA Special Conditions Document for drawing format and content requirements. The data package shall include the following:

      - Section I - Drawings:

        - General – Drawings shall conform to VA CAD Standards Guide. All text associated with security details shall be 1/8” tall and meet VA text standard for AutoCAD™ drawings.

        - Cover Sheet – Cover sheet shall consist of Project Title and Address, Project Number, Area and Vicinity Maps.

        - General Information Sheets – General Information Sheets shall consist of General Notes, Abbreviations, Symbols, Wire and Cable Schedule, Project Phasing, and Sheet Index.

        - Floor Plans – Floor plans shall be produced from the Architectural backgrounds issued in the Construction Documents. The contractor shall receive floor plans from the prime A/E to develop these drawing sets. Security devices shall be placed on drawings in scale. All text associated with security details shall be 1/8” tall and meet VA text standard for AutoCAD™ drawings. Floor plans shall identify the following:

          - Security devices by symbol,

          - The associated device point number (derived from the loading sheets),

          - Wire & cable types and counts

          - Conduit sizing and routing

          - Conduit riser systems

          - Device and area detail call outs

          - Field of View (FOV) floor plans and site plan noting type of camera, mounting, and the associated field of view based on placement

        - Architectural details – Architectural details shall be produced for each device mounting type (door details for EECS and IDS, Intrusion Detection system (motion sensor, vibration, microwave Motion Sensor and Camera mounting,

        - Riser Diagrams – Contractor shall provide a riser diagram indicating riser architecture and distribution of the SMS throughout the facility (or area in scope).

        - Block Diagrams – Contractor shall provide a block diagram for the entire system architecture and interconnections with SMS subsystems. Block diagram shall identify SMS subsystem (e.g., electronic entry control, intrusion detection, closed circuit television, intercom, and other associated subsystems) integration; and data transmission and media conversion methodologies.

- Security Details:

  - Device Mounting Details – Provide mounting detailed drawing for each security device (physical access control system, intrusion detection, video surveillance and assessment, and intercom systems) for each type of wall and ceiling configuration in project. Device details shall include device, mounting detail, wiring and conduit routing.

  - Details of connections to power supplies and grounding

  - Details of surge protection device installation

  - Sensor detection patterns – Each system sensor shall have associated detection patterns.

  - Equipment Rack Detail – For each equipment rack, provide a scaled detail of the equipment rack location and rack space

utilization. Use of BISCI wire management standards shall be employed to identify wire management methodology. Transitions between equipment racks shall be shown to include use vertical and horizontal latter rack system.

  - Security Control Room – The contractor shall provide a layout plan for the Security Control Room. The layout plan shall identify all equipment and details associated with the installation.

  - Operator Console – The contractor shall provide a layout plan for the Operator Console. The layout plan shall identify all equipment and details associated with the installation. Equipment room - the contractor shall provide a layout plan for the equipment room. The layout plan shall identify all equipment and details associated with the installation.

  - Equipment Room – Equipment room details shall provide architectural, electrical, mechanical, plumbing, IT/Data and associated equipment and device placements both vertical and horizontally.

      - Camera Schedule - A camera schedule shall be developed for each camera. Contractors shall coordinate with the Resident Engineer to determine camera starting numbers and naming conventions. All drawings shall identify wire and cable standardization methodology. Color coding of all wiring conductors and jackets is required and shall be communicated consistently throughout the drawings package submittal. At a minimum, the camera schedule shall include the following information:

        - Item Number

        - Camera Number

        - Naming Conventions

        - Description of Camera Coverage

        - Camera Location

        - Floor Plan Sheet Number

        - Camera Type

        - Mounting Type

        - Standard Detail Reference

        - Power Input & Draw

        - Power Panel Location

        - Remarks Column for Camera

- Section II - Manufacturers’ Data: The data package shall include manufacturers’ data for all materials and equipment, including sensors, local processors and console equipment provided under this specification.

- Section III - System Description and Analysis: The data package shall include system descriptions, analysis, and calculations used in sizing equipment required by these specifications. Descriptions and calculations shall show how the equipment will operate as a system to meet the performance requirements of this specification. The data package shall include the following:

  - Central processor memory size; communication speed and protocol description; rigid disk system size and configuration; flexible disk system size and configuration; back-up media size and configuration; alarm response time calculations; command response time calculations; start-up operations; expansion capability and method of implementation; sample copy of each report specified; and color photographs representative of typical graphics.

  - Software Data: The data package shall consist of descriptions of the operation and capability of the system, and application software as specified.

  - Overall System Reliability Calculations: The data package shall include all manufacturers’ reliability data and calculations required to show compliance with the specified reliability.

- Section IV – Certifications & References: All specified manufacturer’s certifications shall be included with the data package. Contractor shall provide Project references as outlined in Paragraph 1.4 “Quality Assurance”.

    - Group II Technical Data Package

      - The Contractor shall prepare a report of “Current Site Conditions” and submit a report to the Resident Engineer documenting changes to the site, particularly those conditions that affect performance of the system to be installed. The Contractor shall provide specification sheets, or written functional requirements to support the findings, and a cost estimate to correct those site changes or conditions which affect the installation of the system or its

performance. The Contractor shall not correct any deficiency without written permission from the COTR.

      - System Configuration and Functionality (Video Surveillance System): The contractor shall provide the results of the meeting with VA to develop system requirements and functionality including but not limited to:

        - Baseline configuration

        - Schedules (intrusion detection, physical access control, holidays, etc.)

        - System monitoring and reporting (unit level and central control)

        - Naming conventions and descriptors

    - Group III Technical Data Package (Video Surveillance System)

      - Development of Test Procedures: The Contractor will prepare performance test procedures for the system testing. The test procedures shall follow the format of the VA Testing procedures and be customized to the contract requirements. The Contractor will deliver the test procedures to the Resident Engineer for approval at least 60 calendar days prior to the requested test date.

    - Group IV Technical Data Package (Video Surveillance System)

      - Performance Verification Test

        - Based on the successful completion of the pre-delivery test, the Contractor shall finalize the test procedures and report forms for the performance verification test (PVT) and the endurance test. The PVT shall follow the format, layout and content of the pre-delivery test. The Contractor shall deliver the PVT and endurance test procedures to the Resident Engineer for approval. The Contractor may schedule the PVT after receiving written approval of the test procedures.	The Contractor shall deliver the final PVT and endurance test reports within 14 calendar days from completion of the tests. Refer to Part 3 of this section for System Testing and Acceptance requirements.

      - Training Documentation

        - New Facilities and Major Renovations: Familiarization training shall be provided for new equipment or systems. Training can include site familiarization training for VA technicians and administrative personnel. Training shall include general information on new system layout including closet locations,

turnover of the completed system including all documentation, including manuals, software, key systems, and full system administration rights. Lesson plans and training manuals training shall be oriented to type of training to be provided.

        - New Unit Control Room:

          - Provide the security personnel with training in the use, operation, and maintenance of the entire control room system (Unit Control and Equipment Rooms). The training documentation must include the operation and maintenance. The first of the training sessions shall take place prior to system turnover and the second immediately after turnover. Coordinate the training sessions with the Owner. Completed classroom sessions will be witnessed and documented by the Architect/Engineer, and approved by the Resident Engineer. Instruction is not to begin until the system is operational as designed.

          - The training documents will cover the operation and the maintenance manuals and the control console operators’ manuals and service manuals in detail, stressing all important operational and service diagnostic information necessary for the maintenance and operations personnel to efficiently use and maintain all systems.

          - Provide an illustrated control console operator's manual and service manual. The operator's manual shall be written in laymen's language and printed so as to become a permanent reference document for the operators, describing all control panel switch operations, graphic symbol definitions and all indicating functions and a complete explanation of all software.

          - The service manual shall be written in laymen's language and printed so as to become a permanent reference document for maintenance personnel, describing how to run internal self- diagnostic software programs, troubleshoot head end hardware and field devices with a complete scenario simulation of all possible system malfunctions and the appropriate corrective measures.

          - Provide a professional color DVD instructional recording of all the operational procedures described in the operator's manual. All charts used in the training session shall be clearly presented on the video. Any DVD found to be inferior in recording or material content shall be reproduced at no cost until an acceptable DVD is submitted. Provide four copies of the training DVD, one to the architect/engineer and three to the owner.

      - System Configuration and Data Entry:

        - The contractor is responsible for providing all system configuration and data entry for the SMS and subsystems (e.g., cloud access as coordinated with VA OIT, individual camera on- board storage devices, recording rates, days of storage, etc.). All data entry shall be performed per VA standards & guidelines. The Contractor is responsible for participating in all meetings with the client to compile the information needed for data entry. These meetings shall be established at the beginning of the project and incorporated in to the project schedule as a milestone task. The contractor shall be responsible for all data collection, data entry, and system configuration. The contractor shall collect, enter, & program and/or configure the following components:

          - Video surveillance, control and recording systems.

          - All other security subsystems shown in the contract documents.

c. Refer to Part 3 for system programming requirements and planning guidelines.

      - Graphics: Based on CAD as-built drawings developed for the construction project, create all map sets showing locations of all alarms and field devices. Graphical maps of all alarm points installed under this contract including perimeter and exterior alarm points shall be delivered with the system. The Contractor shall create and install all graphics needed to make the system operational. The Contractor shall utilize data from the contract documents, Contractor’s field surveys, and all other pertinent information in the Contractor’s possession to complete the graphics. The Contractor shall identify and request from the COTR, any additional data needed to provide a complete graphics package.

Graphics shall have sufficient level of detail for the system operator to assess the alarm. The Contractor shall supply hard copy, color examples at least 203.2 x 254 mm (8 x 10 in) of each type of graphic to be used for the completed Security system. The graphics examples shall be delivered to the Resident Engineer for review and approval at least 90 calendar days prior to the scheduled date the Contractor requires them.

    - Group V Technical Data Package: Final copies of the manuals shall be delivered to the Resident Engineer as part of the acceptance test. The draft copy used during site testing shall be updated with any changes required prior to final delivery of the manuals. Each manual’s contents shall be identified on the cover. The manual shall include names, addresses, and telephone numbers of each sub-contractor installing equipment or systems, as well as the nearest service representatives for each item of equipment for each system. The manuals shall include a table of contents and tab sheets. Tab sheets shall be placed at the beginning of each chapter or section and at the beginning of each appendix. The final copies delivered after completion of the endurance test shall include all modifications made during installation, checkout, and acceptance. Six (6) hard-copies and one (1) soft copy on CD of each item listed below shall be delivered as a part of final systems acceptance.

      - Functional Design Manual: The functional design manual shall identify the operational requirements for the entire system and explain the theory of operation, design philosophy, and specific functions. A description of hardware and software functions, interfaces, and requirements shall be included for all system operating modes. Manufacturer developed literature may be used; however, shall be produced to match the project requirements.

      - Equipment Manual: A manual describing all equipment furnished including:

        - General description and specifications; installation and checkout procedures; equipment electrical schematics and layout drawings; system schematics and layout drawings; alignment and calibration procedures; manufacturer’s repair list indicating sources of supply; and interface definition.

      - Software Manual: The software manual shall describe the functions of all software and include all other information necessary to enable proper loading, testing, and operation. The manual shall include:

        - Definition of terms and functions; use of system and applications software; procedures for system initialization, start-up, and shutdown; alarm reports; reports generation, database format and data entry requirements; directory of all disk files; and description of all communications protocols including data formats, command characters, and a sample of each type of data transfer.

      - Operator’s Manual: The operator’s manual shall fully explain all procedures and instructions for the operation of the system, including:

        - Computers and peripherals; system start-up and shutdown procedures; use of system, command, and applications software; recovery and restart procedures; graphic alarm presentation; use of report generator and generation of reports; data entry; operator commands’ alarm messages, and printing formats; and system access requirements.

      - Maintenance Manual: The maintenance manual shall include descriptions of maintenance for all equipment including inspection, recommend schedules, periodic preventive maintenance, fault diagnosis, and repair or replacement of defective components.

      - Spare Parts & Components Data: At the conclusion of the Contractor's work, the Contractor shall submit to the Resident Engineer a complete list of the manufacturer's recommended spare parts and components required to satisfactorily maintain and service the systems, as well as unit pricing for those parts and components.

      - Operation, Maintenance & Service Manuals: The Contractor shall provide two (2) complete sets of operating and maintenance manuals in the form of an instructional manual for use by the VA Security Guard Force personnel. The manuals shall be organized into suitable sets of manageable size. Where possible, assemble instructions for similar equipment into a single binder. If multiple volumes are required, each volume shall be fully indexed and coordinated.

      - Equipment and Systems Maintenance Manual: The Contractor shall provide the following descriptive information for each piece of equipment, operating system, and electronic system:

        - Equipment and/or system function.

        - Operating characteristics.

        - Limiting conditions.

        - Performance curves.

        - Engineering data and test.

        - Complete nomenclature and number of replacement parts.

        - Provide operating and maintenance instructions including assembly drawings and diagrams required for maintenance and a list of items recommended to stock as spare parts.

        - Provide information detailing essential maintenance procedures including the following: routine operations, troubleshooting guide, disassembly, repair and re-assembly, alignment, adjusting, and checking.

        - Provide information on equipment and system operating procedures, including the following; start-up procedures, routine and normal operating instructions, regulation and control procedures, instructions on stopping, shut-down and emergency instructions, required sequences for electric and electronic systems, and special operating instructions.

        - Manufacturer equipment and systems maintenance manuals are permissible.

      - Project Redlines: During construction, the Contractor shall maintain an up-to-date set of construction redlines detailing current location and configuration of the project components. The redline documents shall be marked with the words ‘Master Redlines’ on the cover sheet and be maintained by the Contractor in the project office. The Contractor will provide access to redline documents anytime during the project for review and inspection by the Resident Engineer or authorized Office of Protection Services representative. Master redlines shall be neatly maintained throughout the project and secured under lock and key in the contractor’s onsite project office. Any project component or assembly that is not installed in strict accordance with the drawings shall be as noted on the drawings. Prior to producing

Record Construction Documents, the contractor will submit the Master Redline document to the Resident Engineer for review and approval of all changes or modifications to the documents. Each sheet shall have Resident Engineer initials indicating authorization to produce “As Built” documents. Field drawings shall be used for data gathering & field changes. These changes shall be made to the master redline documents daily. Field drawings shall not be considered “master redlines”.

      - Record Specifications: The Contractor shall maintain one (1) copy of the Project Specifications, including addenda and modifications issued, for Project Record Documents. The Contractor shall mark the Specifications to indicate the actual installation where the installation varies substantially from that indicated in the Contract Specifications and modifications issued. (Note related Project Record Drawing information where applicable). The Contractor shall pay particular attention to substitutions, selection of product options, and information on concealed installations that would be difficult to identify or measure and record later. Upon completion of the mark ups, the Contractor shall submit record Specifications to the COTR. As with master relines, Contractor shall maintain record specifications for Resident Engineer review and inspection at any time.

      - Record Product Data: The Contractor shall maintain one (1) copy of each Product Data submittal for Project Record Document purposes. The Data shall be marked to indicate the actual product installed where the installation varies substantially from that indicated in the Product Data submitted. Significant changes in the product delivered to the site and changes in manufacturer's instructions and recommendations for installation shall be included. Particular attention will be given to information on concealed products and installations that cannot be readily identified or recorded later. Note related Change Orders and mark up of Record Construction Documents, where applicable. Upon completion of mark up, submit a complete set of Record Product Data to the COTR.

      - Miscellaneous Records: The Contractor shall maintain one (1) copy of miscellaneous records for Project Record Document purposes. Refer to other Specifications for miscellaneous record-keeping

requirements and submittals concerning various construction activities. Before substantial completion, complete miscellaneous records and place in good order, properly identified and bound or filed, ready for use and reference. Categories of requirements resulting in miscellaneous records include a minimum of the following:

        - Certificates received instead of labels on bulk products.

        - Testing and qualification of tradesmen. (“Contractor’s Qualifications”)

        - Documented qualification of installation firms.

        - Load and performance testing.

        - Inspections and certifications.

        - Final inspection and correction procedures.

        - Project schedule

      - Record Construction Documents (Record As-Built)

        - Upon project completion, the contractor shall submit the project master redlines to the Resident Engineer prior to development of Record construction documents. The Resident Engineer shall be given a minimum of a thirty (30) day review period to determine the adequacy of the master redlines. If the master redlines are found suitable by the Resident Engineer, the Resident Engineer will initial and date each sheet and turn redlines over to the contractor for as built development.

        - The Contractor shall provide the Resident Engineer a complete set of "as-built" drawings and original master redlined marked "as- built" blue-line in the latest version of AutoCAD drawings unlocked on CD or DVD. The as-built drawing shall include security device number, security closet connection location, data gathering panel number, and input or output number as applicable. All corrective notations made by the Contractor shall be legible when submitted to the COTR. If, in the opinion of the COTR, any redlined notation is not legible, it shall be returned to the Contractor for re-submission at no extra cost to the Owner. The Contractor shall organize the Record Drawing sheets into manageable sets bound with durable paper cover sheets with suitable titles, dates, and other identifications printed on the cover. The submitted as built shall be in editable formats and

the ownership of the drawings shall be fully relinquished to the owner.

        - Where feasible, the individual or entity that obtained record data, whether the individual or entity is the installer, sub- contractor, or similar entity, is required to prepare the mark up on Record Drawings. Accurately record the information in a comprehensive drawing technique. Record the data when possible after it has been obtained. For concealed installations, record and check the mark up before concealment. At the time of substantial completion, submit the Record Construction Documents to the COTR. The Contractor shall organize into bound and labeled sets for the COTR's continued usage. Provide device, conduit, and cable lengths on the conduit drawings. Exact in- field conduit placement/routings shall be shown. All conduits shall be illustrated in their entire length from termination in security closets; no arrowed conduit runs shall be shown. Pull box and junction box sizes are to be shown if larger than 100mm (4 inch).

    - FIPS 201 Compliance Certificates

      - Provide Certificates for all software components and device types utilizing credential verification. Provide certificates for:

        - Facial Image Capturing Camera

        - PIV Middleware

        - Template Matcher

        - Electromagnetically Opaque Sleeve

        - Certificate Management

          - CAK Authentication System

          - PIV Authentication System

          - Certificate Validator

          - Cryptographic Module

    - Approvals will be based on complete submission of manuals together with shop drawings.

    - After approval and prior to installation, furnish the Resident Engineer with one sample of each of the following:

      - A 300 mm (12 inch) length of each type and size of wire and cable along with the tag from the coils of reels from which the samples were taken.

      - Each type of conduit and pathway coupling, bushing and termination fitting.

      - Conduit hangers, clamps and supports.

      - Duct sealing compound.

  - APPLICABLE PUBLICATIONS

    - The publications listed below (including amendments, addenda, revisions, supplement, and errata) form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.

    - American National Standards Institute (ANSI)/ International Code Council (ICC):

A117.1..................Standard on Accessible and Usable Buildings and

Facilities

    - American National Standards Institute (ANSI)/ Security Industry Association (SIA):

TVAC-01.................CCTV to Access Control Standard - Message Set for System Integration

    - American National Standards Institute (ANSI)/Electronic Industries Alliance (EIA):

330-09..................Electrical Performance Standards for CCTV

Cameras

375A-76.................Electrical Performance Standards for CCTV

Monitors

F. American Society for Testing and Materials (ASTM)

B1-07...................Standard Specification for Hard-Drawn Copper

Wire

B3-07...................Standard Specification for Soft or Annealed

Copper Wire

B8-04...................Standard Specification for Concentric-Lay-

Stranded Copper Conductors, Hard, Medium-Hard, or Soft

H. Department of Justice: American Disability Act (ADA)

28 CFR Part 36-2010 ADA Standards for Accessible Design

I. Department of Veterans Affairs:

VHA National CAD Standard Application Guide, 2006

VA BIM Guide, V1.0 10

K. Federal Information Processing Standards (FIPS):

FIPS-201-1..............Personal Identity Verification (PIV) of Federal

Employees and Contractors

L. Federal Specifications (Fed. Spec.):

A-A-59544-08............Cable and Wire, Electrical (Power, Fixed

Installation)

M. Government Accountability Office (GAO):

GAO-03-8-02.............Security Responsibilities for Federally Owned and Leased Facilities

N. Homeland Security Presidential Directive (HSPD):

HSPD-12.................Policy for a Common Identification Standard for

Federal Employees and Contractors

O. Institute of Electrical and Electronics Engineers (IEEE):

81-1983.................IEEE Guide for Measuring Earth Resistivity,

Ground Impedance, and Earth Surface Potentials of a Ground System

802.3af-08..............Power over Ethernet Standard

802.3at-09 .............Power over Ethernet (PoE) Plus Standard C2-07...................National Electrical Safety Code

C62.41-02...............IEEE Recommended Practice on Surge Voltages in

Low-Voltage AC Power Circuits

C95.1-05................Standards for Safety Levels with Respect to

Human Exposure in Radio Frequency Electromagnetic Fields

Q. National Electrical Contractors Association

303-2005................Installing Closed Circuit Television (CCTV)

Systems

R. National Electrical Manufactures Association (NEMA):

250-08..................Enclosures for Electrical Equipment (1000 Volts

Maximum)

TC-3-04.................PVC Fittings for Use with Rigid PVC Conduit and

Tubing

FB1-07..................Fittings, Cast Metal Boxes and Conduit Bodies

for Conduit, Electrical Metallic Tubing and Cable

S. National Fire Protection Association (NFPA):

70-11................... National Electrical Code (NEC)

731-08..................Standards for the Installation of Electric

Premises Security Systems 99-2005.................Health Care Facilities

W. Section 508 of the Rehabilitation Act of 1973

X. Security Industry Association (SIA):

AG-01 ..................Security CAD Symbols Standards

Y. Underwriters Laboratories, Inc. (UL):

1-05....................Flexible Metal Conduit

5-04....................Surface Metal Raceway and Fittings

6-07....................Rigid Metal Conduit

44-05...................Thermoset-Insulated Wires and Cables

50-07...................Enclosures for Electrical Equipment

83-08...................Thermoplastic-Insulated Wires and Cables

294-99..................The Standard of Safety for Access Control

System Units

360-09..................Liquid-Tight Flexible Steel Conduit

444-08..................Safety Communications Cables

467-07..................Electrical Grounding and Bonding Equipment

486A-03.................Wire Connectors and Soldering Lugs for Use with

Copper Conductors

486C-04.................Splicing Wire Connectors

486D-05.................Insulated Wire Connector Systems for

Underground Use or in Damp or Wet Locations 486E-00.................Equipment Wiring Terminals for Use with

Aluminum and/or Copper Conductors

493-07..................Thermoplastic-Insulated Underground Feeder and

Branch Circuit Cable 514A-04.................Metallic Outlet Boxes

514B-04.................Fittings for Cable and Conduit

51-05...................Schedule 40 and 80 Rigid PVC Conduit

651-05..................Schedule 40 and 80 Rigid PVC Conduit

797-07..................Electrical Metallic Tubing

1242-06.................Intermediate Metal Conduit

1479-03.................Fire Tests of Through-Penetration Fire Stops

1981-03.................Central Station Automation System

60950...................Safety of Information Technology Equipment

60950-1.................Information Technology Equipment - Safety -

Part 1: General Requirements

Z. Uniform Federal Accessibility Standards (UFAS) 1984

AA. United States Department of Commerce:

Special Pub 500-101 ....Care and Handling of Computer Magnetic Storage

Media

  - COORDINATION

    - Coordinate arrangement, mounting, and support of electronic safety and security equipment:

      - To allow maximum possible headroom unless specific mounting heights that reduce headroom are indicated.

      - To provide for ease of disconnecting the equipment with minimum interference to other installations.

      - To allow right of way for piping and conduit installed at required slope.

      - So connecting raceways, cables, wireways, cable trays, and busways will be clear of obstructions and of the working and access space of other equipment.

    - Coordinate installation of required supporting devices and set sleeves in masonry walls, and other structural components as they are constructed.

    - Coordinate location of access panels and doors for electronic safety and security items that are behind finished surfaces or otherwise concealed.

  - MAINTENANCE & SERVICE

    - General Requirements

      - The Contractor shall provide all services required and equipment necessary to maintain the entire integrated electronic security system in an operational state as specified for a period of one (1) year after formal written acceptance of the system and provide a cost for a full five (5) years of maintenance and service. The Contractor shall provide all necessary material required for performing scheduled adjustments or other non-scheduled work. Impacts on facility operations shall be minimized when performing scheduled adjustments or other non-scheduled work. See also General Project Requirements.

    - Description of Work

      - The adjustment and repair of the security system includes all software updates, panel firmware, and the following new items computers equipment, communications transmission equipment and data transmission media (DTM), local processors, security system sensors, facility interface, signal transmission equipment, and video equipment.

    - Personnel

      - Service personnel shall be certified in the maintenance and repair of the selected type of equipment and qualified to accomplish all work promptly and satisfactorily. The Resident Engineer shall be advised in writing of the name of the designated service representative, and of any change in personnel. The Resident Engineer shall be provided copies of system manufacturer certification for the designated service representative.

    - Schedule of Work

      - The work shall be performed during regular working hours, Monday through Friday, excluding federal holidays.

    - System Inspections

      - These inspections shall include:

a. The Contractor shall perform two (2) minor inspections at six (6) month intervals or more if required by the manufacturer, and two

(2) major inspections offset equally between the minor inspections to effect quarterly inspection of alternating magnitude.

- Minor Inspections shall include visual checks and operational tests of all console equipment, peripheral equipment, local processors, sensors, electrical and mechanical controls, and adjustments on printers.

- Major Inspections shall include all work described for Minor Inspections and the following: clean all system equipment and local processors including interior and exterior surfaces; perform diagnostics on all equipment; operational tests of the CPU, switcher, peripheral equipment, recording devices, monitors, picture quality from each camera; check, walk test, and calibrate each sensor; run all system software diagnostics

and correct all problems; and resolve any previous outstanding problems.

    - Emergency Service

      - The owner shall initiate service calls whenever the system is not functioning properly. The Contractor shall provide the Owner with an emergency service center telephone number. The emergency service center shall be staffed 24 hours a day 365 days a year. The Owner shall have sole authority for determining catastrophic and non- catastrophic system failures within parameters stated in General Project Requirements.

        - For catastrophic system failures, the Contractor shall provide same day four (4) hour service response with a defect correction time not to exceed eight (8) hours from [arrival on site]. Catastrophic system failures are defined as any system failure that the Owner determines will place the facility(s) at increased risk.

        - For non-catastrophic failures, the Contractor within eight (8) hours with a defect correction time not to exceed 24 hours from notification.

    - Operation

      - Performance of scheduled adjustments and repair shall verify operation of the system as demonstrated by the applicable portions of the performance verification test.

    - Records & Logs

      - The Contractor shall maintain records and logs of each task and organize cumulative records for each component and for the complete system chronologically. A continuous log shall be submitted for all devices. The log shall contain all initial settings, calibration, repair, and programming data. Complete logs shall be maintained and available for inspection on site, demonstrating planned and systematic adjustments and repairs have been accomplished for the system.

    - Work Request

      - The Contractor shall separately record each service call request, as received. The record shall include the serial number identifying the component involved, its location, date and time the call was received, specific nature of trouble, names of service personnel

assigned to the task, instructions describing the action taken, the amount and nature of the materials used, and the date and time of commencement and completion. The Contractor shall deliver a record of the work performed within five (5) working days after the work was completed.

    - System Modifications

      - The Contractor shall make any recommendations for system modification in writing to the Resident Engineer. No system modifications, including operating parameters and control settings, shall be made without prior written approval from the Resident Engineer. Any modifications made to the system shall be incorporated into the operation and maintenance manuals and other documentation affected.

    - Software

      - The Contractor shall provide all software updates when approved by the Owner from the manufacturer during the installation and 12-month warranty period and verify operation of the system. These updates shall be accomplished in a timely manner, fully coordinated with the system operators, and incorporated into the operations and maintenance manuals and software documentation. There shall be at least one (1) scheduled update near the end of the first year’s warranty period, at which time the Contractor shall install and validate the latest released version of the Manufacturer’s software. All software changes shall be recorded in a log maintained in the unit control room. An electronic copy of the software update shall be maintained within the log. At a minimum, the contractor shall provide a description of the modification, when the modification occurred, and name and contact information of the individual performing the modification. The log shall be maintained in a white

3 ring binder and the cover marked “SOFTWARE CHANGE LOG”.

  - MINIMUM REQUIREMENTS

    - References to industry and trade association standards and codes are minimum installation requirement standards.

    - Drawings and other specification sections shall govern in those instances where requirements are greater than those specified in the above standards.

  - DELIVERY, STORAGE, & HANDLING

    - Equipment and materials shall be protected during shipment and storage against physical damage, dirt, moisture, cold and rain:

      - During installation, enclosures, equipment, controls, controllers, circuit protective devices, and other like items, shall be protected against entry of foreign matter; and be vacuum cleaned both inside and outside before testing and operating and repainting if required.

      - Damaged equipment shall be, as determined by the Resident Engineer, placed in first class operating condition or be returned to the source of supply for repair or replacement.

      - Painted surfaces shall be protected with factory installed removable heavy craft paper, sheet vinyl or equal.

      - Damaged paint on equipment and materials shall be refinished with the same quality of paint and workmanship as used by the manufacturer so repaired areas are not obvious.

    - Central Station, Workstations, and Controllers:

      - Store in temperature and humidity controlled environment in original manufacturer's sealed containers. Maintain ambient temperature between 10 to 30 deg C (50 to 85 deg F), and not more than 80 percent relative humidity, non-condensing.

      - Open each container; verify contents against packing list, and file copy of packing list, complete with container identification for inclusion in operation and maintenance data.

      - Mark packing list with designations which have been assigned to materials and equipment for recording in the system labeling schedules generated by cable and asset management system.

      - Save original manufacturer's containers and packing materials and deliver as directed under provisions covering extra materials.

  - PROJECT CONDITIONS

    - Environmental Conditions: System shall be capable of withstanding the following environmental conditions without mechanical or electrical damage or degradation of operating capability:

      - Interior, Controlled Environment: System components, except central-station control unit, installed in temperature-controlled interior environments shall be rated for continuous operation in ambient conditions of 2 to 50 deg C (36 to 122 deg F) dry bulb and

20 to 90 percent relative humidity, non-condensing. NEMA 250, Type

1 enclosure.

      - Interior, Uncontrolled Environment: System components installed in non-temperature-controlled interior environments shall be rated for continuous operation in ambient conditions of -18 to 50 deg C (0 to 122 deg F) dry bulb and 20 to 90 percent relative humidity, non- condensing. NEMA 250, Type 4X enclosures.

      - Exterior Environment: System components installed in locations exposed to weather shall be rated for continuous operation in ambient conditions of -34 to 50 deg C (-30 to 122 deg F) dry bulb and 20 to 90 percent relative humidity, condensing. Rate for continuous operation where exposed to rain as specified in NEMA 250, winds up to 137 km/h (85 mph) and snow cover up to 610 mm (24 in) thick. NEMA 250, Type 4X enclosures.

      - Corrosive Environment: For system components subjected to corrosive fumes, vapors, and wind-driven salt spray in coastal zones, provide NEMA 250, Type 4X enclosures.

    - Security Environment: Use vandal resistant enclosures in high-risk areas where equipment may be subject to damage.

    - Console: All console equipment shall, unless noted otherwise, be rated for continuous operation under ambient environmental conditions of 15.6 to 29.4 deg C (60 to 85 deg F) and a relative humidity of 20 to 80 percent.

  - EQUIPMENT AND MATERIALS

    - Materials and equipment furnished shall be of current production by manufacturers regularly engaged in the manufacture of such items, for which replacement parts shall be available.

    - When more than one unit of the same class of equipment is required, such units shall be the product of a single manufacturer.

    - Equipment Assemblies and Components:

      - Components of an assembled unit need not be products of the same manufacturer.

      - Manufacturers of equipment assemblies, which include components made by others, shall assume complete responsibility for the final assembled unit.

      - Components shall be compatible with each other and with the total assembly for the intended service.

      - Constituent parts which are similar shall be the product of a single manufacturer.

    - Factory wiring shall be identified on the equipment being furnished and on all wiring diagrams.

  - ELECTRICAL POWER

    - Electrical power of 120 Volts Alternating Current (VAC) shall be existing in the existing TR rooms. VA OIT shall confirm and verify existing power infrastructure is sufficient to support the associated active OIT components (network switches) required to support CCTV additions to each TR.. Additional locations requiring primary power required by the security system shall be identified by OIT and will be shown as part of these contract documents. Primary power for the security system shall be configured to switch to emergency backup sources automatically if interrupted without degradation of any critical system function.

    - Failure of any on-line battery shall be detected and reported as a fault condition. Battery backed-up power supplies shall be provided sized for [8] hours of operation at actual connected load. Requirements for additional power or locations shall be included with the contract to support equipment and systems offered. The following minimum requirements shall be provided for power sources and equipment provided under the scope of this campus video surveillance system replacement project.

      - Emergency Generator

        - Video Monitors: Unit Control Room

        - Outlets: Security Outlets dedicated to security equipment racks or security enclosure assemblies.

        - Security Device Power Supplies (PoE extenders, OIT network switches, etc.) powered from the security closets or remotely: various locations

        - VASS Camera Power Supplies: Telecommunication Rooms (TR)

        - VASS Pan/Tilt Units: Various Locations

        - VASS Outdoor Housing Heaters and Blowers: Various Sites

      - Uninterruptible Power Supply (UPS) on Emergency Power

        - The following 120VAC circuits shall be provided by others. The Security Contractor shall coordinate exact locations with the Government:

          - Security System Monitors and Keyboards: Control Room

          - CPU: Control Equipment Room

          - Communications equipment: Control Equipment Room and various sites.

          - VASS Matrix Switcher: Control Equipment Room

          - VASS: Control Equipment Room

          - Network switches

  - TRANSIENT VOLTAGE SUPPRESSION, POWER SURGE SUPPLESION, & GROUNDING

    - Transient Voltage Surge Suppression: All cables and conductors extending beyond building façade, except fiber optic cables, which serve as communication, control, or signal lines shall be protected against Transient Voltage surges and have Transient Voltage Surge Suppression (TVSS) protection. The TVSS device shall be UL listed in accordance with Standard TIA 497B installed at each end. Lighting and surge suppression shall be a multi-strike variety and include a fault indicator. Protection shall be furnished at the equipment and additional triple solid state surge protectors rated for the application on each wire line circuit shall be installed within 914.4 mm (3 ft) of the building cable entrance. Fuses shall not be used for surge protection. The inputs and outputs shall be tested in both normal mode and common mode to verify there is no interference.

      - A 10-microsecond rise time by 1000 microsecond pulse width waveform with a peak voltage of 1500 volts and a peak current of 60 amperes.

      - An 8-microsecond rise time by 20-microsecond pulse width waveform with a peak voltage of 1000 volts and a peak current of 500 amperes.

      - Maximum series current: 2 AMPS. Provide units manufactured by Advanced Protection Technologies, model # TE/FA 10B or TE/FA 20B.

      - Operating Temperature and Humidity: -40 to 85 deg C (-40 to 185 deg F), 0 to 95 percent relative humidity.

    - Grounding and Surge Suppression

      - The Security Contractor shall provide grounding and surge suppression to stabilize the voltage under normal operating conditions. To ensure the operation of over current devices, such

as fuses, circuit breakers, and relays, under ground-fault conditions.

      - Security Contractor shall engineer and provide proper grounding and surge suppression as required by local jurisdiction and prevailing codes and standards referenced in this document.

      - Principal grounding components and features. Include main grounding buses and grounding and bonding connections to service equipment.

      - Details of interconnection with other grounding systems. The lightning protection system shall be provided by the Security Contractor.

      - Locations and sizes of grounding conductors and grounding buses in electrical, data, and communication equipment rooms and closets.

      - AC power receptacles are not to be used as a ground reference point.

      - Any cable that is shielded shall require a ground in accordance with the best practices of the trade and manufactures installation instructions.

      - Protection should be provided at both ends of cabling.

  - COMPONENT ENCLOSURES

    - Construction of Enclosures

      - Consoles, power supply enclosures, and terminal cabinets, control units, wiring gutters, and other component housings, collectively referred to as enclosures, shall be so formed and assembled as to be sturdy and rigid.

      - Thickness of metal in-cast and sheet metal enclosures of all types shall not be less than those in Tables I and II, UL 611. Sheet steel used in fabrication of enclosures shall be not less than 14 gauge. Consoles shall be 16-gauge.

      - Doors and covers shall be flanged. Enclosures shall not have pre- punched knockouts. Where doors are mounted on hinges with exposed pins, the hinges shall be of the tight pin type or the ends of hinge pins shall be tack welded to prevent removal. Doors having a latch edge length of less than 609.6 mm (24 in) shall be provided with a single construction core. Where the latch edge of a hinged door is more than 609.6 mm (24 in) or more in length, the door shall be provided with a three-point latching device with construction core; or alternatively with two, one located near each end.

      - Any ventilator openings in enclosures and cabinets shall conform to the requirements of UL 611. Unless otherwise indicated, sheet metal enclosures shall be designed for wall mounting with tip holes slotted. Mounting holes shall be in positions that remain accessible when all major operating components are in place and the door is open but shall be in accessible when the door is closed.

      - Covers of pull and junction boxes provided to facilitate initial installation of the system shall be held in place by tamper proof Torx Center post security screws. Stenciled or painted labels shall be affixed to such boxes indicating they contain no connections. These labels shall not indicate the box is part of the Electronic Security System (ESS).

    - Consoles: All consoles and vertical equipment racks shall include a forced air-cooling system to be provided by others.

      - Console racks:

        - Forced air fans shall be installed in the top rear of each console bay. The forced air fan shall consist of one fan rated at 105 CFM mounted to a 133mm vented blank panel the noise level of each fan shall not exceed 55 decibels. The fans shall be installed so air is pulled from the bottom of the rack or cabinet and exhausted out the top.

        - Console racks are to be provided with flush mounted hinged rear doors with recessed locking latch on the bottom and middle sections of the consoles. Provide code access to support wiring for devices located on the work surfaces.

    - Tamper Provisions and Tamper Switches:

      - Enclosures, cabinets, housings, boxes and fittings or every product description having hinged doors or removable covers and which contain circuits, or the integrated security system and its power supplies shall be provided with cover operated, corrosion-resistant tamper switches.

      - Tamper switches shall be arranged to initiate an alarm signal that will report to the monitoring station when the door or cover is moved. Tamper switches shall be mechanically mounted to maximize the defeat time when enclosure covers are opened or removed. It shall take longer than 1 second to depress or defeat the tamper switch after opening or removing the cover. The enclosure and

tamper switch shall function together in such a manner as to prohibit direct line of sign to any internal component before the switch activates.

      - Tamper switches shall be inaccessible until the switch is activated. Have mounting hardware concealed so the location of the switch cannot be observed from the exterior of the enclosure. Be connected to circuits which are under electrical supervision at all times, irrespective of the protection mode in which the circuit is operating. Be spring-loaded and held in the closed position by the door or cover and be wired so they break the circuit when the door cover is disturbed. Tamper circuits shall be adjustable type screw sets and shall be adjusted by the contractor to eliminate nuisance alarms associated with incorrectly mounted tamper device shall annunciate prior to the enclosure door opening (within 1/4 “ tolerance. The tamper device or its components shall not be visible or accessing with common tools to bypass when the enclosure is in the secured mode.

      - The single gang junction boxes for the portrait alarming and pull boxes with less than 102 square mm will not require tamper switches.

      - All enclosures over 305 square mm shall be hinged with an enclosure lock.

      - Control Enclosures: Maintenance/Safety switches on control enclosures, which must be opened to make routing maintenance adjustments to the system and to service the power supplies, shall be push/pull-set automatic reset type.

      - Provide one (1) enclosure tamper switch for each 609 linear mm of enclosure lock side opening evenly spaced.

      - All security screws shall be Torx-Post Security Screws.

      - The contractor shall provide the owner with two (2) torx-post screwdrivers.

  - ELECTRONIC COMPONENTS

    - All electronic components of the system shall be of the solid-state type, mounted on printed circuit boards conforming to UL 796. Boards shall be plug-in, quick-disconnect type. Circuitry shall not be so densely placed as to impede maintenance. All power-dissipating components shall incorporate safety margins of not less than 25 percent

with respect to dissipation ratings, maximum voltages, and current- carrying capacity.

  - SUBSTITUTE MATERIALS & EQUIPMENT

    - Where variations from the contract requirements are requested in accordance with the GENERAL CONDITIONS and Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES, the connecting work and related components shall include, but not be limited to additions or changes to branch circuits, circuit protective devices, conduits, wire, feeders, controls, panels and installation methods.

    - In addition to this Section the Security Contractor shall also reference Section II, Products and associated divisions. The Resident Engineer shall have final authority on the authorization or refusal of substitutions. If there are no proposed substitutions, a statement in writing from the Contractor shall be submitted to the Resident Engineer stating same. In the preparation of a list of substitutions, the following information shall be included, as a minimum:

      - Identity of the material or devices specified for which there is a proposed substitution.

      - Description of the segment of the specification where the material or devices are referenced.

      - Identity of the proposed substitute by manufacturer, brand name, catalog or model number and the manufacturer’s product name.

      - A technical statement of all operational characteristic expressing equivalence to items to be substituted and comparison, feature-by- feature, between specification requirements and the material or devices called for in the specification; and Price differential.

    - Materials Not Listed: Furnish all necessary hardware, software, programming materials, and supporting equipment required to place the specified major subsystems in full operation. Note that some supporting equipment, materials, and hardware may not be described herein. Depending on the manufacturers selected by the COTR, some equipment, materials and hardware may not be contained in either the Contract Documents or these written specifications but are required by the manufacturer for complete operation according to the intent of the design and these specifications. In such cases, the Resident Engineer shall be given the opportunity to approve the additional equipment, hardware and materials that shall be fully identified in the bid and in

the equipment list submittal. The Resident Engineer shall be consulted in the event there is any question about which supporting equipment, materials, or hardware is intended to be included.

    - Response to Specification: The Contractor shall submit a point-by- point statement of compliance with each paragraph of the security specification. The statement of compliance shall list each paragraph by number and indicate “COMPLY” opposite the number for each paragraph where the Contractor fully complies with the specification. Where the proposed system cannot meet the requirements of the paragraph, and does not offer an equivalent solution, the offers shall indicate “DOES NOT COMPLY” opposite the paragraph number. Where the proposed system does not comply with the paragraph as written, but the bidder feels it will accomplish the intent of the paragraph in a manner different from that described, the offers shall indicate “COMPARABLE”. The offers shall include a statement fully describing the “comparable” method of satisfying the requirement. Where a full and concise description is not provided, the offered system shall be considered as not complying with the specification. Any submission that does not include a point- by-point statement of compliance, as described above, shall be disqualified. Submittals for products shall be in precise order with the product section of the specification. Submittals not in proper sequence will be rejected.

  - LIKE ITEMS

    - Where two or more items of equipment performing the same function are required, they shall be exact duplicates produced by one manufacturer. All equipment provided shall be complete, new, and free of any defects.

  - WARRANTY

    - The Contractor shall, as a condition precedent to the final payment, execute a written guarantee (warranty) to the COTR certifying all contract requirements have been completed according to the final specifications. Contract drawings and the warranty of all materials and equipment furnished under this contract are to remain in satisfactory operating condition (ordinary wear and tear, abuse and causes beyond his control for this work accepted) for one (1) year from the date the Contactor received written notification of final acceptance from the COTR. Demonstration and training shall be performed prior to system acceptance. All defects or damages due to

faulty materials or workmanship shall be repaired or replaced without delay, to the COTR's satisfaction, and at the Contractor's expense.

The Contractor shall provide quarterly inspections during the warranty period. The contractor shall provide written documentation to the COTR on conditions and findings of the system and device(s). In addition, the contractor shall provide written documentation of test results and stating what was done to correct any deficiencies. The first inspection shall occur 90 calendar days after the acceptance date. The last inspection shall occur 30 calendar days prior to the end of the warranty. The warranty period shall be extended until the last inspection and associated corrective actions are complete. When equipment and labor covered by the Contractor's warranty, or by a manufacturer's warranty, have been replaced or restored because of its failure during the warranty period, the warranty period for the replaced or repaired equipment or restored work shall be reinstated for a period equal to the original warranty period, and commencing with the date of completion of the replacement or restoration work. In the event any manufacturer customarily provides a warranty period greater than one (1) year, the Contractor's warranty shall be for the same duration for that component.

1.22 SINGULAR NUMBER

Where any device or part of equipment is referred to in these specifications in the singular number (e.g., "the switch"), this reference shall be deemed to apply to as many such devices as are required to complete the installation as shown on the drawings.

PART 2 – PRODUCTS

  - EQUIPMENT AND MATERIALS

    - All equipment associated within the Security Control Room, Security Console and Security Equipment Room shall be UL 827, UL 1981, and UL 60950 compliant and rated for continuous operation. Environmental conditions (i.e. temperature, humidity, wind, and seismic activity) shall be taken under consideration at each facility and site location prior to installation of the equipment.

    - All equipment shall operate on a 120 or 240 volts alternating current (VAC); 50 Hz or 60 Hz AC power system unless documented otherwise in subsequent sections listed within this specification. All equipment

shall have a back-up source of power that will provide a minimum of 8 hours of run time in the event of a loss of primary power to the facility.

    - The system shall be designed, installed, and programmed in a manner that will allow for ease of operation, programming, servicing, maintenance, testing, and upgrading of the system.

    - All equipment and materials for the system will be compatible to ensure correct operation.

  - EQUIPMENT ITEMS

    - The Security Management System shall provide full interface with all components of the security subsystem as follows:

      - Shall allow for communication between the Physical Access Control System and Database Management and all subordinate work and monitoring stations, enrollment centers for badging and biometric devices as part of the PACS, local annunciation centers, the electronic Security Management System (SMS), and all other VA redundant or backup command center or other workstations locations.

      - Shall provide automatic continuous communication with all systems that are monitored by the SMS, and shall automatically annunciate any communication failures or system alarms to the SMS operator providing identification of the system, nature of the alarm, and location of the alarm.

      - Controlling devices shall be utilized to interface the SMS with all field devices.

      - The Security control room and security console will be supported by an uninterrupted power supply (UPS) or dedicated backup generator power circuit.

      - The Security Equipment room, Security Control Room, and Security Operator Console shall house the following equipment i.e. refer to individual master specifications for each security subsystem’s specific requirements:

        - Security Network Server and Workstation

        - CCTV Monitoring, Controlling, and Recording Equipment

G. Wires and Cables:

- Shall meet or exceed the manufactures recommendation for power and signals.

- Shall be carried in an enclosed conduit system, utilizing electromagnetic tubing (EMT) to include the equivalent in flexible metal, rigid galvanized steel (RGS) to include the equivalent of liquid tight, polyvinylchloride (PVC) schedule 40 or 80.

- All conduits will be sized and installed per the NEC. All security system signal and power cables that traverse or originate in a high security office space will contained in either EMT or RGS conduit.

- All conduit, pull boxes, and junction boxes shall be marked with colored permanent tape or paint that will allow it to be distinguished from all other infrastructure conduit.

- Conduit fills shall not exceed 50 percent unless otherwise documented.

- A nylon pull string shall be pulled along and provided with signal and power cables to assist in future installations.

- At all locations where there is a wall penetration or core drilling is conducted to allow for conduit to be installed, fire stopping materials shall be applied to that area.

- High voltage and signal cables shall not share the same conduit and shall be kept separate up to the point of connection. High voltage for the security subsystems shall be any cable or sets of cables carrying 30 VDC/VAC or higher.

- For all equipment that is carrying digital data between the Security Control Room, Security Equipment Room, or at a remote monitoring station, it shall not be less than 20 AWG and stranded copper wire for each conductor. The cable or each individual conductor within the cable shall have a shield that provides 100% coverage. Cables with a single overall shield shall have a tinned copper shield drain wire.

  - TRANSIENT VOLTAGE SURGE SUPPRESSION DEVICES (TVSS) AND SURGE SUPPRESION

    - Transient Voltage Surge Suppression

      - All cables and conductors extending beyond building perimeter, except fiber optic cables, which serve as communication, control, or signal lines shall be protected against Transient Voltage surges and have Transient Voltage surge suppression protection (TVSS) UL listed in accordance with Standard 497B installed at each end. Lighting and surge suppression shall be a multi-strike variety and include a fault indicator. Protection shall be furnished at the equipment and

additional triple solid state surge protectors rated for the application on each wire line circuit shall be installed within 915 mm (36 in) of the building cable entrance. Fuses shall not be used for surge protection. The inputs and outputs shall be tested in both normal mode and common mode using the following waveforms:

        - A 10-microsecond rise time by 1000 microsecond pulse width waveform with a peak voltage of 1500 volts and a peak current of

60 amperes.

        - An 8-microsecond rise time by 20-microsecond pulse width waveform with a peak voltage of 1000 volts and a peak current of 500 amperes.

        - Maximum series current: 2 AMPS. Provide units manufactured by Advanced Protection Technologies, model # TE/FA 10B or TE/FA 20B or approved equivalent.

        - Operating Temperature and Humidity: -40 to + 85 deg C (-40 to 185 deg F), and 0 to 95 percent relative humidity, non- condensing.

E. Video Surveillance System

- Protectors shall be installed on coaxial cable systems on points of entry and exit from separate buildings. Suppressors shall be installed at each exterior camera location and include protection for 12 and/or 24 volt power, data signal and motor controls (for Pan, Tilt and Zoom systems). SPDs shall protect all modes herein mentioned and contain all modes in a single unit system. Protection for all systems mentioned above shall be incorporated at the head end equipment. Additionally a minimum 450VA battery backup shall be used to protect each monitor. Protectors shall meet the following criteria:

  - Head-End Power

    - UL 1778, cUL (Battery Back Up)

    - Minimum Surge Current Capacity: 65,000 Amps (8x20µsec)

    - Minimum of two (2) NEMA 5-15R Receptacles (one (1) AC power only, one (1) with UPS)

    - All modes protected (L-N, L-G, N-G)

    - EMI/RFI Filtering

    - Maximum Continuous Current: 12 Amps

  - Camera Power

    - Minimum Surge Current Capacity: 1,000 Amps (8X20µsec); 240 Amps for IP Video/PoE cameras

    - Screw Terminal Connection

    - All protection modes L-G (all Lines)

    - MCOV <40VAC

  - Video And Data

    - Surge Current Capacity 1,000 Amps per conductor

    - “BNC” Connection (Coax)

    - Protection modes: L-G (Data), Center Pin-G, Shield-G (Coax)

    - Band Pass 0-2GHz

    - Insertion Loss <0.3dB

F. Grounding and Surge Suppression

- The Security Contractor shall provide grounding and surge suppression to stabilize the voltage under normal operating conditions. This is to ensure the operation of over current devices, such as fuses, circuit breakers, and relays, underground- fault conditions.

- The Contractor shall engineer, provide, ad install proper grounding and surge suppression as required by local jurisdiction and prevailing codes and standards, referenced in this document.

- Principal grounding components and features shall include: main grounding buses, grounding, and bonding connections to service equipment.

- The Contractor shall provide detail drawings of interconnection with other grounding systems including lightning protection systems.

- The Contractor shall provide details of locations and sizes of grounding conductors and grounding buses in electrical, data, and communication equipment rooms and closets.

- AC power receptacles are not to be used as a ground reference point.

- Any cable that is shielded shall require a ground in accordance with applicable codes, the best practices of the trade, and all manufactures’ installation instructions.

G. 120 VAC Surge Suppression

- Continuous Current: Unlimited (parallel connection)

- Max Surge Current: 13,500 Amps

- Protection Modes: L - N, L - G, N - G

- Warranty: Ten Year Limited Warranty

- Dimension: 73.7 x 41.1 x 52.1 mm (2.90 x 1.62 x 2.05 in)

- Weight: 2.88 g (0.18 lbs)

- Housing: ABS

  - INSTALLATION KIT

    - General:

      - The kit shall be provided that, at a minimum, includes all connectors and terminals, labeling systems, audio spade lugs, barrier strips, punch blocks or wire wrap terminals, heat shrink tubing, cable ties, solder, hangers, clamps, bolts, conduit, cable duct, and/or cable tray, etc., required to accomplish a neat and secure installation. All wires shall terminate in a spade lug and barrier strip, wire wrap terminal or punch block. Unfinished or unlabeled wire connections shall not be allowed. All unused and partially opened installation kit boxes, and twisted pair cable reels, conduit, cable tray, and/or cable duct bundles, wire rolls, physical installation hardware shall be turned over to the Contracting Officer. The following sections outline the minimum required installation sub-kits to be used:

      - System Grounding:

        - The grounding kit shall include all cable and installation hardware required. All head end equipment and power supplies shall be connected to earth ground via internal building wiring, according to the NEC.

        - This includes, but is not limited to:

          - Control Cable Shields

          - Data Cable Shields

          - Equipment Racks

          - Equipment Cabinets

          - Conduits

          - Cable Duct blocks

          - Cable Trays

          - Power Panels

          - Grounding

          - Connector Panels

- Wire and Cable: The wire and cable kit shall include all connectors and terminals, audio spade lugs, barrier straps, punch blocks, wire

wrap strips, heat shrink tubing, tie wraps, solder, hangers, clamps, labels etc., required to accomplish a neat and orderly installation.

- Conduit, Cable Duct, and Cable Tray: The kit shall include all conduit, duct, trays, junction boxes, back boxes, cover plates, feed through nipples, hangers, clamps, other hardware required to accomplish a neat and secure conduit, cable duct, and/or cable tray installation in accordance with the NEC and this document.

- Equipment Interface: The equipment kit shall include any item or quantity of equipment, cable, mounting hardware and materials needed to interface the systems with the identified sub-system(s) according to the OEM requirements and this document.

- Labels: The labeling kit shall include any item or quantity of labels, tools, stencils, and materials needed to label each subsystem according to the OEM requirements, as-installed drawings, and this document.

- Documentation: The documentation kit shall include any item or quantity of items, computer discs, as installed drawings, equipment, maintenance, and operation manuals, and OEM materials needed to provide the system documentation as required by this document and explained herein.

PART 3 – EXECUTION

  - COMMON REQUIREMENTS FOR ELECTRONIC SAFETY AND SECURITY INSTALLATION

    - Comply with NECA 1.

    - Measure indicated mounting heights to bottom of unit for suspended items and to center of unit for wall-mounting items.

    - Headroom Maintenance: If mounting heights or other location criteria are not indicated, arrange and install components and equipment to provide maximum possible headroom consistent with these requirements.

    - Equipment: Install to facilitate service, maintenance, and repair or replacement of components of both electronic safety and security equipment and other nearby installations. Connect in such a way as to facilitate future disconnecting with minimum interference with other items in the vicinity.

    - Right of Way: Give to piping systems installed at a required slope.

    - Equipment location shall be as close as practical to locations shown on the drawings.

    - Inaccessible Equipment:

      - Where the Government determines that the Contractor has installed equipment not conveniently accessible for operation and maintenance, the equipment shall be removed and reinstalled as directed at no additional cost to the Government.

      - "Conveniently accessible" is defined as being capable of being reached without the use of ladders, or without climbing or crawling under or over obstacles such as, but not limited to, motors, pumps, belt guards, transformers, piping, ductwork, conduit and raceways.

  - FIRESTOPPING

    - Apply firestopping to penetrations of fire-rated floor and wall assemblies for electronic safety and security installations to restore original fire-resistance rating of assembly. Firestopping materials and installation requirements are specified in Division 07 Section 07

84 00 "Firestopping."

  - DEMONSTRATION AND TRAINING

    - Training shall be provided in accordance with Article, INSTRUCTIONS, of Section 01 00 00, GENERAL REQUIREMENTS.

    - Training shall be provided for the particular equipment or system as required in each associated specification.

    - A training schedule shall be developed and submitted by the contractor and approved by the Resident Engineer at least 30 days prior to the planned training.

    - Provide services of manufacturer’s technical representative for <insert hours> hours to instruct VA personnel in operation and maintenance of units.

    - Submit training plans and instructor qualifications in accordance with the requirements of Section 28 08 00 – COMMISIONING OF ELECTRONIC SAFETY AND SECURITY SYSTEMS.

  - WORK PERFORMANCE

    - Job site safety and worker safety is the responsibility of the contractor.

    - For work on existing stations, arrange, phase and perform work to assure electronic safety and security service for other buildings at all times. Refer to Article OPERATIONS AND STORAGE AREAS under Section 01 00 00, GENERAL REQUIREMENTS.

    - New work shall be installed and connected to existing work neatly and carefully. Disturbed or damaged work shall be replaced or repaired to

its prior conditions, as required by Section 01 00 00, GENERAL REQUIREMENTS.

    - Coordinate location of equipment and conduit with other trades to minimize interferences. See the GENERAL CONDITIONS.

  - SYSTEM PROGRAMMING

    - General Programming Requirements

      - This following section shall be used by the contractor to identify the anticipated level of effort (LOE) required setup, program, and configure the Electronic Security System (ESS). The contractor shall be responsible for providing all setup, configuration, and programming to include data entry for the Security Management System (SMS) and subsystems [(e.g., cloud software integration, including integration of subsystems to the SMS (e.g., camera call up, time synchronization, intercoms)]. System programming for existing or new SMS servers shall not be conducted at the project site.

    - Level of Effort for Programming

      - The Contractor shall perform and complete system programming (including all data entry) at an offsite location using the Contractor’s own copy of the SMS software. The Contractor’s copy of the SMS software shall be of the Owners current version. Once system programming has been completed, the Contractor shall deliver the data to the Resident Engineer on data entry forms and an approved electronic medium, utilizing data from the contract documents. The completed forms shall be delivered to the Resident Engineer for review and approval at least 90 calendar days prior to the scheduled date the Contractor requires it. The Contractor shall not upload system programming until the Resident Engineer has provided written approval. The Contractor is responsible for backing up the system prior to uploading new programming data. Additional programming requirements are provided as follows:

        - Programming for New SMS Server: The contractor shall provide all other system related programming. The contractor will be responsible for uploading personnel information (e.g., ID Cards backgrounds, names, access privileges, personnel photos, access schedules, personnel groupings) along with coordinating with Resident Engineer for device configurations, standards, and groupings. VA shall provide database to support Contractor’s

data entry tasks. The contractor shall anticipate a weekly coordination meeting and working with Resident Engineer to ensure data uploading is performed without incident of loss of function or data loss.

        - Programming for Existing SMS Servers: The contractor shall perform all related system programming except for personnel data as noted. The contractor will not be responsible for uploading personnel information (e.g., ID Cards backgrounds, names, access privileges, access schedules, personnel groupings). The contractor shall anticipate a weekly coordination meeting and working alongside of Resident Engineer to ensure data uploading is performed without incident of loss of function or data loss. System programming for SMS servers shall be performed by using the Contractor’s own server and software. These servers shall not be connected to existing devices or systems at any time.

      - The Contractor shall identify and request from the Resident Engineer, any additional data needed to provide a complete and operational system as described in the contract documents.

      - Contractor and Resident Engineer coordination on programming requires a high level of coordination to ensure programming is performed in accordance with VA requirements and programming uploads do not disrupt existing systems functionality. The contractor shall anticipate a minimum a weekly coordination meeting. Contractor shall ensure data uploading is performed without incident of loss of function or data loss. The following Level of Effort Chart is provided to communicate the expected level of effort required by contractors on VA ESS projects. Calculations to determine actual levels of effort shall be confirmed by the contractor before project award. Only those columns applicable to the campus video surveillance system upgrade shall be included and referenced.

|  | Description of Tasks |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Descr iptio n of Syste ms | Develop System Loading Sheets | Coordina tion | Initial Set-up Configur ation | Graphic Maps | Syst em Prog ramm ing | Final Checks | Level of Effort (Typical Tasks) |
|  |  | e.g., retrieve IP addresse s, naming conventi ons, standard event descript ions, programm ing template s, coordina te special system needs |  | e.g., develop naming convent ions, develop file folders , confirm ing accurac y of AutoCAD Floor Plans, convert file into jpeg file | e.g. | e.g., check all system diagno stics (e.g., client s, panels ) | Load and set- up 4-6 CDs and configure servers (to configure Loading and Configuring software Administrative account, audit log, Keystrokes, mouse clicks, multi-screen configuration |
|  |  |  |  |  | , |  |  |
|  |  |  |  |  | prog |  |  |
|  |  |  |  |  | ram |  |  |
|  |  |  |  |  | moni |  |  |
|  |  |  |  |  | tori |  |  |
|  |  |  |  |  | ng |  |  |
|  | e.g., |  |  |  | stat |  |  |
|  | program |  |  |  | ions |  |  |
|  | monitori |  | e.g., |  | , |  |  |
|  | ng |  | Load |  | prog |  |  |
|  | stations |  | system |  | ramm |  |  |
|  | , |  | Operatin |  | ing |  |  |
| SMS | programm |  | g System |  | netw |  |  |
| Setup | ing |  | and |  | orks |  |  |
| & | networks |  | Applicat |  | , |  |  |
| Confi | , |  | ion |  | inte |  |  |
| gurat | intercon |  | software |  | rcon |  |  |
| ion | nections |  | , |  | nect |  |  |
|  | between |  | general |  | ions |  |  |
|  | CCTV, |  | system |  | betw |  |  |
|  | intercom |  | configur |  | een |  |  |
|  | s, time |  | ations |  | CCTV |  |  |
|  | synchron |  |  |  | , |  |  |
|  | ization |  |  |  | inte |  |  |
|  |  |  |  |  | rcom |  |  |
|  |  |  |  |  | s, |  |  |
|  |  |  |  |  | time |  |  |
|  |  |  |  |  | sync |  |  |
|  |  |  |  |  | hron |  |  |
|  |  |  |  |  | izat |  |  |
|  |  |  |  |  | ion |  |  |

|  |  |  |  |  | e.g. |  | e.g., creating a door, door configuration, adding request to exit, door monitors and relays, door timers, door related events (e.g., access, access denied, forced open, held open), linkages, controlled areas, advanced door monitoring, time zones, sequence of operations |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | , |  |  |
|  |  | e.g., | e.g., |  | setu | e.g., |  |
|  |  | confirmi | enter |  | p of | perfor |  |
|  | e.g., | ng | data |  | devi | ming |  |
|  | setup of | device | from |  | ce, | entry |  |
|  | device, | configur | loading |  | door | testin |  |
| Elect ronic Entry Contr ol Syste ms | door groups & schedule s, REX, Locks, | ations, naming conventi ons, event | sheets; configur e componen ts, link |  | grou ps & sche dule s, | g to confir m correc t set- |  |
|  | link | descript | events, |  | REX, | up and |  |
|  | graphics | ion and | cameras, |  | Lock | config |  |
|  |  | narrativ | and |  | s, | uratio |  |
|  |  | es | graphics |  | link | n |  |
|  |  |  |  |  | grap |  |  |
|  |  |  |  |  | hics |  |  |

|  |  |  | e.g., |  |  | e.g., confir m area of covera ge, call- up per event genera ted and record ing rates |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | enter |  |  |  |  |
| CCTV Syste ms | e.g., programm ing call-ups recordin g | e.g., confirmi ng device configur ations, naming conventi ons | data from loading sheets; camera naming conventi on, sequence s, configur e |  | e.g. , prog ramm ing call -ups reco rdin g |  | e.g., setting up cameras points, recording ratios (e.g., normal, alarm event) timed recording, linkages, maps placements, call-ups |
|  |  |  | componen |  |  |  |  |
|  |  |  | ts) |  |  |  |  |
| Conso le Monit oring Compo nents | N/A | per monitor | per monitor | per graphic map | N/A | per monito r | N/A |
| Note: Programming tasks are supported through the contractor’s development of the Technical Data Package Submittals. |  |  |  |  |  |  |  |

Table 1 Contractor Level of Effort

  - TESTING AND ACCEPTANCE

    - Performance Requirements

      - General:

        - The Contractor shall perform contract field, performance verification, and endurance testing and make adjustments of the completed security system when permitted. The Contractor shall provide all personnel, equipment, instrumentation, and supplies necessary to perform all testing. Written notification of planned testing shall be given to the Resident Engineer at least

60 calendar days prior to the test and after the Contractor has received written approval of the specific test procedures.

        - The COTR shall witness all testing and system adjustments during testing. Written permission shall be obtained from the Resident Engineer before proceeding with the next phase of testing. Original copies of all data produced during performance verification and endurance testing shall be turned over to the Resident Engineer at the conclusion of each phase of testing and prior to Resident Engineer approval of the test.

      - Test Procedures and Reports: The test procedures, compliant w/ VA standard test procedures, shall explain in detail, step-by-step actions and expected results demonstrating compliance with the requirements of the specification. The test reports shall be used to document results of the tests. The reports shall be delivered to the Resident Engineer within seven (7) calendar days after completion of each test.

    - The inspection and test will be conducted by a factory-certified contractor representative and witnessed by a Government Representative. The results of the inspection will be officially recorded by a designated Government Representative and maintained on file by the Resident Engineer (RE), until completion of the entire project. The results will be compared to the Acceptance Test results.

    - Contractor’s Field Testing (CFT)

      - The Contractor shall calibrate and test all equipment, verify DTM operation, place the integrated system in service, and test the integrated system. Ground rods installed by this Contractor within the base of camera poles shall be tested as specified in IEEE STD

142. The Contractor shall test all security systems and equipment, and provide written proof of a 100% operational system before a date is established for the system acceptance test. Documentation package for CFT shall include completed (fully annotated details of test details) for each device and system tested, and annotated loading sheets documenting complete testing to Resident Engineer approval. CFT test documentation package shall conform to submittal requirements outlined in this Section. The Contractor’s field testing procedures shall be identical to the Resident Engineer’s acceptance testing procedures. The Contractor shall provide the Resident Engineer with a written listing of all equipment and software indicating all equipment and components have been tested

and passed. The Contractor shall deliver a written report to the Resident Engineer stating the installed complete system has been calibrated, tested, and is ready to begin performance verification testing; describing the results of the functional tests, diagnostics, and calibrations; and the report shall also include a copy of the approved acceptance test procedure. Performance verification testing shall not take place until written notice by contractor is received certifying that a contractors field test was successful.

    - Performance Verification Test (PVT)

      - Test team:

        - After the system has been pretested and the Contractor has submitted the pretest results and certification to the Resident Engineer, then the Contractor shall schedule an acceptance test to date and give the Resident Engineer written, notice as described herein, prior to the date the acceptance test is expected to begin. The system shall be tested in the presence of a Government Representative, an OEM certified representative, representative of the Contractor and other approved by the Resident Engineer. The system shall be tested utilizing the approved test equipment to certify proof of performance, FCC, UL and Emergency Service compliance. The test shall verify that the total system meets all the requirements of this specification. The notification of the acceptance test shall include the expected length (in time) of the test.

      - The Contractor shall demonstrate the completed Physical Access Control System PACS complies with the contract requirements. In addition, the Contractor shall provide written certification that the system is 100% operational prior to establishing a date for starting PVT. Using approved test procedures, all physical and functional requirements of the project shall be demonstrated and shown. The PVT will be stopped and aborted as soon as 10 technical deficiencies are found requiring correction. The Contractor shall be responsible for all travel and lodging expenses incurred for out- of-town personnel required to be present for resumption of the PVT. If the acceptance test is aborted, the re-test will commence from

the beginning with a retest of components previously tested and accepted.

      - The PVT, as specified, shall not begin until receipt of written certification that the Contractors Field Testing was successful. This shall include certification of successful completion of testing as specified in paragraph “Contractor’s Field Testing”, and upon successful completion of testing at any time when the system fails to perform as specified. Upon termination of testing by the Resident Engineer or Contractor, the Contractor shall commence an assessment period as described for Endurance Testing Phase II.

      - Upon successful completion of the acceptance test, the Contractor shall deliver test reports and other documentation, as specified, to the Resident Engineer prior to commencing the endurance test.

      - Additional Components of the PVT shall include:

        - System Inventory

          - All Device equipment

          - All Software

          - All Logon and Passwords

          - All Cabling System Matrices

          - All Cable Testing Documents

          - All System and Cabinet Keys

        - Inspection

          - Contractor shall record an inspection punch list noting all system deficiencies. The contractor shall prepare an inspection punch list format for Resident Engineers approval.

          - As a minimum the punch list shall include a listing of punch list items, punch list item location, description of item problem, date noted, date corrected, and details of how item was corrected.

      - Partial PVT - At the discretion of Resident engineer, the Performance Verification Test may be performed in part should a 100% compliant CFT be performed. In the event that a partial PVT will be performed instead of a complete PVT; the partial PVT shall be performed by testing 10% of the system. The contractor shall perform a test of each procedure on select devices or equipment.

    - Endurance Test

      - The Contractor shall demonstrate the specified probability of detection and false alarm rate requirements of the completed system. The endurance test shall be conducted in phases as specified below. The endurance test shall not be started until the Resident Engineer notifies the Contractor, in writing, that the performance verification test is satisfactorily completed, training as specified has been completed, and correction of all outstanding deficiencies has been satisfactorily completed. VA shall operate the system 24 hours per day, including weekends and holidays, during Phase I and Phase III endurance testing. VA will maintain a log of all system deficiencies. The Resident Engineer may terminate testing at any time the system fails to perform as specified. Upon termination of testing, the Contractor shall commence an assessment period as described for Phase II. During the last day of the test, the Contractor shall verify the appropriate operation of the system. Upon successful completion of the endurance test, the Contractor shall deliver test reports and other documentation as specified to the Resident Engineer prior to acceptance of the system.

      - Phase I (Testing): The test shall be conducted 24 hours per day for

15 consecutive calendar days, including holidays, and the system shall operate as specified. The Contractor shall make no repairs during this phase of testing unless authorized in writing by the Resident Engineer. If the system experiences no failures, the Contractor may proceed directly to Phase III testing after receiving written permission from the Resident Engineer.

      - Phase II (Assessment):

        - After the conclusion of Phase I, the Contractor shall identify all failures, determine causes of all failures, repair all failures, and deliver a written report to the Resident Engineer. The report shall explain in detail the nature of each failure, corrective action taken, results of tests performed, and recommend the point at which testing should be resumed.

        - After delivering the written report, the Contractor shall convene a test review meeting at the job site to present the results and recommendations to the Resident Engineer. The meeting shall not be scheduled earlier than five (5) business days after the Resident Engineer receives the report. As part of this test

review meeting, the Contractor shall demonstrate all failures have been corrected by performing appropriate portions of the performance verification test. Based on the Contractor’s report and the test review meeting, the Resident Engineer will provide a written determine of either the restart date or require Phase I be repeated.

      - Phase III (Testing): The test shall be conducted 24 hours per day for 15 consecutive calendar days, including holidays, and the system shall operate as specified. The Contractor shall make no repairs during this phase of testing unless authorized in writing by the COTR.

      - Phase IV (Assessment):

- After the conclusion of Phase III, the Contractor shall identify all failures, determine causes of all failures, repair all failures, and deliver a written report to the COTR. The report shall explain in detail the nature of each failure, corrective action taken, results of tests performed, and recommend the point at which testing should be resumed.

- After delivering the written report, the Contractor shall convene a test review meeting at the job site to present the results and recommendations to the COTR. The meeting shall not be scheduled earlier than five (5) business days after receipt of the report by the COTR. As a part of this test review meeting, the Contractor shall demonstrate that all failures have been corrected by repeating appropriate portions for the performance verification test. Based on the review meeting the test should not be scheduled earlier than five (5) business days after the Resident Engineer receives the report. As a part of this test review meeting, the Contractor shall demonstrate all failures have been corrected by repeating appropriate portions of the performance verification test. Based on the Contractor’s report and the test review meeting, the Resident Engineer will provide a written determine of either the restart date or require Phase III be repeated. After the conclusion of any re-testing which the Resident Engineer may require, the Phase IV assessment shall be repeated as if Phase III had just been completed.

    - Exclusions

      - The Contractor will not be held responsible for failures in system performance resulting from the following:

        - An outage of the main power in excess of the capability of any backup power source provided the automatic initiation of all backup sources was accomplished and that automatic shutdown and restart of the PACS performed as specified.

        - Failure of an Owner furnished equipment or communications link, provided the failure was not due to Contractor furnished equipment, installation, or software.

        - Failure of existing Owner owned equipment, provided the failure was not due to Contractor furnished equipment, installation, or software.

- - - E N D - - -

SECTION 28 05 01

STATEMENT OF WORK FOR ELECTRONIC SAFETY AND SECURITY CAMPUS VIDEO SURVEILLANCE SYSTEM REPLACEMENT

  - BACKGROUND

The Department of Veterans Affairs Office of the Senior Security Office/Physical Security and Infrastructure Office, along with the Hunter Holmes McGuire Richmond VA Medical Center’s Directors Office and VA Police Department requires a modernized security camera system with analytics in order to comply with the Presidential Mandates below, VA 0730 Handbook, Security and Law Enforcement, and the OIT VA Directive 6517, 6518, 6500 (6500.6 and 6500.11), 6008 along with the OIT Strategic Plan and VA EA Principles, in addition to:

    - Presidential Executive Order 14111, dated November 27, 2023, to enhance the quality and effectiveness of security in and protection of Federal facilities while modernizing those programs and technology with current industry standards

In addition to security measures, the VA has been charged by the U.S. Office of Management and Budget and the White House with the following:

    - Presidential Executive Order 14028 “Improving the Nation’s Cybersecurity” issued May 12, 2021, with advancing agencies towards Zero Trust architecture and accelerating movement to secure cloud services

    - Presidential Executive Order 12997/13286 which established the Interagency Security Committee to enhance the security and protection of federal facilities in the United States

    - Presidential Executive Order 13800 titled "Strengthening the Cybersecurity of Federal Networks and Critical Infrastructure," issued May 11, 2017, aims to improve the nation's cyber posture and capabilities by focusing on modernizing federal IT infrastructure and securing critical infrastructure

    - Guidance issued on February 26, 2025, to implement technological solutions that automate routine tasks while enabling staff to focus on higher-value activities and introduce plans to reduce costs and promote efficiencies through improved technology, including through the adoption of new software systems and the elimination of duplicative systems

The Richmond VA Police Departments face a reality where much of their CCTV physical security video surveillance systems have reached end of life.

Specifically, 171 cameras are currently inoperable. Due to EO 14111, EO14028 and OMB Guidance as well as the additional orders listed above, it is imperative to implement an overhaul of the CCTV surveillance system at Richmond. Due to these orders, the Hunter Holmes McGuire Richmond VA Medical Center] requires a modernized security system that will enhance security, provide an easy-to-use system, minimize on-premises infrastructure, and increase the VA’s cybersecurity posture while meeting National Defense Authorization and TAA manufacturing rules according to the 2023 FAR clauses

while complying with Federal Information Security Management Act (FISMA). The VA Police require that the system be able to integrate with the VA Police’s Body Worn Camera Solution as a Service product, integrate with the OSSO/PSI Physical Security Enterprise One View Process Solution and provide Software as a Service with that is fully FedRAMP Compliant.

The solution will need to be outfitted for the Hunter Holmes McGuire Richmond VA Medical Center’s located at 1201 Broad Rock Blvd, Richmond, VA 23249.

  - SCOPE

This contract will provide all equipment, services, and solutions as a service and defined in the contractor’s response to the contract as needed. The contractor shall provide, as per the contract, all materials needed to properly install and configure the physical security system, which will be delivered to the addresses specified in the contract, which is the Richmond VAMC. Materials required to support the installation shall include but not be limited to the following as based on the scope of work:

    - Phased demolition of existing interior and exterior cameras as noted on the documents

    - Reuse of existing cabling pathways (cable tray, conduit, j-hooks, junction boxes, camera mounts, etc.) as applicable to support the new camera installations

    - Cameras – fixed, multi-lens, pan/tilt/zoom, fisheye

    - Camera mounted as required to suit field conditions

    - Integral camera solid-state storage device sized per recording fps and duration (30 days minimum)

    - Surge protective devices

    - Unshielded Twisted Pair (UTP) and Shielded Twisted Pair (STP) cabling

    - PoE Extender hybrid cabling fiber optic and DC power cabling with associated head end power extenders and end device units

    - UTP/STP patch cords for installation at the cameras and for installation by VA OIT in the TR rooms

    - Exterior pathways consisting of direct buried and surface mounted conduit, handholes, junction boxes, enclosures, and infrastructure to support exterior site cameras where cameras do not presently exist

    - Interior conduit pathways where UTP cable is susceptible to physical damage such as in loading docks, warehouses and similar areas

    - Local UPS units to support two (2) client workstations as detailed below

    - Two (2) client workstations each consisting of two (2) 24” 4k compliant desk top monitors, one (1) 55 inch 4k compliant wall monitor, wall mounting bracket, tower PC workstation (to VA OIT standards), video control keyboard and mouse

    - Client software and camera licenses

    - Termination, labeling and testing of all UTP, STP and PoE Extender cabling provided under this scope of work

Installation shall be completed by the vendor as per the contract and the contract documents. The contracted company will have the SaaS solution either FedRAMP Approved or FedRAMP Ready on the FedRAMP Marketplace (FedRAMP Marketplace) and be willing to do the VA OIT’s FedRAMP Validation and ATO process as part of the contract.

- CONTRACTOR REQUIREMENTS

The Contractor will execute the installation and programming of the proposed Modernized Security System at the Richmond VAMC. The contracted company will have the SaaS solution either FedRAMP Approved or FedRAMP Ready on the FedRAMP Marketplace and be willing to do the VA OIT’s FedRAMP Validation and ATO process as part of the contract.

- PERIOD OF PERFORMANCE

Period of performance: The Installation process will be from the date of award of FedRAMP ATO Approval and VA ATO Approval base 12 months plus four

(4) optional 12 months of the SaaS product support and 5 years total for the Licenses for Government use. The FedRAMP ATO Approval and VA ATO Approval are FISMA Law and would be a conditional factor for the contract as per the SaaS language in the contract as part of the deliverables.

Work shall be performed during the hours of 8:00 a.m. through 4:30 p.m. from Monday through Friday. Excluding weekends and all federally observed holidays. No overtime is authorized.

FEDERAL HOLIDAYS

New Year’s Day	Labor Day Martin Luther King's Birthday	Columbus Day President’s Day	Veterans Day

Memorial Day	Thanksgiving

Juneteenth	Christmas

Independence Day

- TASKS

  - System Requirements

The solution must have the ability to enhance security and have motion intrusion and alerting capabilities in a cloud-managed platform. In addition, it must provide an easy-to-use system, minimize on-premises infrastructure, and increase the VA’s cybersecurity posture while meeting the National Defense Authorization and TAA manufacturing rules according to the 2023 FAR clauses while complying with the Federal Information Security Management Act (FISMA).

    - SaaS compliance with:

      - FISMA Law FedRAMP Ready or Approved

      - NDAA and TAA

      - SOC 2 Type II

      - UL / CUL 62368-1 certification for video, information, and communication technology equipment

The solution must provide a fully integrated architecture of easy-to-scale hardware and an easy-to-use video management SaaS solution provided by the same manufacturer viable on many devices while managing bandwidth efficiently at scale. The solution must utilize a SaaS solution that allows for advanced analytics, including the ability to quickly locate people or vehicles of interest across a site, thus quickly reducing incident response time and minimizing the time security personnel devote to the technological side of investigations.

All data must be able to be stored encrypted locally on each physical camera device on a solid-state drive to prevent any data breach, along with the ability to stream and archive data continuously and indefinitely to the cloud to prevent any loss of data. This solution must have the hardware and software offered as a single solution. A graphical interface must be provided by the same manufacturer and have role-based access control (RBAC) that is configurable by government personnel. Audit trails must be built into the software solution and provided natively, as well as notifications, alerts, and the ability to operate the products without adding or needing any servers.

The Contractor must provide the following capabilities and features in a Hybrid-cloud security platform with all products managed through a single pane of glass and:

- The Contractor must provide a solution that is either FedRAMP Authorized or FedRAMP Ready and must go through the VA's validation process to receive a VA ATO.

- The contractor must provide a SaaS solution operating in FedRAMP Government Cloud (AWS GovCloud, Microsoft Azure, or equivalent)

- Provides 24/7 US-Based 1-800 technical support team that can be reached by phone, email, or in-platform chat included at no additional cost

- SaaS browser-based solution with Single Sign On with PIV/CAC Multifactor Authentication that includes

  - FedRAMP Control process approved

  - Identity Provider Integrations via SAML & SCIM (ADFS, Azure AD, Okta)

  - Capability for a browser-based client that can be accessed across multiple platforms (to include Windows, Chrome OS, MacOS, iOS, and Android) without using proprietary plugins like Java,

Silverlight, or Flash

  - Audit logs

  - Role-based access control natively in the SaaS

  - Auto software updates, updates, and continuous penetration testing at no cost

  - System to have mobile client or mobile device accessibility to securely access and view footage both on and off site at any time and to conduct person/vehicle analytics via the mobile device as well.

  - Emergency Access, audited for usage, sharable content to authorized law enforcement that can view selected cameras

  - Ability to remotely manage users and cameras across multiple sites

  - Certain custodians may view cameras at multiple locations

- Data encryption in transit and at rest- FIPS 140-2 encryption standard

  - In Transit AES-128

  - At Rest AES-256

- Archive video footage with unlimited cloud storage stored indefinitely

- Software licensing for 5-year option

- Does not require an NVR or DVR

- The solution should be modular to allow additional devices at any time

- The solution should have the ability to add in cameras from multiple manufacturers if required

Camera Specifications

- Have built in solid-state hard drive(thumb drive) capable of recording for immediate use of 30 days of continuous recording

  - Has the ability for future use of up to 365 days of continuous video

- Are FIPS 140-2 validated, TAA and FY 2019 NDAA compliant

- Are plug-and-play IP, PoE-based cameras

- Receive firmware and software updates pushed automatically via the cloud at no additional cost as part of the camera or product licenses

- Have a minimum of resting bandwidths 20-50kbsand low bandwidth mode options

- Bandwidth Management Tuning Capabilities

- Must have a 10-year warranty on all fixed camera hardware

- Include all of the following Artificial Intelligence (AI) and analytics capabilities at no additional cost:

  - People/vehicle analytics

  - Occupancy Trends

  - Trajectory Tracking

  - Line Crossing

  - AI Search

  - Loitering

  - Live & Historical Face Blur

  - License Plate Recognition (Bullet cameras only)

  - Privacy Zones

  - Tamper Alerts

  - People, Vehicle, Motion, Loitering, Crowd Alerts

  - Status (Online/Offline) & Tamper Alerts

  - Vehicle Query by Color, Type, Make, Model, Identifiers

- Included 30-day Cloud Backup, with additional retention able to be purchased

- Must provide RTSP capabilities for up to 2 streams

- Operate in Temperature ranges of: -40°F to 122°F

- Have unlimited archive clip storage capabilities in the SaaS solution

- Ability to provide 5MP to 4k (8MP) image resolution (3840 x 2160)

- IP67 rating to protect against dust and environmental elements for outdoor cameras

- Accelerometers for tamper-proof capability

- IK8 vandal resistant rating or above

- Built-in Infrared illumination

- Capability to produce video at a minimum 24 FPS or more

- Image stabilizing to reduce blurring

- Day and Night viewing and recording capability

- Standard ethernet connectivity, including Power Over Ethernet (PoE)

- Motion detection

- Capability to perform computer vision analytics at the edge (on device)

- Ability to see remote locations and run analytics with offsite viewing

- Provide all the proper device mounting kits and proper installation

- Ability to share live links with authorities

- Granular permissions with Role Based Access Control (RBAC)

- Remote deployment capabilities via cellular gateway as required

  - SOW Requirements

The Contractor must provide in the Security capabilities as specified herein.

  - Richmond VAMC Installation Instructions

Main Location: 1201 Broad Rock Blvd, Richmond, VA 23249

- The customer installers will be fully accredited installers of the required cameras and system being installed.

- Required Richmond VAMC staff and Veterans Affairs (VA) Police will have access to the Cameras and the SaaS products for proper CCTV Physical Security surveillance practices and FedRAMP ATO process, SOP, and controls.

- Each camera will come with access to the SaaS back-end product for the VA Police and VA Staff to view said Physical Security surveillance needs and proper 5-year Camera Licenses for Government use.

- The Contractor must provide on-site training with both VA Police Services and OI&T for new system requirements as well as continued training during additional product enhancements, which happen quarterly.

- The Contractor shall provide a service and maintenance plan for a minimum of five (5) years from the date of completion and acceptance of the SaaS system be the Government.

Clarifications:

- All grounding and bonding required will be supplied by the customer.

- All network needs will be provided by the Government within the Telecommunications Rooms (TR).

- Installed wiring will utilize limited j-hooks as required. J-hooks are intended and will be installed for secondary infrastructure pathways ONLY. All pathways to include ladder rack, wire basket, wire trough, and conduit and backboxes, handholes, seals, fire stopping and similar required will be supplied by an electrical sub-contractor to this scope of work.

Note:

- The UPS PAC is expected to be provided for the system. The VA OIT will confirm and verify that power is available in each TR and at the security command center for the incorporation of any additional active networking components.

- The VA OIT backbone network is available and will be used for the new CCTV Physical Security Surveillance System.

- The VA OIT will have to provide the ports and switches for network connectivity.

- The VA OIT will confirm the available space within each TR for the installation of associated patch panels required for the termination of the UTP and PoE Extender cabling as well as horizontal wire managers to support the SaaS cameras.

- The VA will have to provide all the approvals and network security to allow the CCTV Physical Security Surveillance System to communicate with the SaaS solution.

- The VA will provide all the VLANS, IT Whitelist access for hardware to access the VA network securely, and provide an SDL and an Implementation team to track and help the Vendor complete the installation tasks and Program/Project Management.

Warranty:

Provide the necessary labor and assistance for warranty claims against manufacturers due to equipment failure during the manufacturer’s stated warranty period.

The Contractor shall provide a service and maintenance plan for a minimum of five (5) years from the date of completion and acceptance of the SaaS system be the Government.

Clarifications:

Installed wiring will utilize plenum-rated cable as required and specified herein with the exception of exterior cabling may be riser rated, and conduit should be included in the quoted price as noted on the drawings and within the specifications.

- SECURITY

The Contractor is required to check in with the COR before proceeding to the installation location. The contractor will install equipment but will not have access to VA systems.

The C&A requirements do not apply, and a Security Accreditation Package is not required.

- SaaS Contract Language and Price Schedule

Attachment A: SaaS FedRAMP Requirements If the solution is not FedRAMP authorized:

- The information system solution selected by the Contractor shall comply

with the Federal Information Security Management Act (FISMA).

- The Contractor shall comply with FedRAMP requirements for Moderate Impact as mandated by Federal laws and policies, including making available any documentation, physical access, and logical access needed to support this requirement.

- The Contractor shall provide a SaaS product as defined by the following criteria: Software as a Service (SaaS) is an application delivery model in which the application is hosted on a cloud infrastructure outside the security boundary of VA and is provided to the Cloud Service Customer (CSC) over the internet. The CSC uses the SaaS offering via a thin-client interface, such as a web-browser or a program interface. The CSC subscribes to the SaaS offering and is only responsible for minor in-app customizations. The Cloud Service Provider (CSP) offering the application is responsible for the management of the application, safeguarding of data stored or processed by the application, and all elements of the underlying infrastructure. Additionally, the CSP is responsible for all ongoing compliance.

In order to qualify as SaaS for use at VA, and to align with Federal Risk and Authorization Management Program (FedRAMP) requirements, the hosting for the offering must conform to the NIST 800-145 definition of Cloud Computing and thus contain the following key characteristics:

  - On-Demand Self-Service: The CSP fully automates the provisioning of both the customer interface and the underlying cloud components of the SaaS offering. In some cases, the CSP may provision internal resources manually while providing the CSC an automated interface to request and track the service.

  - Broad Network Access: The SaaS capabilities are available over the internet or over a network that is available from all access points the CSC requires. The SaaS offering is accessible through common platforms (e.g., mobile phones, tablets, laptops, and workstations).

  - Resource Pooling: The computing infrastructure supporting the SaaS offering is shared among more than one CSC using a multi-tenant model, and resources are dynamically assigned depending on customer demand.

  - Rapid Elasticity: Computing capabilities are automatically provisioned and released in a manner that scales with customer demand. In some cases, the scaling of resources may not be fully automated, but it should be fast enough to support the needs of the CSC, which the CSC would have to define.

  - Measured Service: Resource usage, such as storage, processing, bandwidth, and user activity, are measured and reported on in a manner that is relevant to the SaaS offering.

The SaaS offering must comply with FedRAMP requirements surrounding data location within the Continental United States. FedRAMP specifies data location requirements in the Moderate baseline as part of control SA-9

(5); however, FedRAMP does not provide or specify data location requirements for other baselines. CSPs should be aware of FedRAMP and be ready to partner with VA through the SaaS FedRAMP Authorization Process.

- Following guidance from the Federal CIO, VA will utilize existing JAB ATO or agency ATO issued by another agency as a starting point for FedRAMP requirements. If neither of those exists, VA will sponsor The Cloud Service Provider for a FedRAMP Authorization. VA will be using the FedRAMP baselines as a starting point since they are specifically tailored for cloud services.

- The Contractor shall, where applicable, assist with the VA ATO Process to help achieve agency authorization of the cloud service or migrated application at the impact level required by VA to utilize the product. For this solution, the required impact level is Moderate Impact.

- The Contractor shall complete a FedRAMP System Security Plan (SSP) and supporting documentation, including required attachments, within 75 calendar days after contract award. (If Data Security Categorization is Moderate Impact, this will be due 94 calendar days after contract award.)

- The Contractor shall work with a VA Subject Matter Expert to develop a specific system boundary diagram, including any integration and connectivity components for VA use. This will be known as the VA Implementation Diagram (VAID) and will demonstrate the proposed implementation of this system at VA. The Contractor shall complete this deliverable with VA within 10 calendar days of contract award.

- The Contractor shall complete a Third-Party Assessment Organization (3PAO) Security Assessment Plan (SAP) within 90 calendar days after contract award. (If Data Security Categorization is Moderate Impact, this will be due after 113 calendar days after contract award.)

- The Contractor shall complete a 3PAO Security Assessment Report (SAR) within

90 calendar days after the SSP is accepted by VA. (If Data Security Categorization is Moderate Impact, this will be due 113 calendar days after the SSP is accepted by VA.)

- The Contractor shall work with VA Subject Matter Experts to test the validity of the IRP and ensure proper troubleshooting of issues that may arise. This should be completed within 30 calendar days of the SSP being delivered.

- The Contractor shall afford VA access to the Contractor’s and Cloud Service Provider’s (CSP) facilities, installations, technical capabilities, operations, documentation, records, and databases.

- If new or unanticipated vulnerabilities are discovered by either VA or the Contractor, or if existing safeguards have ceased to function, the discoverer shall immediately bring the situation to the attention of the other party in accordance with Addendum B, VA Information, and Information System Security/Privacy Language.

- The Contractor shall comply with data management requirements.

- Successful issuance of a VA ATO will be required before live VA data can be used in the system.

- The Contractor shall participate in FedRAMP Continuous Monitoring activities as outlined by FedRAMP’s Continuous Monitoring Strategy.

- The Contractor shall participate in monthly Agency and FedRAMP Sustainment meetings following the granting of a VA ATO.

- The Contractor shall provide continuous monitoring activities including but not limited to scans, security artifacts, and monthly Plan of Action and Milestones (POAM) reports as outlined by VA and FedRAMP requirements.

Deliverables:

- FedRAMP System Security Plan (SSP) and supporting documentation

- VA Implementation Diagram: This is a VA-specific architecture diagram demonstrating the proposed implementation of this system at VA (VAID)

- 3PAO Security Assessment Plan (SAP)

- 3PAO Security Assessment Report (SAR)

- IRP Test

- Continuous monitoring scans are to be reviewed at monthly meetings.

- Plan of Action and Milestones monthly reports.

- Additional deliverables as outlined by FedRAMP’s continuous monitoring strategy.

- VA Privacy and Security deliverables as directed by the VA System Owner.

If the solution is FedRAMP Authorized but not VA Authorized:

  - The information system solution selected by the Contractor shall comply with the Federal Information Security Management Act (FISMA)

  - The Contractor shall comply with FedRAMP requirements as mandated by Federal laws and policies, including making available any documentation, physical access, and logical access needed to support this requirement

  - The system must be FedRAMP Authorized at no less than the Moderate Impact.

  - The Contractor shall, where applicable, assist with the VA ATO Process to help achieve agency authorization of the cloud service or migrated application.

  - The Contractor shall work with a VA Subject Matter Expert to develop a specific system boundary diagram, including any integration and connectivity components for VA use. This will be known as the VA

Implementation Diagram (VAID) and will demonstrate the proposed implementation of this system at VA. The Contractor shall complete this deliverable with VA within 10 calendar days of contract award.

  - The Contractor shall provide confirmation of their FedRAMP System Security Plan (SSP) and supporting documentation completion via their repository ID number and a link for VA to download the SSP and all required artifacts within 5 calendar days of contract award.

  - The Contractor shall provide the results of their most recent Third- Party Assessment Organization (3PAO) Security Assessment Plan (SAP) within 10 calendar days of contract award.

  - The Contractor shall complete a 3PAO Security Assessment Report (SAR) within 10 calendar days after the SSP is accepted by VA.

  - The Contractor shall provide VA with the most recent monthly scans for the production environment within the authorization boundary and their scan upload schedule for FedRAMP within 30 calendar days of contract award.

  - The Contractor shall provide their availability to participate in monthly continuous monitoring meetings to be scheduled following a successful VA ATO within 30 calendar days of contract award.

  - The Contractor shall work with VA Subject Matter Experts to test the validity of the IRP and ensure proper troubleshooting of issues that may arise. This should be completed within 30 calendar days of the SSP being delivered.

  - If new or unanticipated vulnerabilities are discovered by either VA or the Contractor, or if existing safeguards have ceased to function, the discoverer shall immediately bring the situation to the attention of the other party in accordance with Addendum B, VA Information and Information System Security/Privacy Language

  - The Contractor shall comply with data management requirements. 14.Successful issuance of a VA ATO will be required before live VA data

can be used in the system.

- The Contractor shall participate in FedRAMP Continuous Monitoring activities as outlined by FedRAMP’s Continuous Monitoring Strategy.

- The Contractor shall participate in monthly Agency and FedRAMP Sustainment meetings following the granting of a VA ATO.

- The Contractor shall provide continuous monitoring activities including, but not limited to scans, security artifacts, and monthly Plan of Action and Milestones (POAM) reports as outlined by VA and FedRAMP requirements.

Deliverables:

  - FedRAMP System Security Plan (SSP) and supporting documentation

  - VA Implementation Diagram: This is a VA specific architecture diagram demonstrating the proposed implementation of this system at VA (VAID)

  - 3PAO Security Assessment Plan (SAP)

  - 3PAO Security Assessment Report (SAR)

  - IRP Test

  - Continuous monitoring scans to be reviewed at monthly meetings.

  - Plan of Action and Milestones monthly reports.

  - Additional deliverables as outlined by FedRAMP’s continuous monitoring strategy.

  - VA Privacy and Security deliverables as directed by the VA System Owner.

If the solution is FedRAMP Authorized and VA Authorized:

- The information system solution selected by the Contractor shall comply with the Federal Information Security Management Act (FISMA) and have a current VA authorization.

- The Contractor shall comply with FedRAMP requirements as mandated by Federal laws and policies, including making available any documentation, physical access, and logical access needed to support this requirement.

- The FedRAMP Authorization level and existing VA ATO should be no less than the level required for this use case which has been defined as Moderate Impact.

- The Contractor shall, where applicable, assist with the VA ATO Sustainment Process to help maintain health and quality of agency authorization of the cloud service or migrated application.

- The Contractor shall exclusively provide licenses and/or accounts to FedRAMP authorized and VA authorized environments.

- The Contractor shall afford VA access to the Contractor’s and Cloud Service Provider’s (CSP) facilities, installations, technical capabilities, operations, documentation, records, and databases.

- If new or unanticipated vulnerabilities are discovered by either VA or the Contractor, or if existing safeguards have ceased to function, the discoverer shall immediately bring the situation to the attention of the other party in accordance with Addendum B, VA Information and Information System Security/Privacy Language

- The Contractor shall comply with data management requirements.

- Successful issuance of a VA ATO will be required before live VA data can be used in the system.

- The Contractor shall participate in FedRAMP Continuous Monitoring activities as outlined by FedRAMP’s Continuous Monitoring Strategy.

- The Contractor shall participate in monthly Agency and FedRAMP Sustainment meetings following the granting of a VA ATO.

- The Contractor shall provide continuous monitoring activities including, but not limited to scans, security artifacts, and monthly Plan of Action and Milestones (POAM) reports as outlined by VA and FedRAMP requirements.

Deliverables:

  - SAR – delivered no later than 12 months from the previous SAR.

  - Continuous monitoring scans to be reviewed at monthly meetings.

  - Plan of Action and Milestones monthly reports.

  - Additional deliverables as outlined by FedRAMP’s continuous monitoring strategy.

  - VA Privacy and Security deliverables as directed by the VA System Owner.

Vendors are instructed to complete Section B.4: Price Schedule and submit with their quote. Vendors are cautioned that alterations to the line items as specified below may render quotes unacceptable. All questions shall be directed to the Contract Specialist and Contracting Officer prior to the closing date and time specified in the Request for Quote (RFQ).

Any resulting contract will be awarded on a firm-fixed-price basis as defined by Federal Acquisition Regulation Subpart 16.202. Accordingly, the Contractor shall ensure that any and all costs associated with the Contractor’s proposed application(s), software products, software solution, and/or system, shall be

included in the Contractor’s proposed firm-fixed price, and shall serve as the Contractor’s firm-fixed price for the life of any resulting contract. No additional costs or fees relative to the Contractor’s proposed application(s), software products, software solution, and/or system including, but not limited to, licensing costs and any associated licensing maintenance required for the development, delivery, integration, operation, and/or maintenance of the Contractor’s proposed solution will be allowed, accepted, and/or paid by the Government.

The Contractor shall provide unit costs for the following items:

- Camera UTP cable drop consisting of 150 feet of plenum rated cable installed within J-hooks, outlet jack, terminated, labeled and tested

- Each camera type

- Exterior underground conduit installation consisting of 150 feet of 1 inch Schedule 40 PVC, nylon pull cord, and RGS 90-degree elbows with nylon bushing at each end

All deliverables will be destination inspection, acceptance, and F.O.B.

Days used below refer to calendar days unless otherwise stated. Deliverables with due dates falling on a weekend or holiday shall be submitted the following Government workday after the weekend or holiday.

Electronic submission to: VA Project Manager, Contracting Officer, and Contracting Officer’s Representative

| Base Period – FedRAMP Authorization and VA Authorization The period of performance for this effort shall be up to 12 months in accordance with (IAW) Section 4.1 of the Product Description. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| CLIN | Description | Qty | Un it | Unit Price | Extended Price |
|  | FedRAMP approval for Verkada and Moderate categorization – Solution is Not FedRAMP Authorized or VA FedRAMP Authorized |  |  |  |  |
| 0001 | *If a vendor’s solution is not FedRAMP Authorized or VA FedRAMP Authorized the vendor shall complete CLIN 0001 and SLINS 0001AA-0001AD. | 1 | LO | Not Separatel y Priced (NSP) | NSP |
|  | CLINs 0002 and 0003 (and associated SLINs) shall be $0.00. |  |  |  |  |

|  | FedRAMP System Security Plan (SSP) and supporting documentation. |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 0001A A | Due 75 calendar days after contract award. (If Data Security Categorization is Moderate Impact, this will be due 94 calendar days after contract award.) | 1 | LO | NSP | NSP |
|  | *10% of the FedRAMP Approved Solution value. VA does not pay for FedRAMP Authorization fees and/or vendor acquired costs. |  |  |  |  |
|  | VA Implementation Diagram: |  |  |  |  |
| 0001A B | VA specific architecture diagram demonstrating proposed implementation of the system at VA. | 1 | LO | NSP | NSP |
|  | Due 10 calendar days after contract award. |  |  |  |  |
|  | Third Party Assessment Organization (3PAO) Security Assessment Plan (SAP) |  |  |  |  |
| 0001A C | Due 90 calendar days after the SSP is accepted by VA. (If Data Security Categorization is Moderate Impact, this will be due 113 calendar days after the SSP is accepted by VA.) | 1 | LO | NSP | NSP |
|  | *10% of the FedRAMP Approved Solution value. VA does not pay for FedRAMP Authorization fees |  |  |  |  |

|  | and/or vendor acquired costs. |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 0001A D | 3PAO Security Assessment Report (SAR) Due 90 calendar days after contract award. (If Data Security Categorization is Moderate Impact, this will be due 113 calendar days after contract award.) *10% of the FedRAMP Moderate Approved Solution value. VA does not pay for FedRAMP Authorization fees and/or vendor-acquired costs. | 1 | LO | NSP | NSP |
| 0002 | FedRAMP approval for the Verkada and Moderate categorization – Solution is FedRAMP Authorized but NOT VA FedRAMP Authorized * If a vendor’s solution is FedRAMP Authorized but not VA FedRAMP Authorized, the vendor shall complete CLIN 0002 and SLINS 0002AA-0002AD. CLINs 0001 and 0003 (and associated SLINs) shall be $0.00. | 1 | LO | NSP | NSP |
| 0002A A | IRP Table Top scenario Contractor shall work with assigned VA SME to develop a VA specific Incident Response Plan (IRP) and perform an IRP Table Top Exercise with VA Stakeholders. This should be completed within 30 calendar days of the SAR being delivered. | 1 | LO | NSP | NSP |

| 0002A B | VA Implementation Diagram The Contractor shall develop a VA specific system boundary diagram including any integration and connectivity components that will be known as a VA Implementation Diagram (VAID) demonstrating the proposed implementation of this system at VA. The Contractor shall provide the VAID within 10 calendar days of contract award. | 1 |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 0002A C | FedRAMP SSP and supporting documentation. The Contractor shall provide confirmation of their FedRAMP System Security Plan (SSP) and supporting documentation completion via their repository ID number and a link for VA to download the SSP and all required artifacts within 5 calendar days of contract award. | 1 | LO |  |  |
| 0002A C | 3PAO SAP The Contractor shall provide the results of their most recent Third-Party Assessment Organization (3PAO) Security Assessment Plan (SAP) within 10 calendar days of contract award. | 1 | LO |  |  |
| 0002A D | 3PAO SAR | 1 | LO |  |  |

|  | The Contractor shall complete a 3PAO Security Assessment Report (SAR) within 10 calendar days after the SSP is accepted by VA. |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 0003 | FedRAMP approval for Verkada and Moderate categorization - If Solution is FedRAMP Authorized and VA FedRAMP Authorized * In the event that the proposed product is already FedRamp Authorized and VA FedRamp Authorized and proposed pricing is not required, please list $0.00 for CLIN 0001, 0002 and 0003 (and associated SLINs). | 1 | LO | NSP | NSP |
| 0003A A | Dates for Current ATO expiration. Due at time of award. | 1 | LO | NSP | NSP |
| 0003A B | Most recent monthly Plan of Action Milestones finding reports. Due at time of award. | 1 | LO | NSP | NSP |
| Total Base Period |  |  |  |  | $ |
| Base Period Optional Task In accordance with FAR 52.217-7, “Option for Increased Quantity-Separately Priced Line Item,” this Optional Task may be exercised one time during the base period of performance once the solution is FedRAMP Authorized and VA FedRAMP Authorized. If exercised, the Period of Performance shall be up to 12 months. Work shall not commence until, and unless, a formal modification is issued by the Contracting Officer. |  |  |  |  |  |
| CLIN | Description | Qty | Un it | Unit Price | Extended Price |
| 0004 | FedRAMP Moderate Approved Solution in accordance with (IAW) Product Description (PD) Section 1.1. | up to 12 | MO | NSP | NSP |

|  | *70% of FedRAMP Moderate Approved Solution *100% if Solution is already FedRAMP Authorized and VA FedRAMP Authorized. |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

SECTION 28 05 13

CONDUCTORS AND CABLES FOR ELECTRONIC SAFETY AND SECURITY

PART 1 - GENERAL

  - DESCRIPTION

    - This section specifies the finishing, installation, connection, testing and certification the conductors and cables required for a fully functional for electronic safety and security (ESS) system.

  - RELATED WORK

    - Section 01 00 00 - GENERAL REQUIREMENTS. For General Requirements.

    - Section 07 84 00 - FIRESTOPPING. Requirements for firestopping application and use.

    - Section 27 10 00 – STRUCTURED CABLING. Requirements for horizontal work area outlet (WAO) cabling.

    - Section 28 05 00 – COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for general requirements that are common to more than one section in Division 28.

    - Section 28 05 26 - GROUNDING AND BONDING FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for personnel safety and to provide a low impedance path for possible ground fault currents.

    - Section 28 05 28.33 - CONDUITS AND BOXES FOR ELECTRONIC SECURITY AND

SAFETY. Requirements for infrastructure.

  - DEFINITIONS

    - BICSI: Building Industry Consulting Service International.

    - EMI: Electromagnetic interference.

    - IDC: Insulation displacement connector.

    - Ladder Cable Tray: A fabricated structure consisting of two longitudinal side rails connected by individual transverse members (rungs).

    - Low Voltage: As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control and signaling power- limited circuits.

    - Open Cabling: Passing telecommunications cabling through open space (e.g., between the studs of a wall cavity).

    - RCDD: Registered Communications Distribution Designer.

    - Solid-Bottom or Nonventilated Cable Tray: A fabricated structure consisting of integral or separate longitudinal side rails, and a bottom without ventilation openings.

    - Trough or Ventilated Cable Tray: A fabricated structure consisting of integral or separate longitudinal rails and a bottom having openings sufficient for the passage of air and using 75 percent or less of the plan area of the surface to support cables.

    - UTP: Unshielded twisted pair.

  - QUALITY ASSURANCE

    - See section 28 05 00, Paragraph 1.4.

  - SUBMITTALS

    - In accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES, furnish the following:

- Manufacturer's Literature and Data: Showing each cable type and rating.

- Certificates: Two weeks prior to final inspection, deliver to the Resident Engineer/COTR four copies of the certification that the material is in accordance with the drawings and specifications and diagrams for cable management system.

- Shop Drawings: Cable tray layout, showing cable tray route to scale, with relationship between the tray and adjacent structural, electrical, and mechanical elements. Include the following:

  - Vertical and horizontal offsets and transitions.

  - Clearances for access above and to side of cable trays.

  - Vertical elevation of cable trays above the floor or bottom of ceiling structure.

  - Load calculations to show dead and live loads as not exceeding manufacturer's rating for tray and its support elements.

  - System labeling schedules, including electronic copy of labeling schedules that are part of the cable and asset identification system of the software specified in Parts 2 and 3.

- Wiring Diagrams. Show typical wiring schematics including the following:

  - Workstation outlets, jacks, and jack assemblies.

  - Patch cords.

  - Patch panels.

- Cable Administration Drawings: As specified in Part 3 "Identification" Article.

- Project planning documents as specified in Part 3.

- Maintenance Data: For wire and cable to include in maintenance manuals.

  - APPLICABLE PUBLICATIONS

    - Publications listed below (including amendments, addenda, revisions, supplements and errata) form a part of this specification to the extent referenced. Publications are reference in the text by the basic designation only.

    - American Society of Testing Material (ASTM):

D2301-04................Standard Specification for Vinyl Chloride

Plastic Pressure Sensitive Electrical Insulating Tape

    - Federal Specifications (Fed. Spec.):

A-A-59544-08............Cable and Wire, Electrical (Power, Fixed

Installation)

    - National Fire Protection Association (NFPA):

70-11...................National Electrical Code (NEC)

    - Underwriters Laboratories, Inc. (UL):

44-05...................Thermoset-Insulated Wires and Cables

83-08...................Thermoplastic-Insulated Wires and Cables

467-07..................Electrical Grounding and Bonding Equipment

486A-03.................Wire Connectors and Soldering Lugs for Use with

Copper Conductors

486C-04.................Splicing Wire Connectors

486D-05.................Insulated Wire Connector Systems for

Underground Use or in Damp or Wet Locations 486E-00.................Equipment Wiring Terminals for Use with

Aluminum and/or Copper Conductors

493-07..................Thermoplastic-Insulated Underground Feeder and

Branch Circuit Cable

514B-04.................Fittings for Cable and Conduit

1479-03.................Fire Tests of Through-Penetration Fire Stops//

  - DELIVERY, STORAGE, AND HANDLING

    - Test cables upon receipt at Project site.

      - Test each pair of UTP cable for open and short circuits.

  - PROJECT CONDITIONS

    - Environmental Limitations: Do not deliver or install UTP, optical fiber, and coaxial cables and connecting materials until wet work in

spaces is complete and dry, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

PART 2 - PRODUCTS

  - GENERAL

    - Support of Open Cabling: NRTL labeled for support of [Category 6A] cabling, designed to prevent degradation of cable performance and pinch points that could damage cable.

      - Support brackets with cable tie slots for fastening cable ties to brackets.

      - Lacing bars and spools.

      - Straps and other devices.

    - Cable Trays:

      - Cable Tray Materials: Metal, suitable for indoors, and protected against corrosion by hot-dip galvanizing, complying with ASTM A 123/A 123M Grade 0.55, not less than 0.002165 inch (0.055 mm) thick.

      - Basket Cable Trays: 6 inches (150 mm) wide and 2 inches (50 mm) deep. Wire mesh spacing shall not exceed 2 by 4 inches (50 by 100 mm).

    - Conduit and Boxes: Comply with requirements in Division 28 Section "Conduits and Backboxes for Electrical Systems." Flexible metal conduit shall not be used.

      - Outlet boxes shall be no smaller than 2 inches (50 mm) wide, 3 inches (75 mm) high, and 2-1/2 inches (64 mm) deep.

  - LOW-VOLTAGE CONTROL CABLE

    - Paired Lock Cable: NFPA 70, Type CMG.

      - 1 pair, twisted, No. 16 AWG, stranded (19x29) tinned copper conductors.

      - PVC insulation.

      - Unshielded.

      - PVC jacket.

      - Flame Resistance: Comply with UL 1581.

    - Plenum-Rated, Paired Lock Cable: NFPA 70, Type CMP.

      - 1 pair, twisted, No. 16 AWG, stranded (19x29) tinned copper conductors.

      - PVC insulation.

      - Unshielded.

      - PVC jacket.

      - Flame Resistance: Comply with NFPA 262.

    - Paired Lock Cable: NFPA 70, Type CMG.

      - 1 pair, twisted, No. 18 AWG, stranded (19x30) tinned copper conductors.

      - PVC insulation.

      - Unshielded.

      - PVC jacket.

      - Flame Resistance: Comply with UL 1581.

    - Plenum-Rated, Paired Lock Cable: NFPA 70, Type CMP.

      - 1 pair, twisted, No. 18 AWG, stranded (19x30) tinned copper conductors.

      - Fluorinated ethylene propylene insulation.

      - Unshielded.

      - Plastic jacket.

      - Flame Resistance: NFPA 262, Flame Test.

  - CONTROL-CIRCUIT CONDUCTORS

    - Class 1 Control Circuits: Stranded copper, Type THHN-THWN, in raceway complying with UL 83.

    - Class 2 Control Circuits: Stranded copper, Type THHN-THWN, in raceway,

|  | C. | power-limited cable, concealed in building finishes , and/or power- limited tray cable, in cable tray complying with UL 83. Class 3 Remote-Control and Signal Circuits: Stranded copper, Type TW or TF, complying with UL 83. |
| --- | --- | --- |
| 2.4 |  | IDENTIFICATION PRODUCTS |
|  | A. | Comply with UL 969 for a system of labeling materials, including label |
| 2.5 |  | stocks, laminating adhesives, and inks used by label printers. SOURCE QUALITY CONTROL |

- Testing Agency: Engage a qualified testing agency to evaluate cables.

- Factory test UTP cables on reels according to TIA/EIA-568-B.1.

- Factory test UTP cables according to TIA/EIA-568-B.2.

- Cable will be considered defective if it does not pass tests and inspections.

- Prepare test and inspection reports.

  - WIRE LUBRICATING COMPOUND

    - Suitable for the wire insulation and conduit it is used with, and shall not harden or become adhesive.

  - FIREPROOFING TAPE

    - The tape shall consist of a flexible, conformable fabric of organic composition coated one side with flame-retardant elastomer.

    - The tape shall be self-extinguishing and shall not support combustion. It shall be arc-proof and fireproof.

    - The tape shall not deteriorate when subjected to water, gases, salt water, sewage, or fungus and be resistant to sunlight and ultraviolet light.

    - The finished application shall withstand a 200-ampere arc for not less than 30 seconds.

    - Securing tape: Glass cloth electrical tape not less than 0.18 mm (7 mils) thick, and 19 mm (3/4 inch) wide.

PART 3 - EXECUTION

  - INSTALLATION OF CONDUCTORS AND CABLES

    - Comply with NECA 1.

    - General Requirements for Cabling:

      - Comply with TIA/EIA-568-B.1.

      - Comply with BICSI ITSIM, Ch. 6, "Cable Termination Practices."

      - Terminate all conductors; no cable shall contain un-terminated elements. Make terminations only at indicated outlets, terminals, and cross-connect and patch panels.

      - Cables may not be spliced. Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

      - Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIM, "Cabling Termination Practices" Chapter. Install lacing bars and distribution spools.

      - Do not install bruised, kinked, scored, deformed, or abraded cable. Do not splice cable between termination, tap, or junction points.

Remove and discard cable if damaged during installation and replace it with new cable.

      - Cold-Weather Installation: Bring cable to room temperature before dereeling. Heat lamps shall not be used for heating.

      - Pulling Cable:

        - Comply with BICSI ITSIM, Ch. 4, "Pulling Cable." Monitor cable pull tensions.

        - Provide installation equipment that will prevent the cutting or abrasion of insulation during pulling of cables.

        - Use ropes made of nonmetallic material for pulling feeders.

        - Attach pulling lines for feeders by means of either woven basket grips or pulling eyes attached directly to the conductors, as approved by the Resident Engineer/COTR.

        - Pull in multiple cables together in a single conduit.

    - Splice cables and wires where necessary only in outlet boxes, junction boxes, or pull boxes.

      - Splices and terminations shall be mechanically and electrically secure.

      - Where the Government determines that unsatisfactory splices or terminations have been installed, remove the devices and install approved devices at no additional cost to the Government.

    - Seal cable and wire entering a building from underground, between the wire and conduit where the cable exits the conduit, with a non- hardening approved compound.

    - Unless otherwise specified in other sections install wiring and connect to equipment/devices to perform the required functions as shown and specified.

    - Except where otherwise required, install a separate power supply circuit for each system so that malfunctions in any system will not affect other systems.

    - System voltages shall be 120 volts or lower where shown on the drawings or as required by the NEC.

    - UTP Cable Installation:

      - Comply with TIA/EIA-568-B.2.

      - Do not untwist UTP cables more than 1/2 inch (12 mm) from the point of termination to maintain cable geometry.

    - Open-Cable Installation:

      - Install cabling with horizontal and vertical cable guides in telecommunications spaces with terminating hardware and interconnection equipment.

      - Suspend copper cable not in a wireway or pathway a minimum of 8 inches (200 mm) above ceilings by cable supports not more than 60 inches (1525 mm) apart.

      - Cable shall not be run through structural members or in contact with pipes, ducts, or other potentially damaging items.

    - Separation from EMI Sources:

      - Comply with BICSI TDMM and TIA/EIA-569-A recommendations for separating unshielded copper voice and data communication cable from potential EMI sources, including electrical power lines and equipment.

      - Separation between open communications cables or cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

        - Electrical Equipment Rating Less Than 2 kVA: A minimum of 5 inches (127 mm).

        - Electrical Equipment Rating between 2 and 5 kVA: A minimum of 12 inches (300 mm).

        - Electrical Equipment Rating More Than 5 kVA: A minimum of 24 inches (600 mm).

      - Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

        - Electrical Equipment Rating Less Than 2 kVA: A minimum of 2-1/2 inches (64 mm).

        - Electrical Equipment Rating between 2 and 5 kVA: A minimum of 6 inches (150 mm).

        - Electrical Equipment Rating More Than 5 kVA: A minimum of 12 inches (300 mm).

      - Separation between communications cables in grounded metallic raceways and power lines and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

        - Electrical Equipment Rating Less Than 2 kVA: No requirement.

        - Electrical Equipment Rating between 2 and 5 kVA: A minimum of 3 inches (75 mm).

        - Electrical Equipment Rating More Than 5 kVA: A minimum of 6 inches (150 mm).

      - Separation between Cables and Electrical Motors and Transformers, 5 kVA or HP and Larger: A minimum of 48 inches (1200 mm).

      - Separation between Cables and Fluorescent Fixtures: A minimum of 5 inches (127 mm).

  - CONTROL CIRCUIT CONDUCTORS

    - Minimum Conductor Sizes:

      - Class 1 remote-control and signal circuits, No. 14 AWG.

      - Class 2 low-energy, remote-control and signal circuits, No. 16 AWG.

      - Class 3 low-energy, remote-control, alarm and signal circuits, No.

12 AWG.

| 3.3 |  | CONNECTIONS |
| --- | --- | --- |
|  | A. | Comply with requirements in Division 28 Section "VIDEO SURVEILLANCE" |
|  |  | for connecting, terminating, and identifying wires and cables. |
| 3.4 |  | FIRESTOPPING |
|  | A. | Comply with requirements in Division 07 Section "PENETRATION |
|  |  | FIRESTOPPING." |
|  | B. | Comply with TIA/EIA-569-A, "Firestopping" Annex A. |
|  | C. | Comply with BICSI TDMM, "Firestopping Systems" Article. |
| 3.5 |  | GROUNDING |
|  | A. | For communications wiring, comply with ANSI-J-STD-607-A and with BICSI |
|  |  | TDMM, "Grounding, Bonding, and Electrical Protection" Chapter. |
|  | B. | For low-voltage wiring and cabling, comply with requirements in |
|  |  | Division 28 Section "GROUNDING AND BONDING FOR ELECTRONIC SAFETY AND |
| 3.6 |  | SECURITY." IDENTIFICATION |
|  | A. | Identify system components, wiring, and cabling complying with TIA/EIA- |
|  |  | 606-A. |

    - Install a permanent wire marker on each wire at each termination.

    - Identifying numbers and letters on the wire markers shall correspond to those on the wiring diagrams used for installing the systems.

    - Wire markers shall retain their markings after cleaning.

    - In each handhole, install embossed brass tags to identify the system served and function.

  - FIELD QUALITY CONTROL

    - Testing Agency: Engage a qualified testing agency to perform tests and inspections.

    - Perform tests and inspections.

    - Tests and Inspections:

      - Visually inspect UTP cable jacket materials for UL or third-party certification markings. Inspect cabling terminations to confirm color-coding for pin assignments, and inspect cabling connections to confirm compliance with TIA/EIA-568-B.1.

      - Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

      - Test UTP cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors. Test operation of shorting bars in connection blocks. Test cables after termination but not cross connection.

a. Test instruments shall meet or exceed applicable requirements in TIA/EIA-568-B.2. Perform tests with a tester that complies with performance requirements in "Test Instruments (Normative)" Annex, complying with measurement accuracy specified in "Measurement Accuracy (Informative)" Annex. Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

    - Document data for each measurement. Print data for submittals in a summary report that is formatted using Table 10.1 in BICSI TDMM as a guide, or transfer the data from the instrument to the computer, save as text files, print, and submit.

    - End-to-end cabling will be considered defective if it does not pass tests and inspections.

    - Prepare test and inspection reports.

  - EXISTING WIRING

    - Unless specifically indicated on the plans, existing wiring shall not be reused for the new installation. Only wiring that conforms to the specifications and applicable codes may be reused. If existing wiring does not meet these requirements, existing wiring may not be reused and new wires shall be installed.

- - - E N D - - -

SECTION 28 05 26

GROUNDING AND BONDING FOR ELECTRONIC SAFETY AND SECURITY

PART 1 - GENERAL

  - DESCRIPTION

    - This section specifies the finishing, installation, connection, testing and certification of the grounding and bonding required for a fully functional Electronic Safety and Security (ESS) system.

    - “Grounding electrode system” refers to all electrodes required by NEC, as well as including made, supplementary, grounding electrodes.

    - The terms “connect”, and “bond” are used interchangeably in this specification and have the same meaning

  - RELATED WORK

    - Section 01 00 00 - GENERAL REQUIREMENTS. For General Requirements.

    - Section 28 05 00 - REQUIREMENTS FOR ELECTRONIC SAFETY AND SECURITY

INSTALLATIONS. For general electrical requirements, quality assurance, coordination, and project conditions that are common to more than one section in Division 28.

    - Section 28 05 13 - CONDUCTORS AND CABLES FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for low voltage power and lighting wiring.

  - SUBMITTALS

    - Submit in accordance with Section 28 05 00, COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND SECURITY.

    - Shop Drawings:

      - Clearly present enough information to determine compliance with drawings and specifications.

      - Include the location of system grounding electrode connections and the routing of aboveground and underground grounding electrode conductors.

    - Test Reports: Provide certified test reports of ground resistance.

    - Certifications: Two weeks prior to final inspection, submit four copies of the following to the Resident Engineer and COTR:

      - Certification that the materials and installation are in accordance with the drawings and specifications.

      - Certification by the contractor that the complete installation has been properly installed and tested.

  - APPLICABLE PUBLICATIONS

    - Publications listed below (including amendments, addenda, revisions, supplements, and errata) form a part of this specification to the extent referenced. Publications are referenced in the text by designation only.

    - American Society for Testing and Materials (ASTM):

B1-07...................Standard Specification for Hard-Drawn Copper

Wire

B3-07...................Standard Specification for Soft or Annealed

Copper Wire

B8-04...................Standard Specification for Concentric-Lay-

Stranded Copper Conductors, Hard, Medium-Hard, or Soft

    - Institute of Electrical and Electronics Engineers, Inc. (IEEE):

81-1983.................IEEE Guide for Measuring Earth Resistivity,

Ground Impedance, and Earth Surface Potentials of a Ground System

C2-07...................National Electrical Safety Code

    - National Fire Protection Association (NFPA):

70-11...................National Electrical Code (NEC)

99-2005.................Health Care Facilities

    - Underwriters Laboratories, Inc. (UL):

44-05 ..................Thermoset-Insulated Wires and Cables

83-08 ..................Thermoplastic-Insulated Wires and Cables

467-07 .................Grounding and Bonding Equipment

486A-486B-03 ...........Wire Connectors

PART 2 - PRODUCTS

  - GROUNDING AND BONDING CONDUCTORS

    - Equipment grounding conductors shall be UL 83 insulated stranded copper, except that sizes 6 mm² (10 AWG) and smaller shall be solid copper. Insulation color shall be continuous green for all equipment grounding conductors, except that wire sizes 25 mm² (4 AWG) and larger shall be permitted to be identified per NEC.

    - Bonding conductors shall be ASTM B8 bare stranded copper, except that sizes 6 mm² (10 AWG) and smaller shall be ASTM B1 solid bare copper wire.

  - SPLICES AND TERMINATION COMPONENTS

    - Components shall meet or exceed UL 467 and be clearly marked with the manufacturer, catalog number, and permitted conductor size(s).2.4 ground connections

    - Listed and labeled by an NRTL acceptable to authorities having jurisdiction for applications in which used and for specific types, sizes, and combinations of conductors and other items connected.

    - Below Grade: Exothermic-welded type connectors.

    - Above Grade:

      - Bonding Jumpers: Compression-type connectors, using zinc-plated fasteners and external tooth lockwashers.

      - Connection to Building Steel: Exothermic-welded type connectors.

      - Ground Busbars: Two-hole compression type lugs, using tin-plated copper or copper alloy bolts and nuts.

      - Rack and Cabinet Ground Bars: One-hole compression-type lugs, using zinc-plated or copper alloy fasteners.

      - Bolted Connectors for Conductors and Pipes: Copper or Copper Alloy, pressure type with at least two bolts.

        - Pipe Connectors: Clamp type, sized for pipe.

      - Welded Connectors: Exothermic-welding kits of types recommended by kit manufacturer for materials being joined and installation conditions.

  - EQUIPMENT RACK AND CABINET GROUND BARS

    - Provide solid copper ground bars designed for mounting on the framework of open or cabinet-enclosed equipment racks with minimum dimensions of

4 mm thick by 19 mm wide (3/8 inch x ¾ inch).

  - GROUND TERMINAL BLOCKS

    - At any equipment mounting location (e.g., backboards and hinged cover enclosures) where rack-type ground bars cannot be mounted, provide screw lug-type terminal blocks.

  - SECURITY CONTROL ROOM GROUND

    - Provide 50mm2 (1/0 AWG) stranded copper grounding conductor(s) color coded with a green jacket, bolted at the Room’s Communications System Grounding Electrode Cooper Plate and circulate to each equipment rack ground buss bar through the wire management system. Connect each equipment rack, wire management system’s cable tray, ladder, etc. to

the circulating ground wire with a minimum 25mm2 (4AWG) stranded Cooper Wire, color coded with a green jacket.

PART 3 - EXECUTION

  - GENERAL

    - Ground in accordance with the NEC, as shown on drawings, and as specified herein.

    - System Grounding:

      - Secondary service neutrals: Ground at the supply side of the secondary disconnecting means and at the related transformers.

      - Separately derived systems (transformers downstream from the service entrance): Ground the secondary neutral.

    - Equipment Grounding: Metallic structures, including ductwork and building steel, enclosures, raceways, junction boxes, outlet boxes, cabinets, machine frames, and other conductive items in close proximity with electrical circuits, shall be bonded and grounded.

  - INACCESSIBLE GROUNDING CONNECTIONS

    - Make grounding connections, which are buried or otherwise normally inaccessible (except connections for which periodic testing access is required) by exothermic weld.

  - CORROSION INHIBITORS

    - When making ground and ground bonding connections, apply a corrosion inhibitor to all contact surfaces. Use corrosion inhibitor appropriate for protecting a connection between the metals used.

  - CONDUCTIVE PIPING

    - Bond all conductive piping systems, interior and exterior, to the building to the grounding electrode system. Bonding connections shall be made as close as practical to the equipment ground bus.

  - COMPUTER ROOM/SECURITY EQUIPMENT ROOM GROUNDING

    - Conduit: Ground and bond metallic conduit systems as follows:

      - Ground metallic service conduit and any pipes entering or being routed within the computer room at each end using 16 mm² (6AWG) bonding jumpers.

      - Bond at all intermediate metallic enclosures and across all joints using 16 mm² (6 AWG) bonding jumpers.

  - WIREWAY GROUNDING

    - Ground and Bond Metallic Wireway Systems as follows:

      - Bond the metallic structures of wireway to provide 100 percent electrical continuity throughout the wireway system by connecting a

16 mm² (6 AWG) bonding jumper at all intermediate metallic enclosures and across all section junctions.

      - Install insulated 16 mm² (6 AWG) bonding jumpers between the wireway system bonded as required in paragraph 1 above, and the closest building ground at each end and approximately every 16 meters (50 feet).

      - Use insulated 16 mm² (6 AWG) bonding jumpers to ground or bond metallic wireway at each end at all intermediate metallic enclosures and cross all section junctions.

      - Use insulated 16 mm² (6 AWG) bonding jumpers to ground cable tray to column-mounted building ground plates (pads) at each end and approximately every 15 meters.

3.8 EXTERIOR LIGHT/CAMERA POLES

A. Provide 20 ft 6.1 M of No. 4 bare copper coiled at bottom of pole base excavation prior to pour, plus additional unspliced length in and above foundation as required to reach pole ground stud.

3.9 GROUND RESISTANCE

- Grounding system resistance to ground shall not exceed 5 ohms. Make any modifications or additions to the grounding electrode system necessary for compliance without additional cost to the Government. Final tests shall ensure that this requirement is met.

- Resistance of the grounding electrode system shall be measured using a four-terminal fall-of-potential method as defined in IEEE 81. Ground resistance measurements shall be made before the electrical distribution system is energized and shall be made in normally dry conditions not fewer than 48 hours after the last rainfall. Resistance measurements of separate grounding electrode systems shall be made before the systems are bonded together below grade. The combined resistance of separate systems may be used to meet the required resistance, but the specified number of electrodes must still be provided.

- Services at power company interface points shall comply with the power company ground resistance requirements.

- Below-grade connections shall be visually inspected by the Resident Engineer and COTR prior to backfilling. The contractor shall notify the

Resident Engineer and COTR 24 hours before the connections are ready for inspection.

  - LABELING

    - Comply with requirements in Division 27 Section " IDENTIFICATION FOR COMMUNICATIONS SYSTEMS" Article for instruction signs. The label or its text shall be green.

    - Install labels at the telecommunications bonding conductor and grounding equalizer and at the grounding electrode conductor where exposed.

      - Label Text: "If this connector or cable is loose or if it must be removed for any reason, notify the facility manager."

  - FIELD QUALITY CONTROL

    - Perform tests and inspections.

    - Tests and Inspections:

      - After installing grounding system but before permanent electrical circuits have been energized, test for compliance with requirements.

      - Inspect physical and mechanical condition. Verify tightness of accessible, bolted, electrical connections with a calibrated torque wrench according to manufacturer's written instructions.

      - Test completed grounding system at each location where a maximum ground-resistance level is specified, at service disconnect enclosure grounding terminal at individual ground rods. Make tests at ground rods before any conductors are connected.

        - Measure ground resistance no fewer than two full days after last trace of precipitation and without soil being moistened by any means other than natural drainage or seepage and without chemical treatment or other artificial means of reducing natural ground resistance.

        - Perform tests by fall-of-potential method according to IEEE 81.

    - Grounding system will be considered defective if it does not pass tests and inspections.

    - Prepare test and inspection reports.

    - Report measured ground resistances that exceed the following values:

      - Power Distribution Units or Panel boards Serving Electronic Equipment: 3 ohm(s).

    - Excessive Ground Resistance: If resistance to ground exceeds specified values, notify Architect promptly and include recommendations to reduce ground resistance.

- - - E N D - - -

SECTION 28 23 00 VIDEO SURVEILLANCE

PART 1 – GENERAL

  - DESCRIPTION

    - Provide and install a complete Video Surveillance System, which is identified as the Video Assessment and Surveillance System hereinafter referred to as the VASS System as specified in this section.

    - This section includes a cloud-based video surveillance solution including:

      - Cloud-based management platform

      - Edge-based video analytics

      - Indoor Dome Series cameras

      - Outdoor Dome Series cameras

      - Mini Series cameras

      - Bullet Series cameras

      - Fisheye Series cameras

      - Multisensor Series cameras

      - Pan-Tilt-Zoom (PTZ) cameras

      - FIPS-Validated cameras

      - Command Connector

      - Two (2) Viewing Stations within existing security command/control room

      - PoE Injectors

      - Camera mounts, adapters, and accessories

      - Cellular Gateways

      - Wi-Fi Gateways

      - Camera licensing

    - Proposed video surveillance system shall be provided by OEM and the software shall be OEM Command suite. All cameras and associated system peripherals shall be provided by OEM; no substitutions are allowed.

    - Active networking components as required to allow the video surveillance system to access the VA LAN/WAN as well as the “cloud” for data storage shall be provided by VA OIT including but not limited to network switches located within the telecommunication rooms (TR) and tower PC workstations for the two (2) security command stations. Tower PC shall be furnished by VA OIT based on specification requirements noted herein and handed to Division 28 Security Contractor for video surveillance software integration and testing.

  - RELATED WORK

    - Section 01 00 00 - GENERAL REQUIREMENTS. For General Requirements.

    - Section 07 84 00 - FIRESTOPPING. Requirements for firestopping application and use.

    - Section 27 05 33 - CONDUITS AND BACKBOXES FOR COMMUNICATIONS SYSTEMS.

Requirements for infrastructure.

    - Section 28 05 00 – COMMON WORK RESULTS FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for general requirements that are common to more than one section in Division 28.

    - Section 28 05 01 – STATEMENT OF WORK FOR ELECTRONIC SAFETY AND SECURITY – CAMPUS VIDEO SURVEILLANCE SYSTEM REPLACEMENT. Requirements for

general requirements that are Common to more than one section in Division 28.

    - Section 28 05 13 - CONDUCTORS AND CABLES FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for conductors and cables.

    - Section 28 05 26 - GROUNDING AND BONDING FOR ELECTRONIC SAFETY AND

SECURITY. Requirements for grounding of equipment.

  - DEFINITIONS

    - ACS:	Access Control System.

    - AGC: Automatic gain control.

    - API:	Application Programmed Interface

    - B/W: Black and white.

    - CCD: Charge-coupled device.

    - CIF: Common Intermediate Format CIF images are 352 pixels wide and 88/240 (PAL/NTSC) pixels tall (352 x 288/240).

    - 4CIF: resolution is 704 pixels wide and 576/480 (PAL/NTSC) pixels tall (704 x 576/480).

    - CCTV:	Closed Circuit Television

    - CMOS:	Complementary Metal-Oxide Semiconductor

    - DHCP – Dynamic Host Configuration Protocol

    - DNS – Domain Name System

    - DPDT – Double pole, double throw

    - FPS – Frames Per Second

    - H.264 (also known as MPEG4 Part 10): a encoding format that compresses video much more effectively than older (MPEG4) standards.

    - IP:	Internet Protocol

    - ips: Images per second.

    - LAN – Local Area Network

    - LPR – License Plate Recognition

    - MPEG: Moving picture experts group.

    - MPEG4: a video encoding and compression standard that uses inter- frame encoding to significantly reduce the size of the video stream being transmitted.

    - NFC – Near Field Communications

    - NVR – Network Video Recorder

    - NTSC: National Television System Committee.

    - ODBC – Open Database Connectivity

    - PoE – Power Over Ethernet

    - RAM – Random Access Memory

    - SPDT – Single pole, double throw

    - SSL – Secure Sockets Layer

    - SSO – Single sign-on

    - TCP: Transport Control Protocol

    - UPS: Uninterruptible power supply.

    - VMS: Video Management System

    - WDR: Wide Dynamic Range

    - PTZ: refers to a movable camera that has the ability to pan left and right, tilt up and down, and zoom or magnify a scene.

  - QUALITY ASSURANCE

    - The Contractor shall be responsible for providing, installing, and the operation of the VASS System as shown. The Contractor shall also provide certification as required.

    - The security system shall be installed and tested to ensure all components are fully compatible as a system and can be integrated with all associated security subsystems, whether the security system is stand-alone or a part of a complete Information Technology (IT) computer network.

    - The Contractor or security sub-contractor shall be a licensed security Contractor as required within the state or jurisdiction of where the installation work is being conducted.

    - Manufacturers Qualifications: The manufacturer shall regularly and presently produce, as one of the manufacturer's principal products, the equipment and material specified for this project and shall have manufactured the item for at least three years.

    - Product Qualification:

      - Manufacturer's product shall have been in satisfactory operation, on three installations of similar size and type as this project, for approximately three years.

      - The Government reserves the right to require the Contractor to submit a list of installations where the products have been in operation before approval.

    - Contractor Qualification:

      - The Contractor or security sub-contractor shall be a licensed security Contractor with a minimum of five (5) years experience installing and servicing systems of similar scope and complexity. The Contractor shall be an authorized regional representative of the Video Assessment and Surveillance System’s (VASS) manufacturer. The Contractor shall provide four (4) current references from clients with systems of similar scope and complexity which became operational in the past three (3) years. At least three (3) of the references shall be utilizing the same system components, in a similar configuration as the proposed system. The references must include a current point of contact, company or agency name, address, telephone number, complete system description, date of completion, and approximate cost of the project. The owner reserves the option to visit the reference sites, with the site owner’s permission and representative, to verify the quality of installation and the references’ level of satisfaction with the system. The Contractor shall provide copies of system manufacturer certification for all technicians. The Contractor shall only utilize factory-trained technicians to install, program, and service the VASS. The Contractor shall only utilize factory-trained technicians to install, terminate and service cameras, control, and recording equipment. The technicians shall have a minimum of five (5) continuous years of technical experience in electronic security systems. The Contractor shall have a local service facility. The facility shall be located within 60 miles of the project site. The local facility shall include sufficient spare parts inventory to support the service requirements associated with this contract. The facility shall also include appropriate diagnostic equipment to perform diagnostic procedures. The COTR reserves the option of

surveying the company’s facility to verify the service inventory and presence of a local service organization.

      - The Contractor shall provide proof project superintendent with BICSI Certified Commercial Installer Level 1, Level 2, or Technician to provide oversight of the project.

      - Cable installer must have on staff a Registered Communication Distribution Designer (RCDD) certified by Building Industry Consulting Service International. The staff member shall provide consistent oversight of the project cabling throughout design, layout, installation, termination and testing.

    - Service Qualifications: There shall be a permanent service organization maintained or trained by the manufacturer which will render satisfactory service to this installation within four hours of receipt of notification that service is needed. Submit name and address of service organizations.

  - SUBMITTALS

    - Submit below items in conjunction with Master Specification Sections 01

33 23, Shop Drawings, Product Data, and Samples, and Section 02 41 00, Demolition Drawings.

    - Provide certificates of compliance with Section 1.4, Quality Assurance.

    - Submit product Data and Shop Drawings submittals for review and approval prior to the commencement of work:

      - Manufacturer's name, brand name, exact part number, options, accessories, and catalog cutsheet references for all equipment supplied including cabling. Include manufacturer’s published installation instructions. Indicate UL listings for system components.

      - Complete wiring diagrams for all components, including cable types and quantities, routings, floor plans indicating device locations, conduit sizes, and point-to-point termination and riser diagrams.

      - Device legend on the shop drawings that identifies the symbols used for all devices including mounting heights, back box requirements, part and model numbers, operating voltages (if applicable), wire and cabling requirements, label text, and panel termination points.

      - Fully dimensioned shop drawings including floorplans, enlarged plans, elevations, and installation details of all security devices, equipment rooms and closets, consoles, controllers, racks, enclosures, and fabricated equipment, showing locations of all major components including mounting details. Indicate UL system and rating listings for penetration firestop systems through rated partitions and floors.

      - Bill of Materials.

      - Material Safety Data Sheets (MSDS) for fire stopping materials and sealants.

    - Submit System Programming submittals for review and approval prior to commencement of work:

      - Proposed programming, including nomenclature conventions, device names and text descriptions, timings, camera call-up trigger alarms with associated cameras, and sequence of operations.

      - Approved device names and text descriptions as programmed into the security systems shall be reflected on the “As-Built” Record Drawings as well as on device and cable labels.

    - Submit Operation and Maintenance Manuals (O&M’s) submittals for review and approval prior to the completion of the project:

      - Updated product data and shop drawings submittals reflecting the final conditions.

      - Warranty letter with start and end date.

      - Warranty service and maintenance contact information: including names, address, phone number, and website address. Provide specific instructions or forms as required to initiate a trouble ticket or work order request.

      - Letter indicating that all software and licensing is the sole property of the Owner.

      - Troubleshooting checklist information.

      - Replacement parts and consumables ordering information including the contact information for local sources.

      - Provide an updated System Programming submittal including:

        - Final listing of doors, locations, and normal status in CSV format.

        - System administration and management operating instructions.

        - Setting up Users, User Groups, Access Levels, Doors, Door Schedules, and Exceptions

        - Assigning Access Groups to all Users.

        - Monitoring system activity.

        - Running standard reports.

        - Setting up logins and permissions.

    - Provide a pre-installation and as-built design package in both electronic format(CAD and PDF) and on paper, minimum size 1220 x 1220 millimeters (48 x 48 inches); drawing submittals shall be per the established project schedule. Maintain a complete set of “As-Built” Record Drawings at the project site updated with mark-ups of the actual installation conditions.

    - Pre-installation design and as-built packages shall include, but not be limited to:

      - Index Sheet that shall:

        - Define each page of the design package to include facility name, building name, floor, and sheet number.

        - Provide a list of all security abbreviations and symbols.

        - Reference all general notes that are utilized within the design package.

        - Specification and scope of work pages for all security systems that are applicable to the design package that will:

          - Outline all general and job specific work required within the design package.

          - Provide a device identification table outlining device Identification (ID) and use for all security systems equipment utilized in the design package.

      - Floor plans, site plans, and enlarged plans shall:

        - Include a title block as defined above.

        - Define the drawings scale in both standard and metric measurements.

        - Provide device identification and location.

        - Address all signal and power conduit runs and sizes that are associated with the design of the electronic security system and other security elements (e.g., barriers, etc.).

        - Identify all pull box and conduit locations, sizes, and fill capacities.

        - Address all general and drawing specific notes for a particular drawing sheet.

        - Provide Field of View (FOV) floor and site plans indicating each camera location and the associated FOV to scale to represent the

observation capabilities of the cameras proposed for each location.

      - A riser drawing for each applicable security subsystem shall:

        - Indicate the sequence of operation.

        - Relationship of integrated components on one diagram.

        - Include the number, size, identification, and maximum lengths of interconnecting wires.

        - Wire/cable types shall be defined by a wire and cable schedule. The schedule shall utilize a lettering system that will correspond to the wire/cable it represents (example: A = 18 AWG/1 Pair Twisted, Unshielded). This schedule shall also provide the manufacturer’s name and part number for the wire/cable being installed.

      - A system drawing for each applicable security system shall:

        - Identify how all equipment within the system, from main panel to device, shall be laid out and connected.

        - Provide full detail of all system components wiring from point- to-point.

        - Identify wire types utilized for connection, interconnection with associate security subsystems.

        - Show device locations that correspond to the floor plans.

        - All general and drawing specific notes shall be included with the system drawings.

      - A schedule for all of the applicable security subsystems shall be included. All schedules shall provide the following information:

        - Device ID.

        - Device Location (e.g., site, building, floor, room number, location, and description).

        - Mounting type (e.g., flush, wall, surface, etc.).

        - Power supply or circuit breaker and power panel number.

        - In addition, for the VASS Systems, provide the camera ID, camera type (e.g., fixed or pan/tilt/zoom (P/T/Z), lens type (e.g. for fixed cameras only) and housing model number.

      - Detail and elevation drawings for all devices that define how they were installed and mounted.

    - Pre-installation design packages shall be reviewed by the Contractor along with a VA representative to ensure all work has been clearly

defined and completed. All reviews shall be conducted in accordance with the project schedule. There shall be four (4) stages to the review process:

      - 35 percent

      - 65 percent

      - 90 percent

      - 100 percent

    - Provide manufacturer security system product cut-sheets. Submit for approval at least 30 days prior to commencement of formal testing, a Security System Operational Test Plan. Include procedures for operational testing of each component and security subsystem, to include performance of an integrated system test.

    - Submit manufacture’s certification of Underwriters Laboratories, Inc. (UL) listing as specified. Provide all maintenance and operating manuals per the VA General Requirements, Section 01 00 00, GENERAL REQUIREMENTS.

    - Submit completed System Readiness Checklists provided by the Commissioning Agent and completed by the contractor, signed by a qualified technician and dated on the date of completion, in accordance with the requirements of Section 28 08 00 COMMISSIONING OF ELECTRONIC SAFETY AND SECURITY SYSTEMS.

  - APPLICABLE PUBLICATIONS

    - The publications listed below (including amendments, addenda, revisions, supplement, and errata) form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.

    - American National Standards Institute (ANSI)/Electronic Industries Alliance (EIA):

330-09..................Electrical Performance Standards for CCTV

Cameras

375A-76.................Electrical Performance Standards for CCTV

Monitors

    - Institute of Electrical and Electronics Engineers (IEEE):

C62.41-02...............IEEE Recommended Practice on Surge Voltages in

Low-Voltage AC Power Circuits 802.3af-08..............Power over Ethernet Standard

    - Federal Communications Commission (FCC):

(47 CFR 15) Part 15	Limitations on the Use of Wireless Equipment/Systems

    - National Electrical Contractors Association (NECA):

303-2005................Installing Closed Circuit Television (CCTV)

Systems

    - National Fire Protection Association (NFPA):

70-08...................Article 780-National Electrical Code

    - Federal Information Processing Standard (FIPS):

140-2-02................Security Requirements for Cryptographic Modules

    - Underwriters Laboratories, Inc. (UL):

983-06..................Standard for Surveillance Camera Units 3044-01.................Standard for Surveillance Closed Circuit

Television Equipment

  - COORDINATION

    - Coordinate arrangement, mounting, and support of video surveillance equipment:

      - To allow maximum possible headroom unless specific mounting heights that reduce headroom are indicated.

      - To provide for ease of disconnecting the equipment with minimum interference to other installations.

      - To allow right of way for piping and conduit installed at required slope.

      - So connecting raceways, cables, wireways, cable trays, and busways will be clear of obstructions and of the working and access space of other equipment.

    - Coordinate installation of required supporting devices and set sleeves in cast-in-place concrete, masonry walls, and other structural components as they are constructed.

    - Coordinate location of access panels and doors for video surveillance items that are behind finished surfaces or otherwise concealed.

  - DELIVERY, STORAGE, AND HANDLING

    - Ship equipment in original packaging to prevent damage. All handling shall be in accordance with manufacturer recommendations. Inspect all products and materials for any damage immediately upon delivery to the project site.

    - Provide protective covering during construction.

    - Replace equipment and products damaged during shipping, handling, distribution, storage, installation, or construction with new equipment and products.

    - Equipment and products stored at the project site or at an off-site location shall be protected from dust, dirt, and foreign matter. Protect equipment and products from water, damage, dents, bumps, and scratches.

  - SCHEDULING

    - Submit proposed construction schedule detailing the task milestones, durations, and sequences for the project for review and approval prior to commencement of work.

    - When work is performed in a sensitive area or in an area occupied with ongoing business activities coordinate with the Owner and the affected department’s representative to determine the best time to perform the work required.

  - WARRANTY OF CONSTRUCTION

    - Warrant VASS System work subject to the Article “Warranty of Construction” of FAR clause 52.246-21.

    - Provide one-year parts and labor project warranty. Parts and labor shall be guaranteed against defects in materials and workmanship for one year from written notification of acceptance.

    - Provide five-year maintenance and service protection plan for VASS system.

    - Demonstration and training shall be performed prior to system acceptance.

PART 2 – PRODUCTS

  - MANUFACTURER

    - Manufacturer shall be OEM Inc.

      - Headquarters: 405 E 4th Ave. San Mateo, CA 94401

      - Toll Free: (888) 829-0668

      - General: team@OEM.com

      - Sales: sales@OEM.com

      - Website: www.OEM.com

      - Non-OEM Inc. products shall be limited to those identified as compatible within the product descriptions below.

  - LICENSING

    - Provide all required licenses for the specified system components.

    - All system component licenses shall be 5-year licenses.

    - All system monitoring licenses shall be LIC-BV Premium Alarm License.

  - SYSTEM DESCRIPTION

    - A hybrid cloud video surveillance system with storage and image processing on edge devices managed through the OEM Command cloud platform.

    - OEM Command Management Software

      - Access and management for all cameras and users across all sites. Command management functions include:

        - Set up new cameras

        - Create and manage sites at scale

        - One-click device install:

          - Add devices without assigning a site or configuring the device upfront.

          - New devices will be added to and “Unassigned Devices” list

          - Immediately check if device is online and see live data

        - Manage camera device and system settings.

        - Access live and archived footage

        - Manage users

      - Security and Permissions:

        - SAML/OAuth support for single sign-on

        - 2-factor authentication options

        - User permissions can be controlled at camera, site, and organization levels

      - Remote Access

        - Web app access

        - Native apps for iOS, Android, and the OEM VX52 Viewing Station

      - Archiving and Sharing:

        - Command licenses include unlimited cloud archiving.

        - Export footage in MP4 format.

        - Create and share Live Links via text or email.

      - Extended Cloud Backup (ECB)

        - Flexible Structure:

          - Extend cloud backup in 30-day increments (“packs”)

          - Packs can be stacked per device

        - Self-Service Portal:

          - Simple License Claiming: Admins can claim ECB licenses directly through the self-service portal.

          - Seamless License Management: Easily track usage, and support compliance with retention requirements – all from one central dashboard.

          - Automatic Co-Terming: Eliminate the need to manually calculate renewal dates for ECB licenses. ECB licenses will now co-terminate with all other Command product licenses.

    - Analytics:

      - People Analytics:

        - Intelligent edge-based video processing to identify individuals in a scene.

        - Filter identified individuals by attributes, including:

          - Date

          - Time

          - Appearance

          - Clothing color

          - Backpack detection

          - Facial matches

      - AI-Powered Search:

        - Use freeform text queries to search for people and vehicles.

        - Reverse Image Analytics:

          - Upload a photo of a person, vehicle, or object to obtain relevant search results.

      - History Player Search: Instantaneously find footage and construct a chronological timeline of where an individual appeared on multiple cameras across wide areas.

      - Face Search: Quickly search for matching people by selecting an existing face from organizational records uploaded image.

      - Face Blur:

        - Live Face Blur:

          - Blur faces of individuals detected in camera live streams for privacy.

          - Admins can enable Live Face Blur by default for all cameras while also giving users the option to unblur faces in case of an incident.

        - Selective Face Blur:

          - Choose which archived faces to blur to support the privacy of individuals stored in an archive.

      - Person History:

        - Browse through snapshots of people detected in frame.

        - Save snapshots or access associated full-resolution video.

      - Occupancy Trends:

        - Estimate how many people cross a designated line in a camera field of view.

      - Cross-Camera Tracking:

        - Search video from different cameras of the same identified individual.

      - Person Line Crossing: trigger an alarm if a person crosses a predetermined digital line in a specified direction.

      - Direction of Travel: trigger an alarm by specified direction of travel detection.

      - Person Line Crossing: trigger an alarm if a person crosses a predetermined digital line in a specified direction.

      - Person or Vehicle Loitering: trigger an alarm if a person or vehicle is continuously detected in a pre-selected region beyond a certain time threshold.

      - Person of Interest (POI) and License Plate of Interest (LPOI):

        - Receive real-time POI alerts on the live feed when viewing a single camera page.

        - POI alerts display associated LPOI and vice versa.

    - Vehicle Analytics:

      - Intelligent edge-based video processing to identify vehicles in a scene.

      - Filter identified vehicles by attributes, including:

        - Date.

        - Time.

        - Vehicle make.

        - Color.

        - Vehicle body type.

      - Vehicle History:

        - Browse through snapshots of vehicles detected in-frame.

        - Save snapshots or associated full-resolution video.

      - Cross-Camera Tracking:

        - Search video from different cameras of the same identified vehicle.

      - Vehicle Number Tracking: draw a digital line on the video feed and get an estimate of how many vehicles crossed that line.

      - Vehicle Line Crossing: trigger an alarm if a vehicle crosses a predetermined digital line in a specified direction.

      - Vehicle Loitering: trigger an alarm if a vehicle is continuously detected in a pre-selected region beyond a certain time threshold.

      - License Plate Recognition:

        - LPR coverage, monitoring, and search by plate number.

        - Generate License Plate of Interest Alerts via SMS or email with an image or link to review the associated footage.

      - License Plate Recognition Unlock:

        - LPR unlock utilizes a peer-to-peer communication protocol to facilitate secure device-to-device interactions between LPR- enabled CB52 and CB62 bullet cameras and OEM’s AC42 and AC62 door controllers.

        - LPR camera results can be used as an input method for a gate, unlocking that gate anytime an authorized license plate is verified by the access controller.

        - License plates can be added to any access user profile. All unlock events from a license plate are attributed to an access user.

    - Unified Alerts:

      - Set up and configure alerts for access control, cameras, alarms, and environmental sensors from the Alerts page in Command.

      - Configure real-time alerts via SMS, email, Microsoft Teams, and Slack.

a. Search Alert Inbox for alert names, filter across all alerts, star alerts, and create custom sections for related alerts.

    - Enhanced Sensor Alerts:

      - All sensors paired with a context camera to display:

        - People detection thumbnails show all people detected before, during, and after a sensor alert.

        - People activity overlay on the sensor alert graph to mark people's activity.

      - Third-Party VMS Integrations for Air Quality Sensor Events:

        - Send sensor event alerts to the following third-party video management systems: Milestone XProtect, Wisenet WAVE, exacqVision.

    - AI-Powered Alerts:

      - Use freeform language to set up alerts on events of interest.

      - Create alerts based on AI-powered search queries.

    - Shortcuts Navigation Tool:

      - Available for both live streams and historic views:

        - Instantly jump between neighboring camera feeds to quickly track moving subjects during live investigations.

        - Trace a subject’s movements from camera to camera to review and archive a subject's path in historic views.

    - Adaptive Quality with Variable Bitrates: Cameras use variable bitrates for both SQ and HQ video allowing for video to be recorded at a lower bitrate during less complex scenes and a higher bitrate during more complex scenes.

    - PTZ Sentry Mode:

      - Patrol multiple scenes when a live operator is not available.

      - Select up to 25 preset views.

      - Configure how long Sentry Mode dwells on each scene (30 seconds to 24 hours).

    - OEM Verify:

      - Browser-based tool that allows anyone in possession of footage from a OEM camera to verify its authenticity.

      - Verify recorded footage by uploading the file at OEM.com/verify.

    - Enterprise Bandwidth Manager (EBM):

      - Set bandwidth limits for all camera upload traffic, including video archiving, cloud backup, and timelapse.

      - Monitor real-time bandwidth usage and selectively terminate active video streams to free up bandwidth.

    - Application Programming Interface:

      - Streaming API: Stream both live and historical footage from cameras; ingest footage into third-party Global Security Operations Center (GSOC) software for live monitoring or into customized analytics software for operational insights.

      - Occupancy Trend Data API: extract foot or vehicle traffic data for further analysis.

      - Access Events Webhooks: integrate real-time system insights into third-party applications.

    - AWS GovCloud:

      - Optional for US government deployments.

      - Continuous monitoring of the system.

      - FIPS encryption in transit and at rest.

      - Strengthened session and identity management capabilities.

    - Data Hosting:

      - Option to process and store data, including image and video data, locally in OEM data centers in the United States, European Union, or Australia.

      - Customize image and video storage location on an org-wide or camera-by-camera basis.

  - GENERAL

    - Video signal format shall comply with the NTSC standard composite video, interlaced. Composite video signal termination shall be 75 ohms.

    - Surge Protection: Protect components from voltage surges originating external to equipment housing and entering through power, communication, signal, control, or sensing leads. Include surge protection for external wiring of each conductor entry connection to components.

    - Power Connections: Comply with requirements in Section 28 05 00 COMMON WORK REQUIREMENTS FOR ELECTRONIC SAFETY AND SECURITY, Part 2, as

recommended by manufacturer for type of line being protected.

    - Tamper Protection: Tamper switches on enclosures, control units, pull boxes, junction boxes, cabinets, and other system components shall initiate a tamper-alarm signal when unit is opened or partially

disassembled. Control-station, control-unit alarm display shall identify tamper alarms and indicate locations.

  - CAMERAS – FIPS VALIDATED CAMERAS

    - FIPS-Validated Camera Series

      - CD42-F Indoor Dome Camera by OEM Inc.

        - Onboard Storage: 256GB to 1TB based on 30-day retention at 24fps.

        - Sensor Resolution: 5MP (2688 x 1944 pixels)

        - Lens Type: Fixed

        - Image Sensor: 1/2.8” Progressive CMOS

        - Focal Length: 2.8mm

        - Iris: Fixed

        - Aperture: F1.6

        - Lens Distortion Correction (LDC): LDC crops the sensor field of view to deliver a rectified, undistorted output image.

        - Field of View (FoV after LDC):

- Horizontal: 97° (78°)

- Vertical: 71° (63°)

- Diagonal: 128° (91°)

        - IR Range: 15m / 49ft in low light

        - Audio: Yes

        - Resistance Ratings:

- IK08

- FCC

- IEC60950-1

        - Dimensions:

- With Mount Plate:

  - Length: 146mm / 5.75in

  - Width: 146mm / 5.75in

  - Height: 104.3mm / 4.11in

- Without Mount Plate:

  - Length: 146mm / 5.75in

  - Width: 146mm / 5.75in

  - Height: 99.8mm / 3.93in

        - Weight:

- With Mount Plate: 748g / 26.38oz

- Without Mount Plate: 608g / 21.45oz

        - Operating Power: 11W (IEEE 802.3af PoE)

        - Operating Temperature: -10°C to 50°C / 14°F to 122°F

        - Operating Humidity: 0% to 90%

        - Connectivity: Ethernet 10/100Mbps RJ-45 cable connector for Network/PoE connection

        - Security:

- Meets the FIPS 140-2 standard, as certified by NIST

- TAA and FY2019 NDAA compliant

      - CD52-F Indoor Dome Camera by OEM Inc.

        - Onboard Storage: 256GB to 1TB based on 30-day retention at 24fps.

        - Sensor Resolution: 5MP (2688 x 1944 pixels)

        - Lens Type: 3x Optical Zoom

        - Image Sensor: 1/2.8” Progressive CMOS

        - Focal Length: 2.8 to 8mm

        - Iris: P-Iris

        - Aperture: F1.3 to F2.4

        - Lens Distortion Correction (LDC): LDC crops the sensor field of view to deliver a rectified, undistorted output image.

        - Field of View (FoV after LDC):

- Horizontal: 41° to 93° (37° to 84°)

- Vertical: 31° to 76° (28° to 68°)

- Diagonal: 50° to 107° (45° to 97°)

        - IR Range: 30m / 98ft in low light

        - Audio: Yes

        - Resistance Rating:

- IK08

- FCC

- IEC60950-1

        - Dimensions:

- With Mount Plate:

  - Length: 146mm / 5.75in

  - Width: 146mm / 5.75in

  - Height: 104.3mm / 4.11in

- Without Mount Plate:

  - Length: 146mm / 5.75in

  - Width: 146mm / 5.75in

  - Height: 99.8mm / 3.93in

        - Weight:

- With Mount Plate: 916g / 32.31oz

- Without Mount Plate: 776g / 27.37oz

        - Operating Power: 11W (IEEE 802.3af PoE)

        - Operating Temperature: -10°C to 50°C / 14°F to 122°F

        - Operating Humidity: 0% to 90%

        - Connectivity: Ethernet 10/100Mbps RJ-45 cable connector for Network/PoE connection

        - Security:

- Meets the FIPS 140-2 standard, as certified by NIST

- TAA and FY2019 NDAA compliant

      - CD42-E-F Outdoor Dome Camera by OEM Inc.

        - Onboard Storage: 256GB to 1TB based on 30-day retention at 24fps.

        - Sensor Resolution: 5MP (2688 x 1944 pixels)

        - Lens Type: Fixed

        - Image Sensor: 1/2.8” Progressive CMOS

        - Focal Length: 2.8mm

        - Iris: Fixed

        - Aperture: F1.6

        - Lens Distortion Correction (LDC): LDC crops the sensor field of view to deliver a rectified, undistorted output image.

        - Field of View (after LDC):

- Horizontal: 87° (78°)

- Vertical: 70° (63°)

- Diagonal: 101° (91°)

        - IR Range: 15m / 50ft in low light

        - Audio: Yes

        - Resistance Rating:

- IK10

- IP67

- FCC

- IEC60950-1

        - Dimensions:

- With Mount Plate:

  - Length: 155mm / 6.1in

  - Width: 155mm / 6.1in

  - Height: 114.6mm / 4.51in

- Without Mount Plate:

  - Length: 155mm / 6.1in

  - Width: 155mm / 6.1in

  - Height: 107.6mm / 4.24in

        - Weight:

- With Mount Plate: 1021g / 36.01oz

- Without Mount Plate: 847g / 29.88oz

        - Operating Power:

- With IR: IEEE 802.3af Type 1 PoE

- Without IR: IEEE 802.3af Type 1 PoE

        - Extended temperature range: IEEE 802.3at Type 2 PoE+

        - Operating Temperature:

- PoE 802.3af: -20°C to 50°C / -4°F to 122°F

- PoE 802.3at: -40°C to 50°C / -40°F to 122°F

        - Operating Humidity: 0% to 90%

        - Connectivity: Ethernet 10/100Mbps RJ-45 cable connector for Network/PoE connection

        - Regulatory Compliance:

- Meets the FIPS 140-2 standard, as certified by NIST

- TAA and FY2019 NDAA compliant

      - CD52-E-F Outdoor Dome Camera by OEM Inc.

        - Onboard Storage: 256GB to 1TB based on 30-day retention at 24fps.

        - Sensor Resolution: 5MP (2688 x 1944 pixels)

        - Lens Type: 3x Optical Zoom

        - Image Sensor: 1/2.8” Progressive CMOS

        - Focal Length: 2.8 to 8mm

        - Iris: P-Iris

        - Aperture: F1.3 to F2.4

        - Lens Distortion Correction (LDC): LDC crops the sensor field of view to deliver a rectified, undistorted output image.

        - Field of View (FoV after LDC):

- Horizontal: 41° to 93° (37° to 84°)

- Vertical: 31° to 76° (28° to 68°)

- Diagonal: 50° to 107° (45° to 97°)

        - IR Range: 30m / 98ft in low light

        - Audio: Yes

        - Resistance Rating:

- IK10

- IP67

- FCC

- IEC60950-1

        - Dimensions:

- With Mount Plate:

  - Length: 155mm / 6.1in

  - Width: 155mm / 6.1in

  - Height: 114.6mm / 4.51in

- Without Mount Plate:

  - Length: 155mm / 6.1in

  - Width: 155mm / 6.1in

  - Height: 107.6mm / 4.24in

        - Weight:

- With Mount Plate: 1244g / 43.88oz

- Without Mount Plate: 1070g / 37.74oz

        - Operating Power:

- With IR: IEEE 802.3af Type 1 PoE

- Without IR: IEEE 802.3af Type 1 PoE

        - Extended temperature range: IEEE 802.3at Type 2 PoE+

        - Operating Temperature:

- PoE 802.3af: -20°C to 50°C / -4°F to 122°F

- PoE 802.3at: -40°C to 50°C / -40°F to 122°F

        - Operating Humidity: 0% to 90%

        - Connectivity: Ethernet 10/100Mbps RJ-45 cable connector for Network/PoE connection

        - Regulatory Compliance:

- Meets the FIPS 140-2 standard, as certified by NIST

- TAA and FY2019 NDAA compliant

      - CF83-E-F Fisheye Camera by OEM Inc.

        - Onboard Storage: 512GB to 3TB based on 30-day retention at 24fps.

        - Sensor Resolution: 12.5MP (3536 x 3535 pixels)

        - Lens Type: Fixed Zoom

        - Image Sensor: 1/1.6” Progressive CMOS

        - Focal Length: 1.7mm

        - Iris: Fixed

        - Aperture: F2.0

        - Lens Distortion Correction (LDC): LDC crops the sensor field of view to deliver a rectified, undistorted output image.

        - Field of View after LDC:

- Horizontal: 180°

- Vertical: 180°

- Diagonal: 180°

        - IR Range: 20m / 66ft in low light

        - Audio: Yes

        - Resistance:

- IK10

- IP66/67

        - Dimensions

- With Mount Plate:

  - Length: 155mm / 6.1in

  - Width: 155mm / 6.1in

  - Height: 76.2mm / 3.0in

- Without Mount Plate:

  - Length: 155mm / 6.1in

  - Width: 155mm / 6.1in

  - Height: 69.2mm / 2.7in

        - Weight:

- With Mount Plate: 1564g / 75.1oz

- Without Mount Plate: 1368g / 48.2oz

        - Operating Power:

- With IR: IEEE 802.3at Type 2 PoE+

- Extended temperature range: IEEE802.3at Type 2 PoE+

        - Operating Temperature: -40°C to 50°C / -40°F to 122°F

        - Operating Humidity: 0% - 90%

        - Connectivity: Ethernet RJ-45 cable connector for network/PoE connection; 10/100/1000 Mbps

        - Regulatory Compliance:

- FIPS 140-2 validated

- TAA and FY2019 NDAA compliant

      - CH52-E-F Multisensor Camera by OEM Inc.

        - Onboard Storage: 1TB to 8TB based on 30-day retention at 24fps.

        - Sensor Resolution: 4 x 5MP (2688 x 1944 pixels)

        - Lens Type: Varifocal; motorized zoom

        - Image Sensor: 4 x 1 / 2.8” Progressive CMOS

        - Focal Length: 3.7-7.7mm

        - Iris: N/A

        - Aperture: F1.9 - F2.9

        - Sensor Movement:

- Tilt: +0°-105° for each lens from horizon

- Pan: +/- 90° for each lens

- Rotation: +/- 90° for each lens

        - Lens Distortion Correction (LDC): LDC crops the sensor field of view to deliver a rectified, undistorted output image.

        - Field of View (FoV after LDC):

- Horizontal: 37° to 89° (35° to 82°)

- Vertical: 29° to 65° (26° to 60°)

- Diagonal: 46° to 99° (43° to 92°)

        - IR Range: 30m / 98ft

        - Audio: Not supported

        - Resistance:

- FCC

- CE - EN55035

- IK10

- IP67

        - Dimensions

- With Mount Plate:

  - Length: 275mm / 10.83in

  - Width: 275mm / 10.83in

  - Height: 118mm / 4.65in

- Without Mount Plate:

  - Length: 267mm / 10.51in

  - Width: 267mm / 10.51in

  - Height: 114mm / 4.49in

        - Weight:

- With Mount Plate: 3436g / 121.2oz

- Without Mount Plate: 2900g / 102.29oz

        - Operating Power:

- With IR: IEEE 802.3bt Type 3 PoE++

- Without IR: IEEE 802.3at Type 2 PoE+

- Extended temperature range: IEEE 802.3bt Type 3 PoE++

        - Operating Temperature: -40°C to 50°C / -40°F to 122°F

        - Operating Humidity: 0% to 90%

        - Connectivity: Ethernet RJ-45 cable connector for network/PoE connection; 10/100 Mbps

        - Regulatory Compliance:

- FIPS 140-2 validated

- TAA and FY2019 NDAA compliant

      - CP52-E-F PTZ Camera by OEM Inc.

        - Onboard Storage: 512GB to 3TB based on 30-day retention at 24fps.

        - Sensor Resolution: 5MP (2688 x 1944 pixels)

        - Lens Type: Varifocal; motorized zoom

        - Image Sensor: 1/2.8” Progressive CMOS

        - Focal Length: 5.2-148.15mm

        - Iris: DC Iris

        - Aperture: F1.3 - F4.8

        - Lens Distortion Correction (LDC): LDC crops the sensor field of view to deliver a rectified, undistorted output image.

        - Field of View after LDC:

- Horizontal: 55°-2°

- Vertical: 42°-1.5°

- Diagonal: 66°-2.5°

        - IR Range: 100m / 328ft

        - Audio: Not supported

        - Resistance:

- IK10

- IP66

        - Dimensions

- With Pendant Cap:

  - Length: 256mm / 10.1in

  - Width: 256mm / 10.1in

  - Height: 406mm / 16in

- Without Pendant Cap:

  - Length: 256mm / 10.1in

  - Width: 256mm / 10.1in

  - Height: 336mm / 13.2in

        - Weight:

- With Pendant Cap: 8.01Kg / 16.5lbs

- Without Pendant Cap: 7.07kg / 15.6lbs

        - Operating Power:

- With IR: IEEE 802.3bt Type 3 PoE++

- Without IR: IEEE 802.3at Type 2 PoE+

- Extended temperature range: IEEE 802.3bt Type 3 PoE++

        - Operating Temperature: -40°C to 50°C / -40°F to 122°F

        - Operating Humidity: 0% - 90%

        - Connectivity: Ethernet RJ-45 cable connector for network/PoE connection; 10/100/1000 Mbps

        - Regulatory Compliance:

- FIPS 140-2 validated

- TAA and FY2019 NDAA compliant

      - CP63-E-F PTZ Camera by OEM Inc.

        - Onboard Storage: 1TB to 3TB based on 30-day retention at 24fps.

        - Sensor Resolution: 4K (3840 x 2160 pixels)

        - Lens Type: Varifocal; motorized zoom

        - Image Sensor: 1/1.8” Progressive CMOS

        - Focal Length: 6.5-212mm

        - Iris: P-Iris

        - Aperture: F1.4 - F4.9

        - Lens Distortion Correction (LDC): LDC crops the sensor field of view to deliver a rectified, undistorted output image.

        - Field of View after LDC:

- Horizontal: 63.5°-2°

- Vertical: 37.4°-1.1°

- Diagonal: 70.7°-2.3°

        - IR Range: 100m / 328ft

        - Audio: Not supported

        - Resistance:

- IK10

- IP66

        - Dimensions

- With Pendant Cap:

  - Length: 256mm / 10.1in

  - Width: 256mm / 10.1in

  - Height: 406mm / 16in

- Without Pendant Cap:

  - Length: 256mm / 10.1in

  - Width: 256mm / 10.1in

  - Height: 336mm / 13.2in

        - Weight:

- With Pendant Cap: 7940g / 280oz

- Without Pendant Cap: 7053g / 265.6oz

        - Operating Power:

- With IR: IEEE 802.3bt Type 3 PoE++

- Without IR: IEEE 802.3at Type 2 PoE+

- Extended temperature range: IEEE 802.3bt Type 3 PoE++

        - Operating Temperature: -40°C to 50°C / -40°F to 122°F

        - Operating Humidity: 0% - 90%

        - Connectivity: Ethernet RJ-45 cable connector for network/PoE connection; 10/100/1000 Mbps

        - Regulatory Compliance:

- FIPS 140-2 validated

- TAA and FY2019 NDAA compliant

  - COMMAND CONNECTOR

    - Command Connector by OEM Inc.

      - Description:

        - The Command Connector allows adding non-OEM cameras to Command.

        - Supports many features on native OEM cameras, including video analytics, easy remote administration, simplified retention, and a single management platform.

        - ONVIF Profile S conformant and can ingest RTSP feeds.

      - Key Features:

        - Support for recording and playback ranging from 5MP (or less) to 4K resolutions

        - RAID10 for high reliability

        - People and vehicle analytics

        - AI-powered search

        - 5-year warranty

      - Storage and video recording:

        - 4TB-32TB of onboard storage

        - 30-90 days of continuous video recording per channel

        - Adaptive quality recording automatically triggers HQ recording when motion is detected

      - Technical Specifications:

        - CPU: Inteli9-13900K

        - Power Input: Single PSU 600W

        - Power Input Voltage: 90-264VAC

        - Power Input Frequency: 47-63Hz

        - Connectivity: Dual 2.5Gbps RJ45 Ethernet

        - Memory: 32GB RAM

        - Dimensions:

          - Width:18.87in / 479.4mm

          - Height: 1.73in / 44mm

          - Depth: 22.13in / 562.1mm

        - Operating Temperature: 0° to 40° C / 32°F to 104°F

        - Storage Temperature: -20° to 70° C / -4°F to 158°F

        - Operating Humidity: 0%-90% (non-condensing)

        - System Rack Size: 1U

        - Storage:

          - CC300: 4TB-8TB

          - CC500: 8TB-16TB

          - CC700: 16TB-32TB

        - Certifications:

          - FCC Class A

          - NDAA compliant

          - ICES

  - VIEWING STATION

    - VX52 Video Surveillance Viewing Station by OEM Inc.

      - Description:

        - The VX52 is a dedicated device that streams up to 300 camera feeds (30 cameras per page, up to 10 pages) to any display with ultra-low latency, crisp video playback, customizable Smart Tiles and layouts. Built on the powerful Apple TV 4K platform, the VX52 is the viewing platform of choice for customers with mission-critical real-time viewing requirements.

        - Administrator Managed Device – Admins can remotely manage the VX52, select video feeds and Smart Tiles to display as well as customize layouts. Non-admin viewers do not need accounts, cannot access historical footage, and cannot modify display settings.

        - Plug-and-Play by Design – Simply connect the device to your network via ethernet or WiFi and project on a display. The VX52 is ready to stream in minutes with zero configuration needed.

        - Stable and Resilient – Streams play continuously without interruption for both local and remote streaming. There is no need to reset the device or relaunch a browser or application, streams restart automatically after a power outage.

        - Supported by OEM – Admins configure the VX52 in Command, just like their cameras. The VX52 is backed by our industry-leading 10-year warranty and the dedicated OEM customer support team.

      - Key Features:

        - Stream up to 300 cameras across 10 pages on a single display

          - Ultra-low latency with crisp video playback

          - Administrator managed device without requiring additional accounts

          - Plug-and-play with zero local configuration needed

          - Easily configure Smart Tiles and layout display from Command

          - Automatically restarts after a power outage

          - 10-year warranty

    - Technical Specifications:

- Supported Displays: One display per station

- Number of Streams:

  - 30 streams per page

  - 300 streams total

- Processor: A12 Bionic chip

- Dimensions:

  - Length: 99.1mm / 3.9in

  - Width: 99.1mm / 3.9in

  - Height: 35.6mm / 1.4in

- Weight: Weight: 425g / 15oz

- Operating Temperature: 0° to 35° C / 32°F to 95°F

- Operating Humidity: 0% to 95%

- Operating Altitude: Up to 3,000m / 10,000ft

- Display Resolution Supported: Up to 4096 x 2160 pixels

- Included accessories:

  - HDMI cord

  - setup guide

  - power cord

  - Apple TV remote

- Connectors:

- HDMI 2.1 port

- Gigabit Ethernet

- Connectivity: 10/100/1000BASE-T Gigabit Ethernet (RJ-45), 802.11 ax WiFi 6

  - POE INJECTORS

    - INJ-POE-PLUS Power over Ethernet+ Injector by OEM Inc.

      - Description: OEM’s INJ-POE-PLUS is a single port, high-power solution for remote powering of PoE enabled hardware, including OEM security cameras, access control, and environmental sensors. Generating up to 30W, the INJ-POE-PLUS enables remote power for a new range of applications including 802.11n Access Points and

pan-tilt-zoom (PTZ) cameras. It complies to IEEE 802.3at PoE standard and is backward compatible to IEEE802.3af. It can power both existing 10/100Base-T network devices and emerging wireless 1000Base-T devices such as WiMAX and wireless IEEE 802.11n access points.

      - Key Features:

        - IEEE 802.3at compliant with 2-event classification

        - IEEE 802.3af backward compatible

        - Output power of 30W is guaranteed

        - Supports 10/100/1000Base-T applications

        - Compatible with IEEE 802.3af devices

        - Safe – low power devices receive only the power they need

        - Automatic Detection and Protection of non-standard Ethernet terminals

        - Compact design fits easily in WLAN Access Point and IP Cameras installations

      - Technical Specifications

        - Data Rates: 10/100/1000 Mbps

        - Power over Ethernet Output:

        - Pin Assignment and Polarity: Spare Pairs 7/8 (-) and 4/5 (+)

        - Output Power Voltage: 55 VDC

        - User Port Power: 30W (Guaranteed)

        - Input Power Requirements:

          - AC Input Voltage: 100VAC to 240VAC (±10%)

          - AC Input Current: 0.67A @ 100VAC to 240VAC

          - AC Frequency: 50 to 60Hz

        - Dimensions:

          - Length: 160.5mm / 6.32in

          - Width: 51.8mm / 2.04in

          - Height: 34.8mm / 1.37in

        - Weight: 200g / 7.05oz

        - Connectors:

          - Shielded RJ-45

          - EIA 568A

          - EIA 568B

        - Environmental Conditions:

          - Operating Ambient Temperature:

            - -4°F to 104°F (-20 °C to 40°C) @30W

            - -4°F to 131°F (-20 °C to 55°C) @22.5W

        - Operating Humidity: 0% to 90%

        - Operating Altitude: -304.8m to 3,048m / -1,000ft to 10,000 ft

        - MTBF: 100,000 hrs @ 25°C

        - Thermal Rating: 20 BTU/Hr (@240VAC)

        - Regulatory Compliance:

          - IEEE 802.3af (PoE)

          - RoHS Compliant

          - WEEE Compliant

          - CE

        - Electromagnetic Emission and Immunity:

          - FCC Part 15, Class B

          - EN 55032 Class B (Emissions)

          - EN 55024 (Immunity)

          - VCCI

        - Safety: UL/EN/IEC 60950-1 (Ed.2)

    - ACC-POE-60W Power over Ethernet++ Injector by OEM Inc.

      - Description: OEM’s ACC-POE-60W converts two inputs – a power cable and an Ethernet cable – to a single PoE ++ port (IEEE 802.3bt standard, type 3 compliant) with up to 60W of power. The ACC-POE-60W is designed to power the CH52-E Multisensor camera, but it is also backwards compatible and safe to use with any IEEE 802.3af/at terminals in other OEM devices. The ACC-POE-60W comes with a US power cord (for US customers) and a UK power cord (for Europe customers) and is wall mountable.

      - Key Features

        - IEEE 802.bt Type 3 compliant

        - IEEE 802.3af/at backward compatible

        - Output power of 60W over 4–pairs

        - Supports 10/100/1000 Base–T applications

        - Safe: low–power devices receive only the power they need

        - Automatic detection and protection of non–standard Ethernet terminals

        - Compact design fits easily in WLAN access point and IP camera installations

      - Technical Specifications

        - Data Rates: 10/100/1000 Mbps

        - Power over Ethernet Output:

          - Data Pairs:

1) 1/2 (-)

2) 3/6 (+)

          - Spare Pairs:

1) 7/8 (-)

2) 4/5 (+)

        - Output Voltage: 55 V nominal

        - Output Power Voltage: 55 VDC

        - User Port Power: 30W (Guaranteed)

        - Input Power Requirements:

          - AC Input Voltage: 100 to 240V

          - AC Input Current: 1.5A

          - AC Frequency: 50 / 60Hz

        - Dimensions:

          - Length: 151mm / 5.94in

          - Width: 62mm / 2.44in

          - Height: 38mm / 1.5in

        - Weight: 500g / 17.64oz

        - Connectors:

          - Shielded RJ-45

          - EIA 568A

          - EIA 568B

        - Environmental Conditions:

          - Operating Ambient Temperature:

            - -20°C to 40°C / 14°F to 104°F @ 60W

            - -20°C to 55°C / 14°F to 131°F @ 30W

        - Operating Humidity: 0% to 90%

        - Operating Altitude: -400m to 3,048m / -1,312ft to 10,000 ft

        - MTBF: 240,000 hrs @ 25°C

        - Thermal Rating: 34 BTU/Hr

        - Regulatory Compliance: IEEE 802.3bt

        - Electromagnetic Emission and Immunity:

          - FCC Part 15, Class B

          - EN 55032 Class B

          - EN 55024

          - VCCI

        - Safety: CE/UL/IEC/EN 62368-1

  - ACCESSORIES

    - ACC-MNT-2 Mounting Arm Kit by OEM Inc.

      - Description: Wall mounted extender arm with built-in 1.5” female NPT thread.

      - Material: Aluminum Alloy

      - Dimensions:

        - Length: 230.5mm / 9.07in

        - Width: 86mm / 3.39in

        - Height: 117mm / 4.61in

      - Color: White

      - Weight: 700g / 24.69oz

    - ACC-MNT-3 Wall Mounted L-Shaped Bracket Kit by OEM Inc.

      - Description: Compact bracket for mounting camera perpendicular to wall.

      - Material: Aluminum Alloy

      - Dimensions:

b. Width: 150mm / 5.91in

c. Height: 110mm / 4.33in

      - Color: White

      - Weight: 577g / 20.35oz

    - ACC-MNT-5 Mini Pendant Cap Mount Kit by OEM Inc.

      - Description: Two-piece threaded cap for mounting a Mini camera to 3/4” NPT threaded drop pipe. Cap piece can be removed and mounted independently with its 1.5” male NPT thread.

      - Material: Aluminum Alloy

      - Dimensions:

        - Length: 100mm / 3.94in

        - Width: 100mm / 3.94in

        - Height: 102.8mm / 4.05in

      - Color: Dark grey

      - Weight: 240g / 8.47oz

      - Included Accessories:

        - Fasteners

        - Set screw

        - Hex key

    - ACC-MNT-6 Mini Camera Junction Box Mount Adapter by OEM Inc.

      - Description: For mounting a Mini camera to a standard junction box.

      - Material: Steel Mount Plate, Plastic Cover

      - Dimensions:

        - Length: 130mm / 5.12in

        - Width: 130mm / 5.12in

        - Height: 7.5mm / 0.3in

      - Color: Grey Mount Plate, White Plastic Cover

      - Weight: 160g / 5.64oz

      - Included Accessories:

        - Fasteners

    - ACC-MNT-7 Angle Mount by OEM Inc.

      - Description: Mounts fisheye and dome cameras 30° from wall for improved field of view.

      - Material: Aluminum Alloy

      - Dimensions:

b. Width: 149mm / 5.87in

c. Height: 82mm / 3.23in

      - Color: White

      - Weight: 390g / 13.76oz

      - Included Accessories:

        - Metal mount ring

        - 3x countersink screws

        - 3x thumbscrews

        - Rubber plug

    - ACC-MNT-8 Pendant Cap Mounting Adapter Kit by OEM Inc.

      - Description: Threaded cap adapter enables mounting of Indoor Dome Series, Outdoor Dome Series, Fisheye Series, and Multisensor Series cameras to hardware with 3/4” female NPT and 1.5” male NPT threads, including ACC-MNT-2 Mounting Arm Kit by OEM Inc.

      - Material: Aluminum Alloy

      - Dimensions:

        - Length: 155mm / 6.1in

        - Width: 155mm / 6.1in

        - Height: 42mm / 1.65in

      - Color: White

      - Weight: 300g / 10.58oz

      - Included Accessories:

        - Set screw

        - 3x thumbscrews.

    - ACC-MNT-9 Pole Mount Adapter by OEM Inc.

      - Description: For mounting a camera to a circular pole.

      - Mounting Pole Diameter: 32mm to 152.4mm / 1.25in to 6in

      - Material: Steel

      - Dimensions:

        - Length: 160mm / 6.3in

        - Width: 160mm / 6.3in

        - Height: 68mm / 2.68in

      - Color: White

      - Weight: 742g / 26.17oz

      - Included Accessories:

        - Adapter plate

        - 2x Metal strap set

        - Fasteners for compatible mounts

    - ACC-MNT-10 Corner Mount by OEM Inc.

      - Description: Versatile bracket for mounting a range of accessories and cameras on corners.

      - Material: Steel

      - Dimensions:

        - Length: 190mm / 7.48in

        - Width: 263mm / 10.35in

        - Height: 170mm / 6.69in

      - Color: White

      - Weight: 1,890g / 66.67oz

    - ACC-MNT-11 Square Junction Box

      - Description: Square junction box for mounting Bullet Series cameras.

      - Material: Aluminum alloy

      - Dimensions:

        - Length: 128mm / 5.04in

        - Width: 128mm / 5.04in

        - Height: 40mm / 1.57in

      - Color: White

      - Weight: 303g / 10.69oz

      - Included Accessories:

        - 2x ¾in NPT plugs

        - 4x buttonhead screws

    - ACC-CAM-SHIELD-1

      - Description: Weather shield for protecting Dome Series and Fisheye Series cameras.

      - Material: Steel mount plate, polycarbonate visor

      - Dimensions:

        - Length: 192mm / 7.56in

        - Width: 185mm / 7.28in

        - Height: 78mm / 3.07in

      - Color:

        - Black mount plate

        - White and black visor

      - Weight: 173g / 6.1oz

      - Included Accessories:

        - Mounting fasteners

  - CELLULAR GATEWAYS

    - GC31 Indoor Cellular Gateway

      - Description:

        - Indoor cellular gateway to send both power and data to any OEM device via PoE.

        - Flexible power options.

        - OEM data plan or BYO plan.

        - Cloud-managed in OEM Command.

      - Technical Specifications:

        - Cellular:

          - Connectivity: LTE cellular CAT 12

          - SIM: 2 SIM slots (Nano 4FF), dual SIM/auto SIM failover

          - Antennas: 2 x SMA

        - Inputs and Outputs:

          - Ethernet: 2 x GigE RJ45 outputs

          - Power Input: 54VDC Barrel Jack (6.5/3.55mm OD/ID), 100-240VAC AC/DC power adaptor included (region specific)

          - Power Output: 2 x PoE RJ45 outputs @ 60W total (2 x IEEE 802.3at Type 2 PoE+ 30W or 1 x IEEE 802.3bt Type 3 PoE++ 60W)

        - Dimensions:

          - Length: 125mm / 4.9in

          - Width: 125mm / 4.9in

          - Height: 30mm / 1.2in

        - Weight: 0.6kg / 1.3lb

        - Operating Temperature: -10°C to 50°C / 14°F to 122°F

        - Operating Humidity: 5% to 90%

        - Compliance:

          - FCC

          - CE

          - IC

          - UL/IEC 62368-1

          - CSA C22.2 No. 62368-1

          - PTCRB

          - Verizon

          - AT&T

          - FirstNet

        - Included Accessories:

          - 2 x SMA antennas

          - AC/DC power adapter and cord

          - Mounting Hardware: Mounting plate, 4 x wall anchors, T10 security torx screwdriver, 4 M4 x 25mm PH2 wall screws, RJ45 port cover

    - GC31-E Outdoor Cellular Gateway

      - Description:

        - Outdoor cellular gateway to send both power and data to any OEM device via PoE.

        - Flexible power options.

        - OEM data plan or BYO plan.

        - Cloud-managed in OEM Command.

      - Technical Specifications:

        - Cellular:

          - Connectivity: LTE cellular CAT 12

          - SIM: 2 SIM slots (Nano 4FF), dual SIM/auto SIM failover

          - Antennas: 2 x N Type

        - Inputs and Outputs:

          - Ethernet: 1 x GigE RJ45 input, 2 x GigE RJ45 outputs

          - Power Input: 54VDC Barrel Jack (6.5/3mm OD/ID), IEEE 802.3bt Type 4 PoE++ 90W, 12-36VDC Terminal Block

          - Power Output: 2 x PoE RJ45 outputs @ 60W total (2 x IEEE 802.3at Type 2 PoE+ 30W or 1 x IEEE 802.3bt Type 3 PoE++ 60W)

        - Dimensions:

          - Length: 243mm / 9.6in

          - Width: 148mm / 5.9in

          - Height: 33mm / 1.3in

        - Weight: 1.4kg / 3.0lb

        - Operating Temperature: -40°C to 50°C / -40°F to 122°F

        - Operating Humidity: 5% to 90%

        - Compliance:

          - FCC

          - CE

          - IC

          - UL/IEC 62368-1

          - CSA C22.2 No. 62368-1

          - PTCRB

          - Verizon

          - AT&T

          - FirstNet

          - IP66

        - Included Accessories:

          - 2 x N type antennas

          - Mounting Hardware: Mounting plate, 2 x pole straps, 4 x wall anchors, 4 x wall screws, T10 security torx screwdriver, 4 x 7-9 mm cable grommets, 1 x 3-5mm cable grommet, 1 x 3-wire cable grommet

  - WIFI GATEWAYS

    - GW31-E Outdoor Cellular Gateway

      - Description:

        - Outdoor Wi-Fi gateway to provide to send both power and data to any OEM devices.

        - Flexible power options (AC receptacles, solar/batteries, light poles).

        - Built-in PoE switch.

        - Cloud-managed in OEM Command.

      - Technical Specifications:

        - Connectivity:

          - Wi-Fi Standards: 802.11a/b/g/n/ac/ax (Wi-Fi 6); 2.4 or 5 GHz (single radio)

          - Wi-Fi Security: WPA2/3 PSK; WPA2/3 Enterprise

          - Wi-Fi Operating Mode: Client/STA

          - Wi-Fi Antennas: 2 x external omni (N-type male); ACC-ANT-20 Directional Antenna also available

          - Networking Interface: 3 x GigE RJ45 ports (2 x LAN and 1 x WAN/LAN configurable)

        - Power:

          - Power Consumption: 9W above -25°C / -13°F; 19W below -25°C /

-13°F (does not include connected devices)

          - Power Input: 54V DC Barrel Jack (6.5/3.0mm OD/ID); 802.3bt Type 4 PoE 90W; 12-36V DC Terminal Block

          - Power Output: 2 x 802.3bt PoE++ capable ports; 60W total power budget

        - Dimensions:

          - Length: 243mm / 9.6in

          - Width: 148mm / 5.9in

          - Height: 33mm / 1.3in

        - Weight: 1.4kg / 3.0lb

        - Operating Temperature: -40°C to 50°C / -40°F to 122°F

        - Operating Humidity: 5% to 90%

        - Compliance:

          - FCC

          - CE

          - IC

          - UKCA

          - RCM

          - MIC

          - UL/IEC 62368-1

          - CSA C22.2 No. 62368-1

          - IP66

        - Included Accessories:

          - 2 x N type antennas

          - Mounting Hardware: Mounting plate, 2 x pole straps, 4 x wall anchors, 4 x wall screws, T10 security torx screwdriver, 4 x 7-9 mm cable grommets, 1 x 3-5mm cable grommet, 1 x 3-wire cable grommet

  - VIDEO DISPLAY EQUIPMENT

    - Video Display Equipment – Two (2) desk mount and one (1) 55 inch wall mount monitors per workstation. All monitors to be 4K capable and rated for 24 hour operation.

      - Will consist of color monitors and shall be EIA 375A compliant.

      - Shall be able to display analog, digital, and other images in either NTSC or MPEG format associated with the operation of the Security Management System (SMS).

      - Shall:

        - Have front panel controls that provide for power on/off, horizontal and vertical hold, brightness, and contrast.

        - Accept multiple inputs, either directly or indirectly.

        - Have the capabilities to observe and program the VASS System.

        - Be installed in a manner that they cannot be witnessed by the general public.

    - Color Video Monitors Technical Characteristics:

| Sync Format | PAL/NTSC |
| --- | --- |
| Display Tube | 90° deflection angle |
| Horizontal Resolution | 250 TVL minimum, 300 TVL typical |
| Video Input | 1.0 Vp-p, 75 Ohm |
| Front Panel Controls | Volume, Contrast, Brightness, Color |
| Connectors | BNC |

    - Liquid Crystal Display (LCD) Flat Panel Display Monitor – Desk Mount

    - The 24-inch color LCD monitor shall have a flat screen and 24-inch diagonal viewing area and consists of an LCD panel, bezel, and stand.

    - The monitor shall meet or exceed the following specifications:

      - The monitor shall incorporate a 24 -inch active matrix TFT LCD panel.

        - The pixel pitch of the monitor’s LCD panel shall be 0.264 mm horizontal and 0.264 mm vertical.

        - The monitor shall have a maximum resolution of <500> television lines.

        - The contrast ratio shall be 500:1.

        - The typical brightness shall be 250 cd/m²

        - The monitor shall display at least 16.7 million colors.

        - The light source for the LCD panel shall have a lifetime of 50,000 hours.

        - The scan frequency horizontal shall be 30 K to 80 KHz and the scan frequency vertical shall be 56 to 75 Hz.

        - The viewing angle for the monitor shall be 170 degrees horizontal and 170 degrees vertical.

      - The monitor shall have automatic NTSC or PAL recognition.

      - The monitor shall have a picture-in-picture function.

      - The monitor shall use the following signal connectors:

        - Video 1.0 V peak-to-peak at 75 ohms

- Y/C (S-video) in/out

- Audio in/out

- VGA 15-pin D-Sub

- HDMI

      - The monitor shall have two <2> audio speaker(s).

        - The speaker shall be 0.5 W minimum.

      - The monitor shall have the following front control panel buttons:

        - Power on/off

        - LED indicator

        - Mode

        - Increase (volume)

        - Decrease (volume)

        - Up (contrast adjustment)

        - Down (brightness adjustment)

        - Menu

        - Auto

      - The monitor shall have the following options for adjustment in an onscreen display menu:

        - Color

        - Tint

- NTSC mode only

  - Brightness

  - Contrast

  - Sharpness

  - Volume

  - Language

  - Scan

  - Color Temp

  - H-Position

  - Recall

    - The electrical specifications for the monitor shall be as follows:

      - Input voltage shall be 12 VDC/3 A.

      - Power consumption shall be 50 W maximum.

    - The environmental specifications for the monitor shall be as follows:

      - Operating temperature shall be 32 to 104 degrees Fahrenheit or 0 to

40 degrees Celsius.

      - Operating humidity shall be 10 to 85 percent.

    - The physical specifications for the monitor shall be as follows:

    - The monitor shall conform to these compliance standards:

      - FCC

      - CE (EMC/LVD)3. UL

  - CONTROLLING EQUIPMENT

    - Shall be utilized to call up, operate, and program all cameras associated VASS System components.

    - Will have the ability to operate the cameras locally and remotely..

D. Control and programming keyboards shall be provided with its own type of switcher. All keyboards shall:

- Be located at each monitoring station.

- Be addressable for programming purposes.

- Provide interface between the operator and the VASS System.

- Provide full control and programming of the switcher.

- Have the minimum following controls:

  - programming

  - switching

  - lens function

  - P/T/Z

  - environmental housing

  - annotation

  - WIRES AND CABLES

    - Shall meet or exceed the manufactures recommendation for power and signal.

    - Will be carried in an enclosed conduit system, utilizing electromagnetic tubing (EMT) to include the equivalent in flexible metal, rigid galvanized steel (RGS) to include the equivalent of liquid tight, polyvinylchloride (PVC) schedule 40 or 80.

    - All conduits will be sized and installed per the NEC. All security system signal and power cables that traverse or originate in a high security office space will be contained in either EMT or RGS conduit.

    - All conduit, pull boxes, and junction boxes shall be clearly marked with colored permanent tape or paint that will allow it to be distinguished from all other conduit and infrastructure.

    - Conduit fills shall not exceed 50 percent unless otherwise documented.

    - A pull string shall be pulled along and provided with signal and power cables to assist in future installations.

    - At all locations where there is a wall penetration or core drilling is conducted to allow for conduit to be installed, fire stopping materials shall be applied to that area

    - High voltage and signal cables shall not share the same conduit and shall be kept separate up to the point of connection. High voltage for the security system shall be defined as any cable or sets of cables carrying 30 VDC/VAC or higher.

    - For all equipment that is carrying digital data between the Physical Access Control System and Database Management or at a remote monitoring station, shall not be less than 20 AWG and stranded copper wire for each conductor. The cable or each individual conductor within the cable shall have a shield that provides 100% coverage. Cables with a single overall shield shall have a tinned copper shield drain wire.

    - All cables and conductors, except fiber optic cables, which act as a control, communication, or signal lines shall include surge protection. Surge protection shall be furnished at the equipment end and additional triple electrode gas surge protectors rated for the application on each wire line circuit shall be installed within 1 m. (3 ft.) of the building cable entrance. The inputs and outputs shall be tested in both normal and common mode using the following wave forms:

      - A 10 microsecond rise time by 1000 microsecond pulse width waveform with a peak voltage of 1500 watts and peak current of 60 amperes.

      - An 8 microsecond rise time by 20 microsecond pulse width wave form with a peak voltage of 1000 volts and peak current of 500 amperes.

    - The surge suppression device shall not attenuate or reduce the video or sync signal under normal conditions. Fuses and relays shall not be used as a means of surge protection.

      - Signal Cables:

a. Refer to Division 27 and Section 280513 Conductors and Cables for Electronic Safety and Security Systems. Signal wiring for PoE cameras depends on the distance the camera is being installed from either a hub or the server.

PART 3 - EXECUTION

3.1. GENERAL

- Installation: The Contractor shall install all system components including Owner furnished equipment, and appurtenances in accordance

with the manufacturer’s instructions, ANSI C2 and as shown, and shall furnish all necessary connectors, terminators, interconnections, services, and adjustments required for a complete and operable data transmission system.

  - Installers: Installation shall be performed by technicians that have successfully completed the OEM Certified Engineer (VCE) program. For more information, visit www.OEM.com/partners/trainings.

- Identification and Labeling: The Contractor shall supply permanent identification labels for each cable at each end that will appear on the as-built drawings. The labeling format shall be identified and a complete record shall be provided to the Owner with the final documentation. Each cable shall be identified by type or signal being carried and termination points. The labels shall be printed on letter size label sheets that are self-laminated vinyl that can be printed from a computer data base or spread sheet. The labels shall be E-Z code WES12112 or equivalent.

  - The Contractor shall provide all personnel, equipment, instrumentation, and supplies necessary to perform all testing.

- Transient Voltage Surge Suppressors (TVSS): The Contractor shall mount TVSS within 3 m (118 in) of equipment to be protected inside terminal cabinets or suitable NEMA 1 enclosure. Terminate off-premise conductors on input side of device. Connect the output side of the device to the equipment to be protected. Connect ground lug to a low impedance earth ground (less than 10 ohms) via Number 12 AWG insulated, stranded copper conductor.

- Contractor’s Field Test: The Contractor shall verify the complete operation of the data transmission system during the Contractor’s Field Testing. Field test shall include a bit error rate test. The Contractor shall perform the test by sending a minimum of 1,000,000 bits of data on each DTM circuit and measuring the bit error rate. The bit error rate shall not be greater than one (1) bit out of each 100,000 bits sent for each dial-up DTM circuit, and one (1) bit out of 1,000,000 bits sent for each leased or private DTM circuit. The Contractor shall submit a report containing results of the field test.

- Acceptance Test and Endurance Test: The wire line data transmission system shall be tested as a part of the completed IDS and EECS during the Acceptance test and Endurance Test as specified.

- Identification and Labeling: The Contractor shall supply identification tags or labels for each cable. Cable shall be labeled at both end points and at intermediate hand holes, manholes, and junction boxes. The labeling format shall be identified and a complete record shall be provided to the Owner with the final documentation. Each cable shall be identified with type of signal being carried and termination points.

  - EXAMINATION

    - Installation surfaces shall be clean and free from dust, dirt, and obstructions.

    - Examine pathway elements intended for cables. Check raceways, cable trays, and other elements for compliance with space allocations, installation tolerances, hazards to cable installation, and other conditions affecting installation.

    - Examine rough-in for LAN and control cable conduit systems to PCs, controllers, cameras, and other cable-connected devices to verify actual locations of conduit and back boxes before device installation.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - PREPARATION

    - Refer to the OEM Quick Start Guide applicable to each product.

    - Pre-Installation Conference: Prior to installation arrange conference between supplier, Owner, and related trades to review materials, procedures, and coordinating related work.

    - Furnish or coordinate any inserts required for building into concrete, masonry, and other work, to support and attach work of this Section. Furnish or coordinate in ample time to comply with schedule of work into which inserts are built.

    - Verify that power and outlets are in correct locations.

    - Verify that building structure is properly prepared for mounting, attachment, and support of equipment.

    - Prior to installation of systems components and devices, verify all required preparations have been properly performed and that substrates are acceptable for installation.

      - Verify all rough-ins and field dimensions.

    - Report in writing to the Owner’s representative any prevailing conditions that will adversely affect satisfactory execution of work in this Section.

      - Owner or their representative reserves the right to review proposed methods of construction and installation, reject proposed methods, and have the installation done in a satisfactory method at the Contractor's cost.

  - INSTALLATION

    - System installation shall be in accordance with NECA 303, manufacturer and related documents and references, for each type of security subsystem designed, engineered and installed.

    - Components shall be configured with appropriate “service points” to pinpoint system trouble in less than 30 minutes.

    - The Contractor shall install all system components including Government furnished equipment, and appurtenances in accordance with the manufacturer's instructions, documentation, and shall furnish all necessary connectors, terminators, interconnections, services, and adjustments required for a complete and operable system.

    - The VASS System will be designed, engineered, installed, and tested to ensure all components are fully compatible as a system and can be integrated with all associated security subsystems, whether the system is a stand-alone or a complete network.

    - Sequencing: The work shall be performed in the following sequence, unless directed otherwise by Owner or their representative:

      - Installation of cables and network.

      - Installation of new cameras.

      - Installation of front-end equipment.

      - Commissioning of the new system components.

      - End User training

    - Install work in accordance with manufacturer's recommendations and instructions as well as final shop drawings. All components should be installed so as to allow easy access for service in the future.

    - Anchor components securely in place, plumb, level, and accurately aligned.

    - For solution products located in equipment traffic areas, and that are exposed to damage due to collision or impact from forklifts, or

manually moved carts, carriers, or other equipment used by the Owner, provide protective bollards, railings, coverings etc. to ensure that all products installed are properly protected from such damage.

    - Provide fastenings, plates, and other incidental items required for complete and operational installation.

    - Provide required electrical work in accordance with Code requirements.

    - Security and protection:

      - Maintain strict security during the installation of equipment and software. Rooms housing the control station, and workstations that have been powered up shall be locked and secured during periods when a qualified operator in the employ of Contractor is not present.

      - Equipment protection: Provide protective covers, fenders, and barriers as necessary to maintain work of this Section in same condition as installed until time of substantial completion.

    - Cable requirements:

      - Twisted, non-shielded, plenum-rated type cable shall be used except as clarified herein.

      - All exposed cables shall be installed in rigid conduit pathways approved by the Owner. Exposed cabling installed in interior locations shall use electric metallic tubing (EMT). Exposed cabling installed in exterior locations shall use rigid steel conduit (RGS) or intermediate metallic conduit (IMC) as specified herein.

      - All concealed cables routed in j-hook pathways shall be fastened to the structure at least every four feet.

    - Labeling

      - Equipment and product labels shall be printed on self-adhesive labels. Handwritten labels or writing directly on the equipment enclosures is not acceptable.

      - Label equipment and products with the device address as programmed into the security systems and as reflected on the “As-Built” Record Drawings. Coordinate campus nomenclature with VA OIT and VA Security personnel.

      - Label networked equipment enclosures with the IP address as coordinated with VA OIT.

      - Cables shall be individually labeled at origin and termination.

    - Programming

      - Complete all OEM Command configuration programming.

      - Add all OEM Cameras to Command via serial number.

      - Contract will coordinate with the Owner to ensure that new components have appropriate network connections.

      - Coordinate with the Owner to ensure that new components will be properly programmed into the system.

      - Change default passwords to new custom secure passwords as directed by the Owner.

Control System and Database Management of an alarm event.

    - Integration with these security subsystems shall be achieved by computer programming or the direct hardwiring of the systems.

    - For programming purposes refer to the manufacturers requirements for correct system operations. Ensure computers being utilized for system integration meet or exceed the minimum system requirements outlined on the systems software packages.

    - A complete VASS System shall be comprised of, but not limited to, the following components:

      - Cameras

      - Lenses

      - Video Display Equipment – Desk and Wall Mounted Monitors with support bracket

      - Camera Housings and Mounts

      - Controlling Equipment

      - Client workstation requirements

      - Local Uninterruptible Power Supply (UPS)

      - Wiring and Cables

    - The Contractor shall visit the site and verify that site conditions are in agreement/compliance with the design package. The Contractor shall report all changes to the site or conditions that will affect performance of the system to the Contracting Officer in the form of a report. The Contractor shall not take any corrective action without written permission received from the Contracting Officer.

    - Existing Equipment

      - The Contractor shall retain and remove existing video equipment, video and control signal transmission lines, and devices as outlined in the design package once the new VAAS system is tested and operational.

      - The Contractor shall make written requests and obtain approval prior to disconnecting any signal lines and equipment and creating equipment downtime. Such work shall proceed only after receiving Contracting Officer approval of these requests. If any device fails after the Contractor has commenced work on that device, signal or control line, the Contractor shall diagnose the failure and perform any necessary corrections to the equipment.

      - The Contractor shall be held responsible for repair costs due to Contractor negligence, abuse, or incorrect installation of equipment.

      - The Contracting Officer shall be provided a full list of all equipment that is to be removed or replaced by the Contractor, to include description and serial/manufacturer numbers where possible. The Contractor shall dispose of all equipment that has been removed or replaced based upon approval of the Contracting Officer after reviewing the equipment removal list. In all areas where equipment is removed or replaced the Contractor shall repair those areas to match the current existing conditions.

    - Enclosure Penetrations: All enclosure penetrations shall be from the bottom of the enclosure unless the system design requires penetrations from other directions. Penetrations of interior enclosures involving transitions of conduit from interior to exterior, and all penetrations on exterior enclosures shall be sealed with rubber silicone sealant to preclude the entry of water and will comply with VA Master Specification 07 84 00, Firestopping. The conduit riser shall terminate in a hot-dipped galvanized metal cable terminator. The terminator shall be filled with an approved sealant as recommended by the cable manufacturer and in such a manner that the cable is not damaged.

    - Cold Galvanizing: All field welds and brazing on factory galvanized boxes, enclosures, and conduits shall be coated with a cold galvanized paint containing at least 95 percent zinc by weight.

    - Interconnection of Console Video Equipment: The Contractor shall connect signal paths between video equipment as specified by the OEM. Cables shall be as short as practicable for each signal path without causing strain at the connectors. Rack mounted equipment on slide mounts shall have cables of sufficient length to allow full extension of the slide rails from the rack.

    - Cameras:

      - Install the cameras with the focal length lens as indicated for each zone.

      - Connect low voltage lines to the camera.

      - Aim camera to give field of view as needed to cover the alarm zone.

      - Aim fixed mounted cameras installed outdoors facing the rising or setting sun sufficiently below the horizon to preclude the camera looking directly at the sun.

      - Focus the lens (lenses for multilens cameras) to give a sharp picture (to include checking for day and night focus and image quality) over the entire field of view

      - Synchronize all cameras so the picture does not roll on the monitor when cameras are selected.

      - PTZ cameras shall have all preset positions and privacy areas defined and programmed.

      - Coordinate final aiming of each camera with the contracting officer and VA security personnel.

    - Monitors:

      - Install the monitors as shown and specified in design and construction documents.

      - Connect all signal inputs and outputs as shown and specified.

      - Terminate video input signals as required.

      - Connect the monitor to AC power.

    - Software:

      - Install the software onto Government furnished PCs as shown in the design and construction documents, and according to the OEM.

      - Connect all subassemblies for the PC (keyboard, mouse, monitors) as specified by the manufacturer and as shown.

      - Connect video signal inputs and outputs as shown and specified; terminate video inputs as required.

      - Connect alarm signal inputs and outputs as shown and specified; connect control signal inputs and outputs for ancillary equipment or secondary control/monitoring sites as specified by the manufacturer and as shown.

      - Connect the PC workstation to AC power via local UPS unit.

      - Load all software as specified and required for an operational VASS System configured for the site and building requirements, including

data bases, operational parameters, and system, command, and application programs.

      - Provide the original and 2 backup copies for all accepted software upon successful completion of the endurance test.

      - Program the video annotation for each camera.

    - Video Workstation:

      - Install the video workstation per design and construction documents, and as specified by the OEM.

      - Connect video workstation to AC power via local UPS.

      - Connect to VASS network as directed by VA OIT.

      - Install operating system and application software.

      - Provide application software programming per VA guidance and the requirements provided by the Owner. Programming shall include:

        - Screen views

        - Graphical User Interface (GUI) maps, views, icons and actions

        - Alarm outputs

        - Reports

    - Network Switch (Provided by VA OIT):

      - Network switches to support the VASS system shall be provided by VA OIT within the existing TR rooms located throughout the campus.

      - Coordinate network switch IP address requirements for VASS system and cameras with VA OIT.

      - Connection of data cabling from cameras to VA OIT network switches (patch cables from patch panels to switch) shall be provided by VA OIT.

      - Coordinate configuration requirements for networks switches that shall support the VASS system with VA OIT.

    - Network Recording Equipment

      - Install the local SSD storage device within each camera (capacity as determined by OEM vendor) as shown in the design and construction documents, and as specified by the OEM.

      - Configure network connections for each camera as directed by OEM vendor to incorporate each device into the cloud network as coordinated with VA OIT and VA security personnel.

      - Provide software programming per VA guidance and the requirements provided by the Owner. Programming shall include:

        - Camera names

        - Screen views

        - Camera recording schedules (continuous and event) driven recording. Events include alarms from other systems (sensors), manual input, and video motion detection.

        - Video detection zones for each camera requiring video motion detection

        - Alarm interface

        - Alarm outputs

        - GUI maps, views, icons and actions

        - PTZ controls (presets, time schedules for privacy zones etc.)

        - Reports

    - Camera Housings, Mounts, and Poles:

      - Install the camera housings and mounts as specified by the manufacturer and as shown, provide mounting hardware sized appropriately to secure each camera, housing and mount with maximum wind and ice loading encountered at the site.

      - Reuse existing camera junction boxes and cabling pathways where indicated in the documents in locations where a new camera is being installed in the place of an existing camera. Contractor shall confirm the integrity and ability to reuse the existing junction box and pathway infrastructure in the field. Contractor shall notify the Contracting Officer if it is determined that reuse of the existing infrastructure is not feasible due to damage, deterioration or similar condition and provide an alternative method for camera installation.

      - Where cameras are being installed in new locations (exterior or interior), Contractor shall provide junction box and pathways as indicated on the drawings to support the camera and associated cabling.

      - Contractor shall coordinate access to each camera location with the Contracting Officer, VA Security personnel and each building/area user group.

      - Contractor shall restore exterior and interior finishes as required upon completion of camera installation in accordance with the documents. All exterior penetrations shall be sealed and made weather tight in accordance with the documents.

  - ACCEPTANCE TESTING AND SYSTEM START-UP

    - The Contractor shall not apply power to the VASS System until the following items have been completed:

      - VASS System equipment items and have been set up in accordance with manufacturer's instructions.

      - A visual inspection of the VASS System has been conducted to ensure that defective equipment items have not been installed and that there are no loose connections.

      - System wiring has been tested and verified as correctly connected as indicated.

      - All system grounding and transient protection systems have been verified as installed and connected as indicated.

      - Power supplies to be connected to the VASS System have been verified as the correct voltage, phasing, and frequency as indicated.

    - Final Test and Acceptance Plan

      - Develop a final test and acceptance plan to identify each new system component, intent of test, test method, and expected results.

      - Each component listed in the plan shall include space for test part signatures, brief comments, time of test and pass/fail check boxes.

      - Test all equipment, products, and devices in accordance with the plan to ensure completely operational and fully functional security systems. Submit a written final test and acceptance report for review and approval.

      - The report shall be submitted to the Owner’s representative at least

30 days prior to the scheduled system acceptance test.

      - System acceptance of the access control system shall be conditioned upon successful completion and operational demonstration of all system functions and components as documented in the final test and acceptance report.

    - System Acceptance

      - System acceptance shall not occur until after the following activities have been successfully completed:

        - Correction of all deficiencies and punch list items noted on the final test and acceptance report.

        - Acceptance of final test and acceptance report.

        - Acceptance of all project close-out submittals.

        - Delivery of final project close-out documentation.

        - Successful training and demonstration, including operation of systems, systems administration, and system management.

        - Purging of Contractor user privileges and return of all credentials.

    - Satisfaction of the above requirements shall not relieve the Contractor of responsibility for incorrect installation, defective equipment items, or collateral damage as a result of Contractor work efforts.

  - SUPPLEMENTAL CONTRACTOR QUIALITY CONTROL

    - The Contractor shall provide the services of technical representatives who are familiar with all components and installation procedures of the installed VASS System; and are approved by the Contracting Officer.

    - The Contractor will be present on the job site during the preparatory and initial phases of quality control to provide technical assistance.

    - The Contractor shall also be available on an as needed basis to provide assistance with follow-up phases of quality control.

    - The Contractor shall participate in the testing and validation of the system and shall provide certification that the system installed is fully operational as all construction document requirements have been fulfilled.

  - DEMONSTRATION AND TRAINING

    - All testing and training shall be compliant with the VA General Requirements, Section 01 00 00, “GENERAL REQUIREMENTS”.

    - Provide services of manufacturer’s technical representative for minimum of eight (8) hours to instruct VA personnel in operation and maintenance of units.

    - On-site operator training:

      - Instruct operating staff in proper operation, including hands-on training.

      - Minimum of two, four-hour sessions covering the operations for each system installed.

      - Training sessions shall be provided to supervisors, end-user staff, security staff, maintenance personnel, IT personnel, and any other personnel designated by the Owner.

      - Provide training sessions on all work shifts, including day, evening, and night shifts.

    - On-site administrator training: Instruct security system administrators for each system installed, including hands-on training.

      - Minimum of two, four-hour sessions covering the operations for each system installed.

      - Training shall cover all administrative and management functions, including features and controls, for each system.

END

SECTION 31 20 00 EARTHWORK

PART 1 - GENERAL

  - DESCRIPTION OF WORK:

    - This section specifies the requirements for furnishing all equipment, materials, labor, tools, and techniques for earthwork including, but not limited to, the following:

      - Site preparation.

      - Excavation.

4. Filling and backfilling.

6. Soil Disposal.

7. Clean Up.

  - DEFINITIONS:

    - Unsuitable Materials:

      - Fills: Topsoil; frozen materials; construction materials and materials subject to decomposition; clods of clay and stones larger than 75 mm (3 inches); organic material, including silts, which are unstable; and inorganic materials, including silts, too wet to be stable and any material with a liquid limit and plasticity index exceeding 40 and 15 respectively. Unsatisfactory soils also include satisfactory soils not maintained within 2 percent of optimum moisture content at time of compaction, as defined by ASTM D698, D1557, or AASHTO T 99 T 180.

      - Existing Subgrade (Except Footing Subgrade): Same materials as 1.2.A.1, that are not capable of direct support of slabs, pavement, and similar items with possible exception of improvement by compaction, proofrolling, or similar methods.

      - Existing Subgrade (Footings Only): Same as paragraph 1, but no fill or backfill. If materials differ from design requirements, excavate to acceptable strata subject to Resident Engineer's approval.

    - Trench Earthwork: Trenchwork required for utility lines.

    - Site Earthwork: Earthwork operations required in area outside of a line located 1500 mm (5 feet) outside of principal building perimeter and within new construction area with exceptions noted above.

    - Degree of compaction: Degree of compaction is expressed as a percentage of maximum density obtained by laboratory test procedure. This

percentage of maximum density is obtained through use of data provided from results of field test procedures presented in ASTM D1556, ASTM D2167, and ASTM D6938.

    - Fill: Satisfactory soil materials used to raise existing grades. In the Construction Documents, the term “fill” means fill or backfill as appropriate.

    - Backfill: Soil materials or controlled low strength material used to fill an excavation.

    - Unauthorized excavation: Removal of materials beyond indicated sub- grade elevations or indicated lines and dimensions without written authorization by the Resident Engineer. No payment will be made for unauthorized excavation or remedial work required to correct unauthorized excavation.

    - Authorized additional excavation: Removal of additional material authorized by the Resident Engineer based on the determination by the Government’s soils testing agency that unsuitable bearing materials are encountered at required sub-grade elevations. Removal of unsuitable material and its replacement as directed will be paid on basis of Conditions of the Contract relative to changes in work.

    - Subgrade: The undisturbed earth or the compacted soil layer immediately below granular sub-base, drainage fill, or topsoil materials.

    - Borrow: Satisfactory soil imported from off-site for use as fill or backfill.

    - Bedding course: Layer placed over the excavated sub-grade in a trench before laying pipe. Bedding course shall extend up to the springline of the pipe.

    - Sub-base Course: Layer placed between the sub-grade and base course for asphalt paving or layer placed between the sub-grade and a concrete pavement or walk.

    - Utilities include on-site underground pipes, conduits, ducts, and cables as well as underground services within buildings.

    - Debris: Debris includes all materials located within the designated work area not covered in the other definitions and shall include but not be limited to items like vehicles, equipment, appliances, building materials or remains thereof, tires, any solid or liquid chemicals or products stored or found in containers or spilled on the ground.

    - Contaminated soils: Soil that contains contaminates as defined and determined by the Resident Engineer or the Government’s testing agency.

  - RELATED WORK:

    - Materials testing and inspection during construction: Section 01 45 29, TESTING LABORATORY SERVICES.

    - Safety requirements :Section 00 72 00, GENERAL CONDITIONS, Article, ACCIDENT PREVENTION.

    - Protection of existing utilities, fire protection services, existing equipment, roads, and pavements: Section 01 00 00, GENERAL REQUIREMENTS.

    - Subsurface Investigation: Section 01 00 00, GENERAL REQUIREMENTS, Article, PHYSICAL DATA.

    - Erosion Control: Section 01 57 19, TEMPORARY ENVIRONMENTAL CONTROLS,

and Section 32 90 00, PLANTING.

    - Site preparation: Section 31 23 19, DEWATERING, and Section 02 41 00, DEMOLITION.

    - Foundation system requirements: Section 31 62 00, DRIVEN PILES, Section

31 63 16, AUGER CAST GROUT PILES, Section 31 63 26, DRILLED CAISSONS,

Section 31 23 23.33, FLOWABLE FILL.

    - Paving sub-grade requirements: Section 32 12 16, ASPHALT PAVING.

  - CLASSIFICATION OF EXCAVATION:

    - Unclassified Excavation: Removal and disposal of pavements and other man-made obstructions visible on surface; utilities, and other items including underground structures indicated to be demolished and removed; together with any type of materials regardless of character of material and obstructions encountered.

- Rock Excavation:

  - Trenches and Pits: Removal and disposal of solid, homogenous, interlocking crystalline material with firmly cemented, laminated, or foliated masses or conglomerate deposits that cannot be excavated with a late-model, track-mounted hydraulic excavator; equipped with a 1050 mm (42 inch) wide, short-tip-radius rock bucket; rated at not less than 103 kW (138 hp) flywheel power with bucket-curling force of not less than 125 kN (28,090 lbf) and stick-crowd force of not less than 84.5 kN (19,000 lbf); measured according to SAE J-1179.

Trenches in excess of 3000 mm (10 feet) wide and pits in excess of 9000 mm (30 feet) in either length or width are classified as open excavation.

  - Open Excavation: Removal and disposal of solid, homogenous, interlocking crystalline material firmly cemented, laminated, or foliated masses or conglomerate deposits that cannot be dislodged and excavated with a late-model, track-mounted loader; rated at not less than 157 kW (210 hp) flywheel power and developing a minimum of

216 kN (48,510 lbf) breakout force; measured according to SAE J-732.

  - Other types of materials classified as rock are unstratified masses, conglomerated deposits and boulders of rock material exceeding 0.76 m3 (1 cubic yard) for open excavation, or 0.57 m3 (3/4 cubic yard) for footing and trench excavation that cannot be removed by rock excavating equipment equivalent to the above in size and performance ratings, without systematic drilling, ram hammering, ripping, or blasting, when permitted.

.

5. Definitions of rock and guidelines for equipment are presented for general information purposes only. The Contractor is expected to use the information presented in the Geotechnical Engineering Report to evaluate the extent and competency of the rock and to determine both quantity estimations and removal equipment and efforts.

  - MEASUREMENT AND PAYMENT FOR EXCAVATION:

    - Measurement: The unit of measurement for excavation and borrow will be the cubic yard, computed by the average end area method from cross sections taken before and after the excavation and borrow operations, including the excavation for ditches, gutters, and channel changes, when the material is acceptably utilized or disposed of as herein specified. Quantities should be computed by a Registered Professional Land Surveyor specified in Section 01 00 00, GENERAL REQUIREMENTS. authorized excavation of satisfactory subgrade soil, and the volume of loose, scattered rocks and boulders collected within the limits of the work; allowance will be made on the same basis for selected backfill ordered as replacement. The measurement will not include the volume of subgrade material or other material used for purposes other than directed. The volume of overburden stripped from borrow pits and the

volume of excavation for ditches to drain borrow its, unless used as borrow material, will not be measured for payment. The measurement will not include the volume of any excavation performed prior to taking of elevations and measurements of the undisturbed grade.

  - MEASUREMENT AND PAYMENT FOR ROCK EXCAVATION:

    - Measurement: Cross section and measure uncovered and separated materials, and compute quantities by Registered Professional Land Surveyor or Registered Civil Engineer, specified in Section 01 00 00, GENERAL REQUIREMENTS. Do not measure quantities beyond the following limits:

      - 600 mm (24 inches) from outside face of concrete work for which forms are required, except for footings.

      - 300 mm (12 inches) from outside of perimeter of formed footings.

      - 150 mm (6 inches) below bottom of pipe and not more than pipe diameter plus 600 mm (24 inches) in width for pipe trenches.

      - From outside dimensions of concrete work for which no forms are required (trenches, conduits, and similar items not requiring forms).

    - Payment: No separate payment shall be made for rock excavation quantities shown. Contract price and time will be adjusted for overruns or underruns in accordance with Articles, DIFFERING SITE CONDITIONS, CHANGES and CHANGES-SUPPLEMENT of the GENERAL CONDITIONS as

applicable.C.	Payment for Differing Site Conditions: When rock excavation, as classified, is encountered, contract price and time will be adjusted in accordance with Articles, DIFFERING SITE CONDITIONS, CHANGES and CHANGES-SUPPLEMENT of the GENERAL CONDITIONS as applicable.

  - SUBMITTALS:

    - Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

    - Furnish to Resident Engineer:

      - Contractor shall furnish resumes with all personnel involved in the project including Project Manager, Superintendent, and on-site Engineer. Project Manager and Superintendent should have at least 3 years of experience on projects of similar size.

      - Soil samples.

- Classification in accordance with ASTM D2487 for each on-site or borrow soil material proposed for fill, backfill, engineered fill, or structural fill.

- Laboratory compaction curve in accordance with ASTM D698 or D1557 AASHTO T 99 , T 180 for each on site or borrow soil material proposed for fill, backfill, engineered fill, or structural fill.

- Test reports for compliance with ASTM D2940 requirements for subbase material.

- Pre-excavation photographs and videotape in the vicinity of the existing structures to document existing site features, including surfaces finishes, cracks, or other structural blemishes that might be misconstrued as damage caused by earthwork operations.

- The Contractor shall submit a scale plan daily that defines the location, limits, and depths of the area excavated.

      - Contractor shall submit procedure and location for disposal of unused satisfactory material. Proposed source of borrow material. Notification of encountering rock in the project. Notification of encountering materials of an archaeological nature. Advance notice on the opening of excavation or borrow areas. Advance notice on shoulder construction for rigid pavements.

  - APPLICABLE PUBLICATIONS:

    - Publications listed below form a part of this specification to extent referenced. Publications are referenced in text by basic designation only.

    - American Association of State Highway and Transportation Officials (AASHTO):

T99-10 .................Standard Method of Test for Moisture-Density

Relations of Soils Using a 2.5 kg (5.5 lb) Rammer and a 305 mm (12 inch) Drop

T180-10 ................Standard Method of Test for Moisture-Density

Relations of Soils using a 4.54 kg (10 lb) Rammer and a 457 mm (18 inch) Drop

    - American Society for Testing and Materials (ASTM): C33-03 .................Concrete Aggregate

D448-08 ................Standard Classification for Sizes of Aggregate

for Road and Bridge Construction

D698-07e1 ..............Standard Test Method for Laboratory Compaction

Characteristics of Soil Using Standard Effort (12,400 ft. lbf/ft3 (600 kN m/m3))

D1140-00 ...............Amount of Material in Soils Finer than the No.

200 (75-micrometer) Sieve

D1556-07 ...............Standard Test Method for Density and Unit

Weight of Soil in Place by the Sand Cone Method D1557-09 ...............Standard Test Methods for Laboratory Compaction

Characteristics of Soil Using Modified Effort (56,000 ft-lbf/ft3 (2700 kN m/m3))

D2167-08 ...............Standard Test Method for Density and Unit

Weight of Soil in Place by the Rubber Balloon Method

D2487-11 ...............Standard Classification of Soils for

Engineering Purposes (Unified Soil Classification System)

D2940-09 ...............Standard Specifications for Graded Aggregate

Material for Bases or Subbases for Highways or Airports

D6938-10 ...............Standard Test Method for In-Place Density and

Water Content of Soil and Soil-Aggregate by Nuclear Methods (Shallow Depth

    - Society of Automotive Engineers (SAE):

J732-07 ................Specification Definitions - Loaders

J1179-08 ...............Hydraulic Excavator and Backhoe Digging Forces

PART 2 - PRODUCTS

2.1 MATERIALS:

- General: Provide borrow soil material when sufficient satisfactory soil materials are not available from excavations.

- Fills: Material in compliance with ASTM D2487 Soil Classification Groups GW, GP, GM, SW, SP, SM, SC, and ML, or any combination of these groups; free of rock or gravel larger than 75 mm (3 inches) in any dimension, debris, waste, frozen materials, vegetation, and other

deleterious matter. Pursuant to Archaeological Resources Protection Act of 1979, as amended (16 U.S.C. 470aa-mm)and 36 CFR Part 7 - Protection of Archeological Resources, all fill material must come from sources which have been assessed for potential archelogical resources. Documentation must be provided that assures VA that the extraction and utilization of the fill material will not adversely impact known archaeological or tribally-associated sites. Material approved from on site or off site sources having a minimum dry density of 1760 kg/m3 (110 pcf), a maximum Plasticity Index of 15, and a maximum Liquid Limit of 40.

- Engineered Fill: Naturally or artificially graded mixture of compliance with ASTM D2487 Soil Classification Groups GW, GP, GM, SW, SP, SM, SC, and ML, or any combination of these groups, or as approved by the Engineer or material with at least 90 percent passing a 37.5-mm (1 1/2- inch) sieve and not more than 12 percent passing a 75-µm (No. 200) sieve, per ASTM D2940;.

- Bedding: Naturally or artificially graded mixture of natural or crushed gravel, crushed stone, and natural or crushed sand; ASTM D2940; except with 100 percent passing a 25 mm (1 inch) sieve and not more than 8 percent passing a 75-μm (No. 200) sieve.

- Drainage Fill: Washed, narrowly graded mixture of crushed stone, or crushed or uncrushed gravel; ASTM D448; coarse-aggregate grading Size 57; with 100 percent passing a 37.5 mm (1 1/2-inch) sieve and 0 to 5 percent passing a 2.36 mm (No. 8) sieve.

- Granular Fill:

  - Under concrete slab, - granular fill shall consist of clean, poorly graded crushed rock, crushed gravel, or uncrushed gravel placed beneath a building slab with or without a vapor barrier to cut off the capillary flow of pore water to the area immediately below. Fine aggregate grading shall conform to ASTM C 33 with a maximum of

3 percent by weight passing ASTM D 1140, //75 micrometers (No. 200) sieve, or 37.5 mm (1-1/2 inches)and no more than 2 percent by weight passing the 4.75 mm (No. 4) size sieveor coarse aggregate Size 57, 67, or 77.

  - Bedding for sanitary and storm sewer pipe, crushed stone or gravel graded from 13 mm (1/2 inch) to 4.75 mm (No 4), per ASTM D2940.

- Requirements for Offsite Soils: Offsite soils brought in for use as backfill shall be tested for TPH, BTEX and full TCLP including ignitability, corrosivity and reactivity. Backfill shall contain less than 100 parts per million (ppm) of total hydrocarbons (TPH) and less than 10 ppm of the sum of Benzene, Toluene, Ethyl Benzene, and Xylene (BTEX) and shall not fail the TCLP test. TPH concentrations shall be determined by using EPA 600/4-79/020 Method 418.1. BTEX concentrations shall be determined by using EPA SW-846.3-3a Method 5030/8020. TCLP shall be performed in accordance with EPA SW-846.3-3a Method 1311. Provide Borrow Site Testing for TPH, BTEX and TCLP from a composite sample of material from the borrow site, with at least one test from each borrow site.

- Buried Warning and Identification Tape: Polyethylene plastic and metallic core or metallic-faced, acid- and alkali-resistant polyethylene plastic warning tape manufactured specifically for warning and identification of buried utility lines. Provide tape on rolls, 3 inch minimum width, color coded as specific below for the intended utility with warning and identification imprinted in bold black letters continuously over the entire tape length. Warning and identification to read, “CAUTION, BURIED (intended service) LINE BELOW” or similar wording. Color and printing shall be permanent, Unaffected by moisture or soil. Warning tape color codes:

Red:	Electric

Orange: Telephone and Other Communications

- Warning Tape for Metallic Piping: Acid and alkali-resistant polyethylene plastic tape conforming to the width, color, and printing requirements specified above. Minimum thickness of tape shall be 0.076 mm (0.003 inch). Tape shall have a minimum strength of 10.3 MPa (1500 psi) lengthwise, and 8.6 MPa (1250 psi) crosswise, with a maximum 350 percent elongation.

- Detectable Warning Tape for Non-Metallic Piping: Polyethylene plastic tape conforming to the width, color, and printing requirements specified above. Minimum thickness of the tape shall be 0.102 mm (0.004 inch). Tape shall have a minimum strength of 10.3 MPa (1500 psi) lengthwise and 8.6 MPa (1250 psi) crosswise. Tape shall be

manufactured with integral wires, foil backing, or other means of enabling detection by a metal detector when tape is buried up to 0.9 m (3 feet) deep. Encase metallic element of the tape in a protective jacket or provide with other means of corrosion protection.

- Detection Wire For Non-Metallic Piping: Detection wire shall be Insulated single strand, solid copper with a minimum of 12 AWG.

PART 3 - EXECUTION

        - SITE PREPARATION:

          - Clearing: Clear within limits of earthwork operations as shown. Work includes removal of trees, shrubs, fences, foundations, incidental structures, paving, debris, trash, and other obstructions. Remove materials from Medical Center .

D. Stripping Topsoil: Strip topsoil from within limits of earthwork operations as specified. Topsoil shall be a fertile, friable, natural topsoil of loamy character and characteristic of locality. Topsoil shall be capable of growing healthy horticultural crops of grasses. Stockpile topsoil and protect as directed by Resident Engineer. Eliminate foreign materials, such as weeds, roots, stones, subsoil, frozen clods, and similar foreign materials larger than 0.014 m3 (1/2 cubic foot) in volume, from soil as it is stockpiled. Retain topsoil on station. Remove foreign materials larger than 50 mm (2 inches) in any dimension from topsoil used in final grading. Topsoil work, such as stripping, stockpiling, and similar topsoil work shall not, under any circumstances, be carried out when soil is wet so that the composition of the soil will be destroyed. Test the soil for chemicals, pesticides and fertilizers if topsoil is to be removed from lands formerly utilized as farmland, to verify suitability for use as topsoil in the cemetery where new lawn areas are to be established.

E. Concrete Slabs and Paving: Score deeply or saw cut to insure a neat, straight cut, sections of existing concrete slabs and paving to be removed where excavation or trenching occurs. Extend pavement section to be removed a minimum of 300 mm (12 inches) on each side of widest part of trench excavation and insure final score lines are approximately parallel unless otherwise indicated. Remove material from Medical Center.

G. Disposal: All materials removed from the property shall be disposed of at a legally approved site, for the specific materials, and all removals shall be in accordance with all applicable Federal, State and local regulations. No burning of materials is permitted onsite.

        - EXCAVATION:

          - Shoring, Sheeting and Bracing: Shore, brace, or slope, its angle of repose or to an angle considered acceptable by the Resident Engineer, banks of excavations to protect workmen, banks, adjacent paving, structures, and utilities.

            - Design of the temporary support of excavation system is the responsibility of the Contractor. The Contractor shall submit a Shoring and Sheeting plan for approval 15 days prior to starting work. Submit drawings and calculations, certified by a registered professional engineer, describing the methods for shoring and sheeting of excavations. Shoring, including sheet piling, shall be furnished and installed as necessary to protect workmen, banks, adjacent paving, structures, and utilities. Shoring, bracing, and sheeting shall be removed as excavations are backfilled, in a manner to prevent caving.

            - Construction of the support of excavation system shall not interfere with the permanent structure and may begin only after a review by the Resident Engineer.

            - Extend shoring and bracing to a minimum of 1500 mm (5 feet) below the bottom of excavation. Shore excavations that are carried below elevations of adjacent existing foundations.

            - The Contractor is required to hire a Professional Geotechnical Engineer to provide inspection of excavations and soil/groundwater conditions throughout construction. The Geotechnical Engineer shall be responsible for performing pre-construction and periodic site visits throughout construction to assess site conditions. The Geotechnical Engineer shall update the excavation, sheeting and dewatering plans as construction progresses to reflect changing conditions and shall submit an updated plan if necessary. A written report shall be submitted, at least monthly, informing the Contractor and Resident Engineer of the status of the plan and an

accounting of the Contractor's adherence to the plan addressing any present or potential problems. The Geotechnical Engineer shall be available to meet with the Resident Engineer at any time throughout the contract duration.

C. Subgrade Protection: Protect subgrades from softening, undermining, washout, or damage by rain or water accumulation. Reroute surface water runoff from excavated areas and not allow water to accumulate in excavations. Do not use excavated trenches as temporary drainage ditches. When subgrade for foundations has been disturbed by water, remove disturbed material to firm undisturbed material after water is brought under control. Replace disturbed subgrade in trenches with concrete or material approved by the Resident Engineer.

E. Proofrolling:

- After rough grade has been established in cut areas and prior to placement of fill in fill areas under building and pavements, proofroll exposed subgrade with a fully loaded dump truck to check for pockets of soft material.

- Proof rolling shall be done on an exposed subgrade free of surface water (wet conditions resulting from rainfall) which would promote degradation of an otherwise acceptable subgrade. //After stripping, proof roll the existing subgrade of the with six passes of a dump truck loaded with 6 cubic meters (4 cubic yards) of soil 13.6 meter tons (15 ton), pneumatic-tired roller. Operate the roller truck in a systematic manner to ensure the number of passes over all areas, and at speeds between 4 to 5.5 km/hour (2 1/2 to 3 1/2 mph). When proof rolling, one-half of the passes made with the roller shall be in a direction perpendicular to the other passes. Notify the Resident Engineer a minimum of 3 days prior to proof rolling. Proof rolling shall be performed in the presence of the Resident Engineer. Maintain subgrade until succeeding operation has been accomplished.

G. Trench Earthwork:

- Utility trenches (except sanitary and storm sewer):

  - Excavate to a width as necessary for sheeting and bracing and proper performance of the work.

  - Grade bottom of trenches with bell holes scooped out to provide a uniform bearing.

  - Support piping on suitable undisturbed earth unless a mechanical support is shown. Unstable material removed from the bottom of the trench or excavation shall be replaced with select granular material placed in layers not exceeding 150 mm (6 inches) loose thickness.

  - Length of open trench in advance of piping laying shall not be greater than is authorized by Resident Engineer.

  - Provide buried utility lines with utility identification tape. Bury tape 300 mm (12 inches) below finished grade; under pavements and slabs, bury tape 150 mm (6 inches) below top of subgrade

  - Bury detection wire directly above non-metallic piping at a distance not to exceed 300 mm (12 inches) above the top of pipe. The wire shall extend continuously and unbroken, from manhole to manhole. The ends of the wire shall terminate inside the manholes at each end of the pipe, with a minimum of 0.9 m (3 feet) of wire, coiled, remaining accessible in each manhole. The wire shall remain insulated over it's entire length. The wire shall enter manholes between the top of the corbel and the frame, and extend up through the chimney seal between the frame and the chimney seal. For force mains, the wire shall terminate in the valve pit at the pump station end of the pipe.

  - Bedding shall be of the type and thickness shown.// Initial backfill material shall be placed and compacted with approved tampers to a height of at least one foot above the utility pipe or conduit. The backfill shall be brought up evenly on both sides of the pipe for the full length of the pipe. Care shall be taken to ensure thorough compaction of the fill under the haunches of the pipe. Except as specified otherwise in the individual piping section, provide bedding for buried piping in accordance with AWWA C600, Type 4, except as specified herein. Backfill to top of pipe shall be compacted to 95 percent of ASTM D 698 maximum density. Plastic piping shall have bedding to spring line of pipe. Provide materials as follows:

    - Class I: Angular, 6 to 40 mm (0.25 to 1.5 inches), graded stone, including a number of fill materials that have regional significance such as coral, slag, cinders, crushed stone, and crushed shells.

    - Class II: Coarse sands and gravels with maximum particle size of 40 mm (1.5 inches), including various graded sands and gravels containing small percentages of fines, generally granular and noncohesive, either wet or dry. Soil Types GW, GP, SW, and SP are included in this class as specified in ASTM D2487.

    - Clean, coarse-grained sand classified as in accordance with gradation of the DOT State Standard.

    - Clean, coarsely graded natural gravel, crushed stone or a combination thereof identified as in accordance with gradation of the DOT State Standard.

H. Site Earthwork: Earth excavation includes excavating pavements and obstructions visible on surface; underground structures, utilities, and other items indicated to be removed; together with soil, boulders, and other materials not classified as rock or unauthorized excavation. Excavation shall be accomplished as required by drawings and specifications. Excavate to indicated elevations and dimensions within a tolerance of plus or minus 25 mm (1 inch). Extend excavations a sufficient distance from structures for placing and removing concrete formwork, for installing services and other construction, complying with OSHA requirements, and for inspections. Remove subgrade materials that are determined by Resident Engineer as unsuitable, and replace with acceptable material. If there is a question as to whether material is unsuitable or not, the contractor shall obtain samples of the material, under the direction of the Resident Engineer, and the materials shall be examined by an independent testing laboratory for soil classification to determine whether it is unsuitable or not. Testing of the soil shall be performed by the VA Testing Laboratory. When unsuitable material is encountered and removed, contract price and time will be adjusted in accordance with Articles, DIFFERING SITE CONDITIONS, CHANGES and CHANGES-SUPPLEMENT of the GENERAL CONDITIONS as

applicable. Adjustments to be based on volume in cut section only.

- Site Grading:

  - Provide a smooth transition between adjacent existing grades and new grades.

  - Cut out soft spots, fill low spots, and trim high spots to comply with required surface tolerances.

  - Slope grades to direct water away from buildings and to prevent ponds from forming where not designed. Finish subgrades to required elevations within the following tolerances:

    - Lawn or Unpaved Areas: Plus or minus 25 mm (1 inch).

    - Walks: Plus or minus 25 mm (1 inch).

    - Pavements: Plus or minus 13 mm (1 inch).

  - Grading Inside Building Lines: Finish subgrade to a tolerance of

13 mm (1/2 inch) when tested with a 3000 mm (10 foot) straightedge.

  - FILLING AND BACKFILLING:

    - General: Do not fill or backfill until all debris, water, unsatisfactory soil materials, obstructions, and deleterious materials have been removed from excavation. For fill and backfill, use excavated materials and borrow meeting the criteria specified herein, as applicable. Borrow will be supplied at no additional cost to the Government. Do not use unsuitable excavated materials. Do not backfill until foundation walls have been completed above grade and adequately braced, waterproofing or dampproofing applied, foundation drainage, and pipes coming in contact with backfill have been installed and work inspected and approved by Resident Engineer.

    - Placing: Place materials in horizontal layers not exceeding 200 mm (8 inches) in loose depth for material compacted by heavy compaction equipment, and not more than 100 mm (4 inches) in loose depth for material compacted by hand-operated tampers and then compacted. Place backfill and fill materials evenly on all sides of structures to required elevations, and uniformly along the full length of each structure. Place no material on surfaces that are muddy, frozen, or contain frost.

    - Compaction: Compact with approved tamping rollers, sheepsfoot rollers, pneumatic tired rollers, steel wheeled rollers, vibrator compactors, or other approved equipment (hand or mechanized) well suited to soil being

compacted. Do not operate mechanized vibratory compaction equipment within 3000 mm (10 feet) of new or existing building walls without prior approval of Resident Engineer. Moisten or aerate material as necessary to provide moisture content that will readily facilitate obtaining specified compaction with equipment used. Backfill adjacent to any and all types of structures shall be placed and compacted to at least 90 percent laboratory maximum density for cohesive materials or

95 percent laboratory maximum density for cohesionless materials to prevent wedging action or eccentric loading upon or against the structure. Compact soil to not less than the following percentages of maximum dry density, according to ASTM D698 or ASTM D1557 as specified below:

- Fills, Embankments, and Backfill

  - Under proposed structures, building slabs, steps, and paved areas, scarify and recompact top 300 mm (12 inches) of existing subgrade and each layer of backfill or fill material in accordance with AASHTO T99 T180 Method A T 191, T 310, ASTM D698 D1557,Method A, D1556, D2167, D6938 95 percent.

- Under Sidewalks, scarify and recompact top 150 mm (6 inches) below subgrade and compact each layer of backfill or fill material in accordance with AASHTO T99, T180 Method A T 191 T 310 ASTM D698, D1557, Method A D1556, D2167, D6938 95 percent.

- Landscaped areas, top 400 mm (16 inches), AASHTO T99 T180 Method A T 191 T 310 ASTM D698 D1557 Method A D1556 D2167 D6938 85

percent.

- Landscaped areas, below 400 mm (16 inches) of finished grade, AASHTO T99 T180 Method A T 191 T 310 ASTM D698 D1557 Method A D1556 D2167 D6938 90 percent.

- Natural Ground (Cut or Existing)

  - Under building slabs, steps and paved areas, top 150 mm (6 inches), AASHTO T99 T180 Method A T 191 T 310 ASTM D698 D1557

Method A D1556 D2167 D6938 95 percent.

  - Curbs, curbs and gutters, top 150 mm (6 inches), AASHTO T99 T180 Method A T 191 T 310 ASTM D698 D1557 Method A D1556 D2167 D6938

95 percent.

  - Under sidewalks, top 150 mm (6 inches), AASHTO T99 T180 Method A T 191 T 310 ASTM D698 D1557 Method A D1556 D2167 D6938 95

percent.

    - Borrow Material: Borrow material shall be selected to meet the requirements and conditions of the particular fill or embankment for which it is to be used. Borrow material shall be obtained from the borrow areas within the limits of the project site, selected by the Contractor or from approved private sources. Unless otherwise provided in the contract, the Contractor shall obtain from the owners the right to procure material, pay royalties and other charges involved, and bear the expense of developing the sources, including rights-of-way for hauling. Borrow material from approved sources on Government- controlled land may be obtained without payment of royalties. Unless specifically provided, no borrow shall be obtained within the limits of the project site without prior written approval. Necessary clearing, grubbing, and satisfactory drainage of borrow pits and the disposal of debris thereon shall be considered related operations to the borrow excavation.

    - Opening and Drainage of Excavation and Borrow Pits: The Contractor shall notify the Resident Engineer sufficiently in advance of the opening of any excavation or borrow pit to permit elevations and measurements of the undisturbed ground surface to be taken. Except as otherwise permitted, borrow pits and other excavation areas shall be excavated providing adequate drainage. Overburden and other spoil material shall be transported to designated spoil areas or otherwise disposed of as directed. Borrow pits shall be neatly trimmed and drained after the excavation is completed. The Contractor shall ensure that excavation of any area, operation of borrow pits, or dumping of spoil material results in minimum detrimental effects on natural environmental conditions.

  - GRADING:

    - General: Uniformly grade the areas within the limits of this section, including adjacent transition areas. Smooth the finished surface within specified tolerance. Provide uniform levels or slopes between points where elevations are indicated, or between such points and existing

finished grades. Provide a smooth transition between abrupt changes in slope.

    - Cut rough or sloping rock to level beds for foundations. In pipe spaces or other unfinished areas, fill low spots and level off with coarse sand or fine gravel.

    - Slope backfill outside building away from building walls for a minimum distance of 1800 mm (6 feet).

    - Finish grade earth floors in pipe basements as shown to a level, uniform slope and leave clean.

    - Finished grade shall be at least 150 mm (6 inches) below bottom line of window or other building wall openings unless greater depth is shown.

    - Place crushed stone or gravel fill under concrete slabs on grade, tamped, and leveled. Thickness of fill shall be 150 mm (6 inches) unless otherwise shown.

    - Finish subgrade in a condition acceptable to Resident Engineer at least one day in advance of paving operations. Maintain finished subgrade in a smooth and compacted condition until succeeding operation has been accomplished. Scarify, compact, and grade subgrade prior to further construction when approved compacted subgrade is disturbed by Contractor's subsequent operations or adverse weather.

    - Grading for Paved Areas: Provide final grades for both subgrade and base course to +/- 6 mm (0.25 inches) of indicated grades.

  - DISPOSAL OF UNSUITABLE AND EXCESS EXCAVATED MATERIAL:

    - Disposal: Remove surplus satisfactory soil and waste material, including unsatisfactory soil, trash, and debris, and legally dispose of it off Medical Center property.

    - Disposal: Transport surplus satisfactory soil to designated storage areas on Medical Center property. Stockpile or spread soil as directed by Resident Engineer.

1. Remove waste material, including unsatisfactory soil, trash, and debris, and legally dispose of it off Medical Center property.

    - Place excess excavated materials suitable for fill and/or backfill on site where directed.

    - Remove from site and dispose of any excess excavated materials after all fill and backfill operations have been completed.

    - Segregate all excavated contaminated soil designated by the Resident Engineer from all other excavated soils, and stockpile on site on two

0.15 mm (6 mil) polyethylene sheets with a polyethylene cover. A designated area shall be selected for this purpose. Dispose of excavated contaminated material in accordance with State and Local requirements.

  - CLEAN UP:

Upon completion of earthwork operations, clean areas within contract limits, remove tools, and equipment. Provide site clear, clean, free of debris, and suitable for subsequent construction operations. Remove all debris, rubbish, and excess material from Medical Center Property.

E N D

SECTION 32 12 16 ASPHALT PAVING

PART 1 - GENERAL

  - DESCRIPTION

This work shall cover the composition, mixing, and construction upon the prepared subgrade, and the protection of hot asphalt concrete pavement. The hot asphalt concrete pavement shall consist of an aggregate or asphalt base course and asphalt surface course constructed in conformity with the lines, grades, thickness, and cross sections as shown. Each course shall be constructed to the depth, section, or elevation required by the drawings and shall be rolled, finished, and approved before the placement of the next course.

  - RELATED WORK

    - Laboratory and field testing requirements: Section 01 45 29, TESTING LABORATORY SERVICES.

    - Subgrade Preparation: Paragraph 3.3 and Section 31 20 00, EARTH MOVING.

    - Pavement Markings: Section 32 17 23, PAVEMENT MARKINGS.

  - INSPECTION OF PLANT AND EQUIPMENT

The Resident Engineer shall have access at all times to all parts of the material producing plants for checking the mixing operations and materials and the adequacy of the equipment in use.

  - ALIGNMENT AND GRADE CONTROL

The Contractor’s Registered Professional Land Surveyor shall establish and control the pavement (aggregate or asphalt base course and asphalt surface course) alignments, grades, elevations, and cross sections as shown on the Drawings.

  - SUBMITTALS

    - In accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES, furnish the following:

    - Data and Test Reports:

      - Aggregate Base Course: Sources, gradation, liquid limit, plasticity index, percentage of wear, and other tests required by State Highway Department.

      - Asphalt Base/Surface Course: Aggregate source, gradation, soundness loss, percentage of wear, and other tests required by State Highway Department.

      - Job-mix formula.

    - Certifications:

      - Asphalt prime and tack coat material certificate of conformance to State Highway Department requirements.

      - Asphalt cement certificate of conformance to State Highway Department requirements.

      - Job-mix certification - Submit plant mix certification that mix equals or exceeds the State Highway Specification.

    - One copy of State Highway Department Specifications.

    - Provide MSDS (Material Safety Data Sheets) for all chemicals used on ground.

PART 2 - PRODUCTS

  - GENERAL

    - Aggregate base Asphaltic base and asphalt concrete materials shall conform to the requirements of the following and other appropriate sections of the latest version of the State Highway Material Specifications, including amendments, addenda and errata. Where the term "Engineer" or "Commission" is referenced in the State Highway Specifications, it shall mean the VA Resident Engineer or VA Contracting Officer.

  - AGGREGATES

    - Provide aggregates consisting of crushed stone, gravel, sand, or other sound, durable mineral materials processed and blended, and naturally combined.

    - Subbase aggregate (where required) maximum size: 38mm(1-1/2").

    - Base aggregate maximum size:

      - Base course over 152mm(6") thick: 38mm(1-1/2");

      - Other base courses: 19mm(3/4").

    - Asphaltic base course:

      - Maximum particle size not to exceed 25.4mm(1”).

      - Where conflicts arise between this specification and the requirements in the latest version of the State Highway Specifications, the State Specifications shall control.

    - Aggregates for asphaltic concrete paving: Provide a mixture of sand, mineral aggregate, and liquid asphalt mixed in such proportions that the percentage by weight will be within:

Sieve Sizes	Percentage Passing 19mm(3/4")		100

| 9.5mm(3/8") |  | 67 | to | 85 |
| --- | --- | --- | --- | --- |
| 6.4mm(1/4") |  | 50 | to | 65 |
| 2.4mm(No. 8 | mesh) | 37 | to | 50 |
| 600µm(No. 30 mesh) |  | 15 | to | 25 |
| 75µm(No. 200 mesh) |  | 3 | to | 8 |

plus 50/60 penetration liquid asphalt at 5 percent to 6-1/2 percent of the combined dry aggregates.

  - ASPHALTS

    - Comply with provisions of Asphalt Institute Specification SS2:

      - Asphalt cement:	Penetration grade 50/60

      - Prime coat:	Cut-back type, grade MC-250

      - Tack coat:	Uniformly emulsified, grade SS-1H

  - SEALER

    - Provide a sealer consisting of suitable fibrated chemical type asphalt base binders and fillers having a container consistency suitable for troweling after thorough stirring, and containing no clay or other deleterious substance.

    - Where conflicts arise between this specification and the requirements in the latest version of the State Highway Specifications, the State Specifications shall control.

PART 3 - EXECUTION

  - GENERAL

The Asphalt Concrete Paving equipment, weather limitations, job-mix formula, mixing, construction methods, compaction, finishing, tolerance, and protection shall conform to the requirements of the appropriate sections of the State Highway Specifications for the type of material specified.

  - MIXING ASPHALTIC CONCRETE MATERIALS

    - Provide hot plant-mixed asphaltic concrete paving materials.

      - Temperature leaving the plant: 143 degrees C(290 degrees F) minimum,

160 degrees C(320 degrees F) maximum.

      - Temperature at time of placing: 138 degrees C(280 degrees F) minimum.

  - SUBGRADE

    - Shape to line and grade and compact with self-propelled rollers.

    - All depressions that develop under rolling shall be filled with acceptable material and the area re-rolled.

    - Soft areas shall be removed and filled with acceptable materials and the area re-rolled.

    - Should the subgrade become rutted or displaced prior to the placing of the subbase, it shall be reworked to bring to line and grade.

    - Proof-roll the subgrade with maximum 45 tonne (50 ton) gross weight dump truck as directed by VA Resident Engineer or VA Contracting Officer. If pumping, pushing, or other movement is observed, rework the area to provide a stable and compacted subgrade.

  - BASE COURSES

    - Subbase (when required)

      - Spread and compact to the thickness shown on the drawings.

      - Rolling shall begin at the sides and continue toward the center and shall continue until there is no movement ahead of the roller.

      - After completion of the subbase rolling there shall be no hauling over the subbase other than the delivery of material for the top course.

    - Base

      - Spread and compact to the thickness shown on the drawings.

      - Rolling shall begin at the sides and continue toward the center and shall continue until there is no movement ahead of the roller.

      - After completion of the base rolling there shall be no hauling over the base other than the delivery of material for the top course.

    - Thickness tolerance: Provide the compacted thicknesses shown on the Drawings within a tolerance of minus 0.0mm (0.0") to plus 12.7mm (0.5").

    - Smoothness tolerance: Provide the lines and grades shown on the Drawings within a tolerance of 5mm in 3m (3/16 inch in ten feet).

    - Moisture content: Use only the amount of moisture needed to achieve the specified compaction.

  - PLACEMENT OF ASPHALTIC CONCRETE PAVING

    - Remove all loose materials from the compacted base.

    - Apply the specified prime coat, and tack coat where required, and allow to dry in accordance with the manufacturer’s recommendations as approved by the Architect or Engineer.

    - Receipt of asphaltic concrete materials:

      - Do not accept material unless it is covered with a tarpaulin until unloaded, and unless the material has a temperature of not less than

130 degrees C(280 degrees F).

      - Do not commence placement of asphaltic concrete materials when the atmospheric temperature is below 10 degrees C (50 degrees F), not during fog, rain, or other unsuitable conditions.

    - Spreading:

      - Spread material in a manner that requires the least handling.

      - Where thickness of finished paving will be 76mm (3") or less, spread in one layer.

    - Rolling:

      - After the material has been spread to the proper depth, roll until the surface is hard, smooth, unyielding, and true to the thickness and elevations shown own the drawings.

      - Roll in at least two directions until no roller marks are visible.

      - Finished paving smoothness tolerance:

        - No depressions which will retain standing water.

        - No deviation greater than 3mm in 1.8m (1/8" in six feet).

  - APPLICATION OF SEAL COAT

    - Prepare the surfaces, mix the seal coat material, and apply in accordance with the manufacturer’s recommendations as approved by the Architect or Engineer.

    - Achieve a finished surface seal which, when dry and thoroughly set, is smooth, tough, resilient, of uniform black color, and free from coarse textured areas, lap marks, ridges, and other surface irregularities.

    - When sealing new asphalt paving wait an entire year to allow for the expansion and contraction of a year’s cycle of both warm and cool temperatures. This allows for the asphalt’s oils to properly cure and begin oxidation before applying a seal coat.

    - When seal coating in less than a year apply two coats, spray applied. This application method is preferred for less than a year application when there is still plenty of asphalt cement present for the seal coat to bond to.

    - When seal coating existing paving that has new asphalt patches, apply two coats sprayed to the existing asphalt and a single lighter coat on new patch work, just enough to make the color of the new patches match the rest of the reseal coated paving.

  - PROTECTION

Protect the asphaltic concrete paved areas from traffic until the sealer is set and cured and does not pick up under foot or wheeled traffic.

  - FINAL CLEAN-UP

Remove all debris, rubbish, and excess material from the work area.

- - - E N D - - -

SECTION 32 17 23 PAVEMENT MARKINGS

PART 1 - GENERAL

  - SUMMARY

    - Section Includes:

      - Paint on pavement surfaces, in form of traffic lanes, parking bays, areas restricted to handicapped persons, crosswalks, and other detail pavement markings.

  - RELATED REQUIREMENTS

    - Paint VOC Limits: Section 01 81 13, SUSTAINABLE CONSTRUCTION REQUIREMENTS.

    - Paint Color: Section 09 06 00, SCHEDULE FOR FINISHES.

  - APPLICABLE PUBLICATIONS

    - Comply with references to extent specified in this section.

    - Federal Specifications (Fed. Spec.):

      - TT-P-1952F - Paint, Traffic and Airfield Marking, Waterborne.

    - Master Painters Institute (MPI):

      - No. 97 - Traffic Marking Paint, Latex.

  - SUBMITTALS

    - Submittal Procedures: Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

    - Submittal Drawings:

      - Show pavement marking configuration and dimensions.

      - Show international symbol of accessibility at designated parking spaces.

    - Manufacturer's Literature and Data:

      - Description of each product.

      - Application instructions.

    - Samples:

      - Paint: 200 mm (8 inches) square, each type and color.

    - Certificates: Certify products comply with specifications.

    - Qualifications: Substantiate qualifications comply with specifications.

      - Installer with project experience list.

  - QUALITY ASSURANCE

    - Installer Qualifications:

      - Regularly installs specified products.

      - Installed specified products with satisfactory service on five similar installations for minimum five years.

        - Project Experience List: Provide contact names and addresses for completed projects.

  - DELIVERY

    - Deliver products in manufacturer's original sealed packaging.

    - Mark packaging, legibly. Indicate manufacturer's name or brand, type, color, production run number, and manufacture date.

    - Before installation, return or dispose of products within distorted, damaged, or opened packaging.

  - STORAGE AND HANDLING

    - Store products indoors in dry, weathertight conditioned facility.

    - Protect products from damage during handling and construction operations.

  - FIELD CONDITIONS

    - Environment:

      - Product Temperature: Minimum 13 degrees C (55 degrees F) for minimum

48 hours before installation.

a. Surface to be painted and ambient temperature: Minimum

10 degrees C (50 degrees F) and maximum 35 degrees C (95 degrees F).

    - Field Measurements: Verify field conditions affecting traffic marking installation. Show field measurements on Submittal Drawings.

  - WARRANTY

    - Construction Warranty: FAR clause 52.246-21, "Warranty of Construction."

PART 2 - PRODUCTS

  - SYSTEM PERFORMANCE

    - Design paint complying with specified performance:

      - Application: Fed. Spec. TT-P-1952.

  - PRODUCTS - GENERAL

    - Basis of Design: Refer to VA D.O.T. standards.

  - PAINT APPLICATOR

    - Apply marking paint with approved mechanical equipment. Provide equipment with constant agitation of paint and travel at controlled speeds. Synchronize one or more paint "guns" to automatically begin and cut off paint flow in case of skip lines. Equipment to have manual control to apply continuous lines of varying length and marking widths as indicated on Drawings. Provide pneumatic spray guns for hand application of paint in areas where mobile paint applicator cannot be used.

  - PAINT

    - Paint: MPI No. 97. For obliterating existing markings comply with Fed. Spec. TT-P-1952. Provide minimum 18 L (5 gallons) containers.

PART 3 - EXECUTION

  - PREPARATION

    - Examine and verify substrate suitability for product installation.

      - Allow new pavement surfaces to cure for period of minimum 14 days before application of marking materials.

    - Protect existing construction and completed work from damage.

    - Clean substrates. Remove contaminants capable of affecting subsequently installed product's performance.

      - Remove dust, dirt, and other granular surface deposits by sweeping, blowing with compressed air, rinsing with water, or combination of these methods.

      - Completely remove rubber deposits, existing paint markings, and other coatings adhering to pavement with scrapers, wire brushings, sandblasting, mechanical abrasion, or approved chemicals as directed by Contracting Officer's Representative.

      - As an option, comply with Fed. Spec. TT-P-1952 for removal of existing paint markings on asphalt pavement. Apply black paint in as many coats as necessary to completely obliterate existing markings.

      - Scrub affected areas with several applications of trisodium phosphate solution or other approved detergent or degreaser, and

rinse thoroughly after each application, Where oil or grease are present on old pavements to be marked, .

        - After cleaning, seal oil-soaked areas with cut shellac to prevent bleeding through new paint.

      - Clean and dry surface before pavement marking.Do not begin any marking until Contracting Officer's Representative inspected surface and gives permission to proceed.

  - TEMPORARY PAVEMENT MARKING

    - Apply Temporary Pavement Markings of colors, widths and lengths shown on drawings or directed by Contracting Officer's Representative. After temporary marking has served its purpose and when so ordered by Contracting Officer's Representative, remove temporary marking by carefully controlled sandblasting, approved grinding equipment, or other approved method to prevent damage on applied surface.

    - As an option, provide approved preformed pressure sensitive,

// reflective, // adhesive tape type of temporary pavement marking of required colors, widths and lengths in lieu of temporary painted // and reflective // marking. Continuous durability and effectiveness of such marking is required during period for which its use is required. Remove any unsatisfactory tape type marking and replace with painted // and reflective // markings.

  - INSTALLATION - GENERAL

    - Install products according to manufacturer's instructions and approved submittal drawings.

      - When manufacturer's instructions deviate from specifications, submit proposed resolution for Contracting Officer's Representative consideration.

  - PAINT APPLICATION

    - Apply uniformly painted pavement marking of required colors, length, and width with true, sharp edges and ends on properly cured, prepared, and dried surfaces.

    - Comply with details as indicated on drawings and established control points.

    - Apply paint at wet film thickness of 0.4 mm (0.015 inch). Apply paint in one coat. When directed by Contracting Officer's Representative,

apply additional coats at markings showing light spots. Comply with paint manufacturer's maximum drying time requirements to prevent undue softening of asphalt, and pick-up, displacement, or discoloration by tires of traffic.

    - When deficiency in marking drying occurs, discontinue paint operations until cause of slow drying is determined and corrected.

    - Remove and replace marking applied less than minimum material rates, deviates from true alignment, exceeds stipulated length and width tolerances, or shows light spots, smears, or other deficiencies or irregularities.

    - Remove marking by carefully controlled sandblasting, approved grinding equipment, or other approve method to prevent damage on applied surface.

  - DETAIL PAVEMENT MARKING APPLICATION

    - Apply Detail Pavement Markings, exclusive of actual traffic lane marking as follows:

      - At exit and entrance islands and turnouts.

      - On curbs.

      - At crosswalks.

      - At parking bays.

      - Other locations as indicated on drawings.

    - Apply International Handicapped Symbol at indicated parking spaces. Color as shown on drawings. Apply paint for symbol using suitable template that will provide pavement marking with true, sharp edges and ends.

    - Install detail pavement markings of colors, widths and lengths, and design pattern at locations indicated on drawings.

  - TOLERANCES

    - Length and Width of Lines: Plus or minus 75 mm (3 inches) and plus or minus 3 mm (1/8 inch), respectively, in case of skip markings.

    - Length of intervals exceeding line length tolerance are not acceptable.

  - CLEANING

    - Remove excess paint before paint sets.

  - PROTECTION

    - Protect pavement markings from traffic and construction operations.

      - Protect newly painted markings from vehicular traffic until paint is dry and track free.

      - Place warning signs at beginning of wet line, and at points well in advance of marking equipment for alerting approaching traffic from both directions.

      - Place small flags or other similarly effective small objects near freshly applied markings at frequent intervals to reduce crossing by traffic.

    - Repair damage.

- - - E N D - - -

SECTION 32 90 00 PLANTING

PART 1 - GENERAL

  - SUMMARY

    - Section Includes:

      - Plants, soils, edging, turf, and landscape materials.

  - RELATED REQUIREMENTS

  - DEFINITIONS

    - Pesticide: Any substance or mixture of substances, including biological control agents, that may prevent, destroy, repel, or mitigate pests and is specifically labeled for use by U.S. Environmental Protection Agency (EPA). Also, any substance used as plant regulator, defoliant, disinfectant, or biocide.

    - Planter Bed: An area containing one or combination of following plant types: shrubs, vines, wildflowers, annuals, perennials, ground cover, and mulch topdressing, excluding turf. Trees may also be found in planter beds.

    - Stand of Turf: 100 percent of established species.

  - APPLICABLE PUBLICATIONS

    - Comply with references to extent specified in this section.

    - American National Standards Institute (ANSI):

      - Z60.1-2014 - Nursery Stock.

    - American Society for Testing And Materials (ASTM):

      - B221-14 - Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

      - B221M-13 - Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

      - C33/C33M-16-Concrete Aggregates.

      - C136/C136M-14 - Sieve Analysis of Fine and Coarse Aggregates.

      - C602-13a - Agricultural Liming Materials.

      - D977-13e1 - Emulsified Asphalt.

      - D5268-13 - Topsoil Used for Landscaping Purposes.

    - Hortus Third: Concise Dictionary of Plants Cultivated in United States and Canada.

    - Tree Care Industry Association (TCIA):

      - A300P1-2008 - Tree Care Operations - Trees, Shrubs and Other Woody Plant Maintenance Standard Practices (Pruning).

      - Z133.1-2012 - Arboricultural Operations - Safety Requirements.

    - Turfgrass Producers International (TPI):

      - 2006 Guideline Specifications to Turfgrass Sodding.

    - United States Department of Agriculture (USDA):

      - DOA SSIR 42-2014 - Soil Survey Laboratory Methods Manual.

      - Handbook No. 60 - Diagnosis and Improvement of Saline and Alkali Soils.

  - PREINSTALLATION MEETINGS

    - Conduct preinstallation meeting at project site minimum 30 days before beginning Work of this section.

      - Required Participants:

        - Contracting Officer's Representative.

        - Contractor.

        - Installer.

      - Meeting Agenda: Distribute agenda to participants minimum 3 days before meeting.

        - Inspection of planting materials.

        - Installation schedule.

        - Installation sequence.

        - Preparatory work.

        - Protection before, during, and after installation.

        - Installation.

        - Inspecting.

        - Environmental procedures.

      - Document and distribute meeting minutes to participants to record decisions affecting installation.

  - SUBMITTALS

    - Submittal Procedures: Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

    - Manufacturer's Literature and Data:

      - Description of each product.

      - Photographs: Color photographs of each plant species showing actual size and condition of plants to be provided with measuring device

included for scale. Where more than 20 plants are required of any species, submit minimum three photographs of average, best, and worst quality plant to be provided. Include on each photograph, plant full scientific name, size, and source nursery.

      - Installation instructions.

      - Warranty.

    - Samples:

      - Trees and Shrubs: Full sized of each variety and size. Deliver samples to project site and maintain samples for duration of construction period.

      - Organic and Compost Mulch: 0.5 L. (1 pint) sealed plastic bag of each required mulch, including label with percentage weight of each material and source representing material to be provided. Samples to match color, texture, and composition of installed material.

      - Mineral Mulch: 1.0 kg (2 lb.) sealed plastic bag of mulch, including label with source. Samples to match color, texture, and composition of installed material.

      - Filter Fabric: 300 by 300 mm (12 by 12 inches).

      - Edging Materials and Accessories: Manufacturer's standard sizes.

      - Tree Wrap: Width of panel by 300 mm (12 inches).

    - Test reports: Certify products comply with specifications.

    - Certificates: Certify products comply with specifications.

      - Plant Materials: Department of Agriculture certification by State Nursery Inspector declaring material to be free from insects and disease.

      - Seed and Turf Materials: Notarized certificate of product analysis.

    - Qualifications: Substantiate qualifications comply with specifications.

      - Installer, including supervisor with project experience list.

    - Operation and Maintenance Data:

      - Care instructions for each plant material.

  - QUALITY ASSURANCE

    - Installer Qualifications:

      - Regularly installs specified products.

      - Installed specified products with satisfactory service on five similar installations for minimum five years.

        - Project Experience List: Provide contact names and addresses for completed projects.

      - Member in good standing of either Professional Landcare Network or American Nursery and Landscape Association.

      - Field supervisor certified in categories from Professional Landcare Network and submit one copy of certificate to Contracting Officer’s Representative:

        - Certified Landscape Technician (CLT) - Exterior, with maintenance designated CLT-Exterior.

    - Licensed Arborist required to submit one copy of license to Contracting Officer’s Representative.

    - Independent or university laboratory, recognized by State Department of Agriculture, with experience and capability to conduct testing indicated and that specializes in types of tests to be performed.

    - Measure plants according to ANSI Z60.1. Pruning to obtain required sizes will not be permitted.

    - Contracting Officer’s Representative may review plant materials either at place of growth or project site before planting for compliance with requirements. Contracting Officer’s Representative retains right to inspect trees and shrubs to determine if any unacceptable conditions exist and to reject any trees or shrubs at any time during Project. All rejected trees and shrubs must be immediately removed from Project site.

      - Submit plant material source information to Contracting Officer’s Representative seven in advance of delivery to Project site.

    - Material Test Reports: For standardized ASTM D5268 topsoil existing native surface topsoil existing in-place surface soil and imported or manufactured topsoil.

      - For each unamended soil type, provide soil analysis and written report by qualified soil-testing laboratory stating percentages of organic matter; gradation of sand, silt, and clay content; cation exchange capacity; deleterious material; pH; and mineral and plant-nutrient content of soil.

      - Comply with USDA's Handbook No. 60 testing methods and written recommendations.

      - Soil-testing laboratory to oversee soil sampling; with depth, location, and number of samples to be taken per instructions from Contracting Officer’s Representative. Take minimum 3 representative samples from varied locations for each soil to be used or amended for planting purposes.

      - Report suitability of tested soil for plant growth.

      - Based on test results, state recommendations for soil treatments and soil amendments to be incorporated. State recommendations in weight per 92.9 sq. m (1000 sq. ft.) or volume per 0.76 cu. m (1 cu. yd.) for nitrogen, phosphorus, and potash nutrients and soil amendments to be added to produce satisfactory planting soil suitable for healthy, viable plants.

      - Report presence of problem salts, minerals, or heavy metals, including aluminum, arsenic, barium, cadmium, chromium, cobalt, lead, lithium, and vanadium. If such problem materials are present, provide additional recommendations for corrective action.

  - DELIVERY

    - Deliver packaged products in manufacturer's original sealed packaging.

    - Bulk Products:

      - Deliver bulk products away from buildings, utilities, pavement, and existing turf and planted areas. Maintain dry bulk product storage away from contaminants.

      - Install erosion control materials to prevent erosion or displacement of bulk products.

    - Apply antidesiccant to trees and shrubs according to manufacturer's instructions to protect during digging, handling, and transportation.

      - For deciduous trees or shrubs in full leaf, spray with antidesiccant at nursery before transporting and again two weeks after planting.

    - Wrap trees and shrubs with tree wrap according to manufacturer's instructions to protect from wind and other damage during digging, handling, and transportation.

    - Deliver bare-root stock plants freshly dug with root system packed in wet straw, hay, or similar material.

    - Deliver branched plants with branches tied and exposed branches covered with material that allows air circulation. Prevent damage to branches, trunks, root systems, and root balls and desiccation of leaves.

    - Use of equipment such as "tree spades" is permitted provided plant balls are sized according to ANSI Z60.1 and tops are protected from damage.

  - STORAGE AND HANDLING

    - Store bulbs, corms, and tubers in dry location at 16 to 18 degrees C (60 to 65 degrees F) until planting.

    - Store seeds and other packaged materials in dry locations away from contaminants.

    - Plant Storage and Protection: Store and protect plants not planted on day of arrival at Project site as follows:

      - Shade and protect plants in outdoor storage areas from wind and direct sunlight until planted.

      - Heel-in bare root plants.

      - Protect balled and burlapped plants from freezing or drying out by covering balls or roots with moist burlap, sawdust, wood chips, shredded bark, peat moss, or other approved material. Provide covering that allows air circulation.

      - Keep plants in moist condition until planted by watering with fine mist spray.

      - Do not store plant materials directly on concrete or bituminous surfaces.

    - Topsoil: Before stockpiling topsoil, eradicate on site undesirable growing vegetation. Clear and grub existing vegetation three to four weeks before stockpiling existing topsoil.

    - Root Control Barrier and Weed Control Fabric: Store materials in site in enclosures or under protective covering in dry location out of direct sunlight. Do not store materials directly on ground.

    - Handling: Do not drop or dump plants from vehicles. Avoid damaging plants being moved from nursery or storage area to planting site. Handle balled and potted plants carefully to avoid damaging or breaking earth ball or root structure. Do not handle plants by trunk or stem. Puddle bare-root plants after removal from heeling-in bed to protect roots from drying out. Remove damaged plants from Project site.

  - FIELD CONDITIONS

    - Environment:

      - Coordinate installation of planting materials during optimal planting seasons for each type of plant material required.

      - Planting Dates: As approved by VA schedule in the fall and spring season.

      - Restrictions: Do not plant when ground is frozen, snow covered, muddy, or when air temperature exceed 32 degrees C (90 degrees F).

    - Weather Limitations: Install plantings only during current and forecasted weather conditions that are comply with plant requirements. Apply associated products in compliance with manufacturers' instructions.

  - WARRANTY

    - Construction Warranty: FAR clause 52.246-21, "Warranty of Construction."

    - Manufacturer's Warranty: Warrant plantings and against material defects.

      - Warranty Period: Two years.

      - Plant and Turf Warranty Periods will begin from date of planting completion.

      - Contracting Officer's Representative will reinspect plants and turf at end of Warranty Period. Replace any dead, missing, or defective plant material and turf immediately. Warranty Period will end on date of this inspection provided Contractor has complied with warranty work required by this specification. Comply with following requirements:

        - Replace any plants more than 25 percent dead, missing or defective plant material before final inspection.

        - Only one replacement of each plant will be required except when losses or replacements are due to failure to comply with these requirements.

        - Complete remedial measures directed by Contracting Officer’s Representative to ensure plant and turf survival.

        - Repair damage caused while making plant or turf replacements.

PART 2 - PRODUCTS

  - PRODUCTS - GENERAL

    - Provide each product from one source or manufacturer.

  - PLANT MATERIALS

    - Plant Materials: ANSI Z60.1, conforming to varieties specified and be true to scientific name as listed in Hortus Third. Well-branched,

well-formed, sound, vigorous, healthy planting stock free from disease, sunscald, windburn, abrasion, and harmful insects or insect eggs and having healthy, normal, and undamaged root system.

      - Trees-Deciduous and Evergreen: Single trunked with single leader, unless otherwise indicated; symmetrically developed deciduous trees and shrubs of uniform habit of growth; straight boles or stems; free from objectionable disfigurements; evergreen trees and shrubs with well-developed symmetrical tops, with typical spread of branches for each particular species or variety. Trees with damaged, crooked, or multiple leaders; tight vertical branches where bark is squeezed between two branches or between branch and trunk; crossing trunks; cut-off limbs more than 19 mm (3/4 inch) in diameter; or with stem girdling roots will be rejected.

      - Ground Cover and Vine Plants: Provide number and length of runners for size specified on drawings, together with proper age for grade of plants specified. Provide vines and ground cover plants well established in removable containers, integral containers, or formed homogeneous soil sections. Provide plants grown under climatic conditions similar to those in locality of project. Spray all plants budding into leaf or having soft growth with an anti-desiccant at nursery before digging.

      - Provide plants of sizes indicated, measured before pruning with branches in normal position. Plants larger in size than specified is acceptable with approval of Contracting Officer’s Representative, with no change in contract price. When larger plants are used, increase ball of earth or spread of roots according to ANSI Z60.1.

      - Provide nursery grown plant material conforming to requirements and recommendations of ANSI Z60.1. Dig and prepare plants for shipment in manner that will not cause damage to branches, shape, and future development after planting.

      - Balled and burlapped (B&B) plant ball sizes and ratios will conform to ANSI Z60.1, consisting of firm, natural balls of soil wrapped firmly with burlap or strong cloth and tied.

      - Bare root (BR) plants to have root system substantially intact, but with earth carefully removed. Cover roots with thick coating of mud by "puddling" after plants are dug.

      - Container grown plants to have sufficient root growth to hold earth intact when removed from containers, but not be root bound.

      - Make substitutions only when plant (or alternates as specified) is not obtainable and Contracting Officer’s Representative authorizes change order providing for use of nearest equivalent obtainable size or variety of plant with same essential characteristics and an equitable adjustment of contract price.

      - Existing plants to be relocated: Ball sizes to conform to requirements for collected plants in ANSI Z60.1, and plants dug, handled, and replanted according to applicable articles of this Section.

      - Only plants grown in nursery are permitted.

    - Label plants with durable, waterproof labels in weather-resistant ink. Provide labels stating correct botanical and common plant name and variety and size as specified in list of required plants. Groups of plants may be labels by tagging one plant. Labels to be legible for minimum 60 days after delivery to planting site.

  - SOD

    - Sod: Nursery grown, certified and classified in TPI's "Guideline Specifications to Turfgrass Sodding" as GSS. Machine cut sod at uniform thickness of 19 mm (3/4 inch) within tolerance of 6 mm (1/4 inch), excluding top growth and thatch. Each individual sod piece to be strong enough to support its own weight when lifted by ends. Broken pads, irregularly shaped pieces, and torn or uneven ends will not be permitted.

    - Sod Species: Genetically pure, free of weeds, pests, and disease.

      - Full Sun: Match existing minimum of 3 cultivars.

      - Sun and Partial Shade: Proportion grass species as follows:

        - Match existing.

      - Shade: Proportion grass species as follows:

        - Match existing.

  - SEED

    - Grass Seed: State-approved seed of latest season's crop delivered in original sealed packages, bearing producer's guaranteed analysis for percentages of mixtures, purity, germination, weed seed content, and inert material. Label in conformance with AMS Seed Act and applicable state seed laws. Wet, moldy, or otherwise damaged seed will not be acceptable. Field mixes will be acceptable when field mix is performed on site in presence of Contracting Officer's Representative.

    - Seed Mixtures: Proportion seed mixtures by weight.

      - Full Sun: Match existing seed mixtures.

  - TURF SELECTIONS

    - Grasses for Cool Regions:

      - Bentgrasses: Redtop (Agrostis alba) and Colonial (Agrostis tenuis).

      - Bluegrasses: Kentucky (Popratensis), Rough-stalked (Potrivialis) and Canada(Poa compressa).

      - Fescue: Red (Festucrubra), Meadow (Festucpratensis) and Tall (Festucarundinacea).

      - Ryegrasses: Perennial (Lolium perenne).

    - Grasses for Warm Regions:

      - Bermuda grass (Cynodon dactylon).

      - Carpetgrass (Axonopus affinis).

      - Centipedegrass (Eremochloophiuroides).

      - St. Augustinegrass (Stenotaphrum secundatum).

      - Zoysiagrass (Zoysimatrella).

  - SPRIGS

    - Sod Sprigs: Healthy living stems, stolons, or rhizomes and attached roots of locally adapted grass without adhering soil, including two to three nodes and from 100 to 150 mm (4 to 6 inches) long. Obtain from heavy, dense certified sod classified as TPI GSS. // Obtain sprigs from designated area on project site. // Provide sprigs grown under climatic conditions similar to those of project site. Coordinate harvesting and planting to prevent sun exposure for more than 30 minutes before covering and moistening. Sprigs containing weeds or other detrimental material or that are heat damaged will be rejected.

  - PLUGS

    - Plugs: Nursery grown sod, certified and classified in TPI's "Guideline Specifications to Turfgrass Sodding" as GSS.

    - Square or round sections with deep, mature root system.

      - Species to match adjacent sod.

      - Plug Size: 50 mm (2 inches) by 50 mm (2 inches).

  - PLANTING SOILS

    - Planting Soil: Evaluate soil for use as topsoil according to ASTM D5268. From 5 to 10 percent organic matter as determined by

topsoil composition tests of Organic Carbon, 6A, Chemical Analysis Method described in USDA DOA SSIR 42. Maximum particle size, 19 mm (3/4 inch), with maximum 3 percent retained on 6 mm (1/4 inch) screen. Mix topsoil with following soil amendments as recommended by soils analysis.

    - Existing Planting Soil: Existing, native surface topsoil formed under natural conditions retained during excavation process and stockpiled

on-site. Verify suitability of native surface topsoil to produce viable planting soil. Clean soil of roots, plants, sod, stones, clay lumps, and other extraneous materials harmful to plant growth.

      - Supplement with another specified planting soil when quantities are insufficient.

      - Mix existing, native surface topsoil with soil amendments and fertilizers as recommended by soils analysis.

    - Imported Planting Soil: Imported topsoil or manufactured topsoil from off-site sources are acceptable if sufficient topsoil is not available on site to meet specified depth. At least 10 days before topsoil delivery, notify Contracting Officer’s Representative of topsoil sources. Obtain imported topsoil displaced from naturally well-drained construction or mining sites where topsoil is at least 100 mm

(4 inches) deep. Topsoil from agricultural land, bogs, or marshes will be rejected.

  - PLANT FERTILIZERS

    - Soil Test: Evaluate existing soil conditions and requirements before fertilizer selection and application to minimize use of all fertilizers and chemical products. Obtain approval of Contracting Officer’s

Representative for allowable products, product alternatives, scheduling and application procedures. Evaluate existing weather and site conditions before application. Apply products during favorable weather and site conditions according to manufacturer's instructions and warranty requirements. Fertilizers to be registered and approved by EPA, acceptable to authorities having jurisdiction, and of type recommended by manufacturer applicable to specific areas as required for Project conditions and application. Provide commercial grade plant and turf fertilizers, free flowing, uniform in composition and conforms to applicable state and federal regulations.

    - Fertilizer for groundcover, wildflowers, and grasses is not acceptable. Provide fertilizer for trees, plants, and shrubs as recommended by plant supplier, except synthetic chemical fertilizers are not acceptable. Fertilizers containing petrochemical additives or that have been treated with pesticides or herbicides are not acceptable.

    - Granular Fertilizer: Organic, granular controlled release fertilizer containing minimum percentages, by weight, of plant food nutrients.

      - Composition: Nitrogen, phosphorous, potassium, sulfur, and iron in amounts recommended in soil reports from qualified soil-testing laboratory.

    - Fertilizer Tablets: Organic plant tablets composed of tightly compressed fertilizer chips, insoluble in water, to provide continuous release of nutrients for minimum 24 months and containing following minimum percentages, by weight, of plant food nutrients:

      - Nutrient Composition: 20 percent available nitrogen, 20 percent available phosphorous, and 5 percent available potassium.

  - WEED CONTROL FABRIC

    - Roll Type Polypropylene or Polyester Mats: Woven, needle punched, or non-woven fabric treated for protection against deterioration due to ultraviolet radiation. Minimum 99 percent opaque to prevent photosynthesis and seed germination, fabric allows air, water, and nutrients to pass through to plant roots.

      - Minimum weight: 0.11 kg per square meter (5 ounces per square yard).

      - Minimum thickness: 0.50 mm (20 mils).

  - MULCH

    - Organic Mulch:

      - Match Existing -Wood cellulose fiber wood chops ground or shredded bark shredded hardwood bark peelings pine straw mulch pine needles for project site when available. Biobased content minimum 100 percent. Wood cellulose fiber processed to contain no growth or germination-inhibiting factors, dyed with non-toxic, biodegradable dye to an appropriate color to facilitate visual metering of application.

        - Straw for Lawn Seed Bed Mulch: Stalks from oats, wheat, rye, barley, or rice free of noxious weeds, mold or other objectionable material. Air dried and suitable for placing with blower equipment.

        - Wood cellulose fiber for hydraulic application of grass seed and fertilizer: Specially prepared wood cellulose fiber, processed to contain no growth or germination inhibiting factors, and dyed an appropriate color to facilitate visual metering of application of materials. Maximum 12 percent moisture dry weight, plus or minus 3 percent at time of manufacture. pH range from 3.5 to 5.0. Manufacturer wood cellulose fiber for application as follows:

          - After addition and agitation in slurry tanks with fertilizers, grass seeds, water, and other approved additives, fibers will become uniformly suspended to form a homogeneous slurry.

          - When hydraulically sprayed, material will form blotter-like cover impregnated uniformly with grass seed.

          - Cover will allow absorption of moisture and allow rainfall or applied water to percolate to underlying soil.

      - Color: Natural.

    - Compost Mulch: Decomposed organic matter with low carbon to nitrogen ratio.

    - Mineral Mulch: Coarse, clean stone of following type, size, and color:

      - Type: Decomposed granite pea gravel .

      - Size: ASTM C136/C136M, 65 mm (2-1/2 inches) maximum and 25 mm (1 inch) minimum.

      - Color: Acceptable to Contracting Officer’s Representative.

  - ANTIDESICCANT

    - Antidesiccant: An emulsion specifically manufactured for agricultural use that will provide protective film over plant surfaces permeable enough to permit transpiration.

  - ROOT CONTROL BARRIER

    - Root Control Barrier: Flexible and permeable geotextile fabric with permanently attached time-release nodules. Pre-formed round, barrier with integral vertical root deflecting ribs constructed of ultraviolet resistant polypropylene material.

  - BIOSTIMULANTS

    - Biostimulants: Formulation containing soil conditioners, VAM fungi, and endomycorrhizal and ectomycorrhizal fungi spores and soil bacteria appropriate for existing soil conditions.

  - TACKIFIERS AND ADHESIVES

    - Nonasphalt Tackifier: Colloidal liquid fixative recommended by fiber mulch manufacturer for hydroseeding.

    - Asphalt emulsion: ASTM D977, Grade SS-1.

  - WATER

    - Water: Source approved by Contracting Officer's Representative and suitable quality for irrigation, containing no elements toxic to plant life, including acids, alkalis, salts, chemical pollutants, and organic matter. Use collected storm water or graywater when available.

  - PESTICIDES

    - Consider IPM (Integrated Pest Management) practices to minimize use of all pesticides and chemical products. Obtain Contracting Officer's Representative's approval for allowable products, product alternatives, scheduling and application procedures. Evaluate existing weather and site conditions before application. Apply products during favorable weather and site conditions according to manufacturer's instructions and warranty requirements.

PART 3 - EXECUTION

  - EXAMINATION

    - Examine areas to receive plants for compliance with requirements and conditions affecting installation and performance.

      - Verify that no materials that would inhibit plant growth are present in planting area. If such materials are present, remove soil and contaminants ad directed by Contracting Officer's Representative and provide new planting soil.

      - Do not mix or place soils and soil amendments in frozen, wet, or muddy conditions.

      - Suspend soil spreading, grading, and tilling operations if soil moisture becomes excessive. Resume soil preparations when moisture content returns to acceptable level.

      - If soil is excessively dry, not workable, and too dusty, moisten uniformly.

      - Special conditions may exist that warrant variance in specified planting dates or conditions. Submit written request to Contracting Officer’s Representative stating special conditions and proposed variance.

    - Proceed with planting operations only after unsatisfactory conditions have been corrected.

  - PREPARATION

    - Protect existing and proposed landscape features, elements, and site construction and completed work from damage. Protect trees, vegetation, and other designated features by erecting high-visibility, reusable construction fencing. Locate fence no closer to trees than drip line. Plan equipment and vehicle access to minimize and confine soil disturbance and compaction to areas indicated on drawings.

    - Install erosion control materials at all areas inside or outside limits of construction that are disturbed by planting operations. Provide erosion control and seeding with native plant species to protect slopes.

  - GROUND COVER AND PLANT INSTALLATION

    - Place ground cover and plants, not including trees, shrubs, and vines,

225 mm (9 inches) apart in even rows and with triangular spacing.

    - Use prepared soil mixture for backfill.

    - Place so roots are in natural position.

    - Do not remove plants from flats or containers until immediately before planting. Plat at depth to sufficiently cover all roots. Start watering areas planted as required by temperature and wind conditions. Water plants at sufficient rate to ensure thorough wetting of soil to 150 mm (6 inches) deep without runoff or puddling. Smooth planting areas after planting to provide even, smooth finish.

    - Plant ground cover in areas to receive erosion control materials through material after erosion control materials are in place.

  - TREE, SHRUB, AND VINE PLANTING

    - Move plant materials only by supporting root ball. Set plants on hand compacted layer of prepared backfill soil mixture 150 mm (6 inches) thick and hold plumb in center of pit until soil has been tamped firmly around root ball.

    - Set plant materials in relation to surrounding finish grade 25 to 50 mm (1 to 2 inches) above depth at which they were grown in nursery, collecting field, or container. Replace plant material whose root balls are cracked or damaged either before or during planting process.

    - Place backfill soil mixture on previously scarified subsoil to completely surround root balls and bring to smooth and even surface, blending into existing areas.

    - Balled and Burlapped Stock: Backfill with // prepared soil mixture // topsoil // to approximately half ball depth then tamp and water. Carefully remove or fold back excess burlap and tying materials from top to minimum 1/3 depth from top of root ball. Tamp and complete backfill, place mulch topdressing, and water. Remove wires and

non-biodegradable materials from plant pit before backfilling.

  - TREE AND SHRUB PRUNING

    - Pruning: Performed by trained and experience personnel according to TCIA A300P1.

    - Remove dead and broken branches. Prune only to correct structural defects.

    - Retain typical growth shape of individual plants with as much height and spread as practical. Do not central leader on trees. Make cuts with

sharp instruments. Do not flush cut with trunk or adjacent branches. Collars to remain in place.

    - Do not apply tree wound dressing to cuts.

  - MULCH INSTALLATION

    - Provide specified mulch over entire planting bed surfaces and individual plant surfaces, including earth mount watering basin around plants, to 75 mm (3 inches) depth after plant installation and before watering. Do not place mulch in crowns of shrubs. Place mulch minimum

50 to 75 mm (2 to 3 inches) away from tree or shrub trunks. Place mulch on all weed control fabric.

  - SPRIGGING

    - Plant sod sprigs after finish grade is properly prepared and thoroughly soaked day in advance. Plant sprigs in rows spaced maximum 300 mm

(12 inches) apart with springs placed in rows at maximum 150 mm

(6 inches) apart. Firm entire area with roller not exceeding 130 kg/m (90 lb./ft.)of roller width. Do not roll slopes over maximum 3: 1.

Water thoroughly and keep soil moist. Weed by hand or hoe. Do not treat sprig area with herbicide.

  - PLUGGING

    - Plant fresh sod plugs after finish grade is properly prepared. Plant plugs in rows, spaced 300 mm (12 inches) apart in both directions. On slopes, contour rows to near level. Water thoroughly and keep soil moist. Weed by hand or hoe. Do not treat plug area with herbicide.

  - SEEDING

    - Broadcast and Drop Seeding: Uniformly broadcast seed at rate of 30 pounds per acre. Use broadcast or drop seeders. Sow one-half seed in one direction and sow remainder at right angles to first sowing. Cover seed uniformly to maximum 6 mm (1/4 inch) deep in clay soils and 13 mm (1/2 inch) deep in sandy soils by means of spike-tooth harrow, cultipacker, raking, or other approved device.

  - TURF RENOVATION

    - General: Restore to original condition existing turf areas damaged during turf installation and construction operations. Keep at least one paved pedestrian access route and one paved vehicular access route to

each building clean at all times. Clean other paving when work in adjacent areas is complete.

    - Aeration: Eradicate weeds and, with Contracting Officer's Representative's approval to proceed, aerate turf areas with approved device. Leave all soil plugs that are produced, in turf area. After aeration operations are complete, topdress entire area 6.35 mm

(1/4 inch) deep. Blend all parts of topdressing mixture to uniform consistency. Clean all soil plugs off of other paving when work is complete.

    - Overseeding: Apply seed according to applicable portions of "Seed Application Method" at rates specified in "Seed Composition."

  - PLANT MAINTENANCE

    - Frequency: Begin maintenance immediately after plants have been installed. Inspect plants at least once week and perform required maintenance promptly.

    - Promotion of Plant Growth and Vigor: Water, prune, fertilize, mulch, eradicate weeds, and perform other operations necessary to promote plant growth and vigor.

    - Planter Beds: Weed, fertilize, and irrigate planter beds and keep pest free, pruned, and mulch levels maintained. Do not permit planter beds encroach into turf areas. Maintain edging breaks between turf areas and planter beds. Fertilize plant materials to promote healthy growth without encouraging excessive top foliar growth. Remove noxious weeds common to area from planter beds by mechanical means.

    - Shrubs: In addition to planter bed maintenance requirements, selectively prune and shape shrubs for health and safety when following conditions exist:

      - Remove growth in front of windows, over entrance ways or walks, and any growth which will obstruct vision at street intersections or of security personnel.

      - Remove dead, damaged, or diseased branches or limbs where shrub growth obstructs pedestrian walkways, where shrub growth is growing against or over structures, and where shrub growth permits concealment of unauthorized persons.

      - Properly dispose of all pruning debris.

    - Trees: Adjust stakes, ties, guy supports and water, fertilize, control pests, mulch, and prune for health and safety .

      - Fertilize trees to promote healthy plant growth without encouraging excessive top foliar growth. Inspect and adjust stakes, ties, guy supports to avoid girdling and promote natural development.

      - Selectively prune all trees within project boundaries, regardless of caliper, for safety and health reasons, including, but not limited to, removal of dead and broken branches and correction of structural defects. Prune trees according to their natural growth characteristics leaving trees well shaped and balanced.

      - All pruning, including palm tree pruning, must be by or in presence of certified member of International Society of Arboriculture and according to TCIA Z133.1.

      - Properly dispose of all pruning debris.

  - REMOVAL OF DYING OR DEAD PLANTS

    - Remove dead and dying plants and provide new plants immediately upon commencement of specified planting season and replace stakes,

guys, mulch, and eroded earth mound water basins. No additional correction period will be required for replacement plants beyond original warranty period. Plants will be considered dead or dying as follows:

      - Tree: Main leader died back or minimum 20 percent of crown died.

      - Shrub and Ground Cover: Minimum 20 percent of plant died.

      - Determination: Scrape on maximum 2 mm (1/16 inch) square branch area to determine dying plant material cause and provide recommendations for replacement.

  - TURF MAINTENANCE

    - Mow turf to uniform finished height measured from soil. Perform mowing in manner that prevents scalping, rutting, bruising, uneven and rough cutting. Before mowing, remove and dispose of all rubbish, debris, trash, leaves, rocks, paper, and limbs or branches on turf areas. Sweep or vacuum clean adjacent paved areas.

    - Apply fertilizer in manner that promotes health, growth, vigor, color and appearance of cultivated turf areas. Determine method of application, fertilizer type and frequencies by results of laboratory

soil analysis. Apply fertilizer by approved methods and according to manufacturer's instructions.

    - Watering: Perform irrigation in manner that promotes health, growth, color, and appearance of cultivated vegetation, complying with Federal, State, and local water agency and authority directives. Prevent overwatering, water run-off, erosion, and ponding due to excessive quantities or rate of application.

  - CLEANING

    - Remove and legally dispose of all excess soil and planting debris.

  - PROTECTION

    - Protect plants from traffic and construction operations.

    - Provide temporary fences or enclosures and signage, at planted areas. Maintain fences and enclosures during maintenance period.

    - Remove protective materials immediately before acceptance.

    - Repair damage.

- - - E N D - - -