| SUBJECT* | Triennial Electrical Inspection for VA Wilkes-Barre |
| --- | --- |

GENERAL INFORMATION

| CONTRACTING OFFICE’S ZIP CODE* | 19104 |
| --- | --- |
| SOLICITATION NUMBER* | 36C24426Q0250 |
| RESPONSE DATE/TIME/ZONE | 04-03-2026 15:00 EASTERN TIME, NEW YORK, USA |
| ARCHIVE | 30 DAYS AFTER THE RESPONSE DATE |
| RECOVERY ACT FUNDS | N |
| SET-ASIDE | SDVOSBC |
| PRODUCT SERVICE CODE* | J061 |
| NAICS CODE* | 238210 |
| CONTRACTING OFFICE ADDRESS | Department of Veterans Affairs Network Contracting Office 4 Services 2 3900 Woodland Ave. Philadelphia, PA 19104 |
| POINT OF CONTACT* | Contract Specialist Allan Tabliago allan.tabliago@va.gov (732) 978-0110 |

PLACE OF PERFORMANCE

| ADDRESS | Department of Veteran Affairs |
| --- | --- |
|  | Wilkes-Barre VA Medical Center |
|  | 1111 East End Boulevard |
|  | Wilkes-Barre PA |
| POSTAL CODE | 18711-0030 |
| COUNTRY |  |

ADDITIONAL INFORMATION

| AGENCY’S URL |  |
| --- | --- |
| URL DESCRIPTION |  |
| AGENCY CONTACT’S EMAIL ADDRESS |  |
| EMAIL DESCRIPTION |  |

DESCRIPTION

5. PROJECT NUMBER (if applicable)

CODE

7. ADMINISTERED BY

2. AMENDMENT/MODIFICATION NUMBER

CODE

6. ISSUED BY

8. NAME AND ADDRESS OF CONTRACTOR

4. REQUISITION/PURCHASE REQ. NUMBER

3. EFFECTIVE DATE

9A. AMENDMENT OF SOLICITATION NUMBER

9B. DATED

PAGE        OF     PAGES

10A. MODIFICATION OF CONTRACT/ORDER NUMBER

10B. DATED

BPA NO.

1. CONTRACT ID CODE

FACILITY CODE

CODE

Offers must acknowledge receipt of this amendment prior to the hour and date specified in the solicitation or as amended, by one of the following methods:

The above numbered solicitation is amended as set forth in Item 14.  The hour and date specified for receipt of Offers

E. IMPORTANT:

is extended,

(a) By completing Items 8 and 15, and returning __________ copies of the amendment; (b) By acknowledging receipt of this amendment on each copy of the

offer submitted; or (c) By separate letter or electronic communication which includes a reference to the solicitation and amendment numbers.  FAILURE OF YOUR

ACKNOWLEDGMENT TO BE RECEIVED AT THE PLACE DESIGNATED FOR THE RECEIPT OF OFFERS PRIOR TO THE HOUR AND DATE SPECIFIED MAY

is not extended.

12. ACCOUNTING AND APPROPRIATION DATA

(REV. 11/2016)

is required to sign this document and return ___________ copies to the issuing office.

is not,

A. THIS CHANGE ORDER IS ISSUED PURSUANT TO:    (Specify authority)   THE CHANGES SET FORTH IN ITEM 14 ARE MADE IN THE CONTRACT ORDER NO. IN ITEM 10A.

15C. DATE SIGNED

B. THE ABOVE NUMBERED CONTRACT/ORDER IS MODIFIED TO REFLECT THE ADMINISTRATIVE CHANGES

SET FORTH IN ITEM 14, PURSUANT TO THE AUTHORITY OF FAR 43.103(b).

RESULT IN REJECTION OF YOUR OFFER.  If by virtue of this amendment you desire to change an offer already submitted, such change may be made by letter

or electronic communication, provided each letter or electronic communication makes reference to the solicitation and this amendment, and is received prior to

the opening hour and date specified.

C. THIS SUPPLEMENTAL AGREEMENT IS ENTERED INTO PURSUANT TO AUTHORITY OF:

D. OTHER

Contractor

16C. DATE SIGNED

14. DESCRIPTION OF AMENDMENT/MODIFICATION

16B. UNITED STATES OF AMERICA

Except as provided herein, all terms and conditions of the document referenced in Item 9A or 10A, as heretofore changed, remains unchanged and in full force and effect.

15A. NAME AND TITLE OF SIGNER

16A. NAME AND TITLE OF CONTRACTING OFFICER

15B. CONTRACTOR/OFFEROR

STANDARD FORM 30

PREVIOUS EDITION NOT USABLE

Prescribed by GSA - FAR (48 CFR) 53.243

(Type or print)

(Type or print)

(Organized by UCF section headings, including solicitation/contract subject matter where feasible.)

(Number, street, county, State and ZIP Code)

(If other than Item 6)

(Specify type of modification and authority)

(such as changes in paying office, appropriation date, etc.)

(If required)

(SEE ITEM 11)

(SEE ITEM 13)

(X)

CHECK

ONE

13. THIS ITEM APPLIES ONLY TO MODIFICATIONS OF CONTRACTS/ORDERS,

IT MODIFIES THE CONTRACT/ORDER NO. AS DESCRIBED IN ITEM 14.

11. THIS ITEM ONLY APPLIES TO AMENDMENTS OF SOLICITATIONS

AMENDMENT OF SOLICITATION/MODIFICATION OF CONTRACT

(Signature of person authorized to sign)

(Signature of Contracting Officer)

3

5

0004

03-27-2026

None

36C244

Department of Veterans Affairs

Network Contracting Office 4

Services 2

3900 Woodland Ave.

Philadelphia PA 19104

36C244

Department of Veterans Affairs

Network Contracting Office 4

To all Offerors/Bidders

36C24426Q0250

X

X

X

** HOUR & DATE for Receipt of Offers is EXTENDED to: 04-03-2026 15:00 EDT

1. The purpose of this amendment is to post RFI responses and extend the RFQ due date.

2. The RFQ due date is changed from 03/27/26 at 15:00 EST to 04/03/26 at 15:00 EST.

3. Please see attached for RFI responses on page 4.

Stephanie Luniewski

Contracting Officer

Amendment 0001

36C24426Q0250--Triennial Electrical Inspection at VA Wilkes-Barre

- Will the VA provide a copy of the single line drawings for quoting?  The AF Study information does not provide the pertinent information.

Response: Attachment 5 Power Study Drawing 1-22 provides all single line drawings for facility.

- Can the VA extend the deadline to allow quotes to be received from the Utility Company?

Response: The RFQ due date has been extended to 03/13/2026 by 3:00 PM EST.

- Will the VA provide the schedule utilized in the previous cycle?  At minimum can the VA provide the total number of weekends needed to complete the previous cycle?

Response: Previous schedules and amount of weekends/shutdowns all varied, depending on size of crew or multiple crews provided by contractor. Multiple crews working at once led to less shutdowns/ weekend worked.

- Can the VA provide the previous contract number(s) for the triennial electrical testing services?

Response: Previous contracts can be found on the USAspending.gov website. 36C24421P0077 and VA244-17-P-2715 are the previous contract numbers.

- Is this just to de-energize the service?  If so is it for one service, or both services?  We will need that to determine the number of crews and type of equipment required.  Also, what day will the work be performed on?

Response: No, this contract is not just to de-energize electrical services, over multiple days of testing and maintenance of all major circuit breakers for 3 substations as well as other electrical equipment will take place.

- RFQ states all work must be completed 6 months from award of contract; when is the contract expected to be awarded?  Is this for completion in 2026 or roll into 2027?

Response: Completion is 12 months from the award. Performance Period changed from 6 to 12 months.

- How long after award of bid will the Schedule be required for submittal & review? Response: After award contractor will work with VA Maintenance staff to build schedule. Schedule is due within 30 days after award.

- Can IR Scan work be performed on Weekday schedule or does this need to be weekend work as well?

Response: IR scan can be completed during the week, during normal VA hours.

- Will facility provide qualified personnel to escort our Thermographers throughout the facility and remove/install covers to help expedite the IR Scanning?

Response: VA will have escorts to give access to electrical closets and substations, but VA personnel are not responsible for removing electrical covers.

- Statement of Work states all equipment in Attachment 1 t be IR Scanned.  I assume there are IR ports in the MV & Equipment to allow scanning and still abide by NFPA70.E You want all IR Scan to be within safety standards correct? Response: Most MV electrical equipment has IR port, some do not. If it has an IR port scan it, if not report it.

- Section B2 – Statement of work 3.9 4-Hour Power Outage Test:  Note: The 4-hour test must be conducted during moderate outdoor air temperature so that a reasonable indoor air temperature can be maintained. Past testing has been conducted in early spring or fall. Will ALL three Generators be addressed on the same outage or is individual required?

Response: All three generators will run during this 4-hour outage with a load bank on each.

- Besides NETA Certifications, what site requirements will our Techs be required to meet?

Response: No, they need to submit all certifications referenced in the RFQ in the deliverables section and evaluation section.

- PTI has a standard Safety Meeting and Lockout Tagout (LOTO) procedure before ALL our jobs.  Is there site safety video(s) or class beyond our standard that will be required prior to beginning of work?

Response: There will be no videos or class that will be required, just standard safety meetings and LOTO procedures.

- How many shutdowns (weekends) do you anticipate to complete the PM Services?  What has been the number of shutdowns in previous cycles?

Response: The amount of shutdowns/weekends have varied in the past, it will all depend on the size of the crews working from the contractor. Previous testing if there were multiple crews working at once led to less shutdowns/weekends worked.

- Included in the package are pages of setting information.  PTI will not make setting adjustments without authorization. Are you looking for us to confirm settings per the attachment?  Or are you looking for us to make modifications / adjust settings per the attachment?  Please clarify

Response: Attachment 4 Protective Device Setting Adjustments. Settings to be adjusted if proposed as per the attachment. Settings determined from previous electrical study.

- Will there be power (120Vac) available for our testing equipment during de-energized portion of our PM & Testing?

Response: Yes, there will be power available.

- Will there be lighting in the substations during our testing equipment during de-energized portion of our PM & Testing?

Response: Yes, there will be lighting in the substations.

- Do we need to provide small generators & lights for our own use?

Response: No, there will be power available for lighting and equipment.

- We are asking for an RFI extension of 2 days extra. Is this possible?

Response: The RFQ due date has been extended to 03/13/2026 by 3:00 PM EST.

- All other VAAR 852.219-75 Limitations on Subcontracting have been (iii) Special trade construction contractors at the 75% requirement consistent with NAICS Code 238210 and nature of execution of contract that requires maintenance and repairs.

Request VA confirm that this solicitation, under 238 NAICS code is designated Special trade construction contractors at the limit of 75% and not Services at the limit of 50%.

Response: The NAICS Code for this project is changed to 811310 Commercial and Industrial Machinery and Equipment (except Automotive and Electronic) Repair and Maintenance via this amendment.

End of Document

.

End of Document