Solicitation Questions and Answers

| # | SOW Reference | Question | Answer |
| --- | --- | --- | --- |
| 1. | Solicitation | Does the Owner intend to issue an ST-3 form confirming tax exempt status? | No, please reference solicitation for 52.229-3 |
| 2. | Division 34 | The pipe bollard details on EK501 do not appear to meet ASTM F2656 as called out in Spec. 34 71 13. Please clarify? | Use detail 4 of sheet EK501 of a removable bollard |
| 3. | Division 26 | Are photographs available identifying primary and secondary connection bays for all transformers, including substations? | Yes, photos are available for most of the transformers with the bay doors open which show the connections. |
| 4. | Division 26 | Are there any vaults on-site that are not indicated on the contract drawings? | No vaults at transformers. |
| 5. | Division 26 | For the 35KV primary terminations, which existing type/brand is used? | Unknown |
| 6. | ES101- General Note | What factors other than length of primary MV conductors would dictate a change? | No other are known at this time. |
| 7. | Division 26 | What wiring methods are currently in place for primary cabling per location (eg. duct bank, multicell, direct bury, ect.)? | Duct bank |
| 8. | Division 26 | If new cabling is required on medium voltage primary, can existing wiring method be used? | Yes, use existing wiring methods. |
| 9. | Division 26 | Are photographs available of transformer nameplates for all units scheduled for replacement? | Yes, photos are available for most of the transformers with the bay doors open which show the nameplates Available photographs are provided with the answer. |
| 10. | General | What is the maximum allowable building outage duration for transformer replacement activities? | This will vary with transformer and building use. |
| 11. | General | Will transformer shutdowns be required to occur outside of normal working hours? | Please see included description of the outage options for each building. |
| 12. | General | Is temporary or backup power required during transformer replacement operations? | Will depend on required outage duration. Many buildings have emergency power available via generator. See list of building-by-building requirements. |
| 13. | General | Who is responsible for switching operations required to isolate transformers for replacement? | VA staff with either open our MV loop, or de-energize the transformer, as required. Contractor will place their Lockout devices for the duration of their work. Coordinate at least 2 weeks in advance with COR. |
| 14. | Division 26 | Transformer TF-50 has external components attached. Please confirm whether this equipment is active and if it is to be replaced as part of this scope. | This is part of a metering system and should be salvaged and installed on the new transformer (unless this transformer is deducted) |
| 15. | Division 1 | Can the Site Superintendent also cover the position of Quality Control and SSHO? Or do they need to be individual roles | Yes, they can serve multiple roles as long as qualified. |
| 16. |  | Can the Site Superintendent also serve as the Quality Control Manager (QCM) for this project, provided all qualifications are met, or does the Government require these to be separate individuals? | Yes, they can serve multiple roles as long as qualified. |
| 17. |  | If a contractor is currently performing work on the St. Cloud VA Campus under a separate contract, would the Government permit the same individual to serve as the Site Superintendent or Site Safety and Health O.icer (SSHO) for this project, or are these roles required to be dedicated exclusively to this contract? | The site superintendent would need to be a dedicated to this project during construction. |
| 18. |  | Please confirm that all existing transformer pads designated to remain are suitable for reuse as-is, and that any required repair, leveling, or replacement due to field conditions will be treated as additional work. | Yes, the transformers with keynotes saying to retain existing pad are suitable for reuse. |
| 19. |  | Please confirm whether a specific phasing sequence is required by the Government or if the Contractor is solely responsible for developing and implementing the phasing plan to maintain continuous operations | The Contractor is responsible for the phasing plan, which requires VA approval. |
| 20. |  | In applying the Limitations on Subcontracting requirements under FAR 52.219-14 for this construction project, please confirm whether the “cost of the contract incurred for personnel” excludes all material costs, including those procured and installed by subcontractors, and that only the labor and service components are used in determining compliance with the 25% self-performance requirement | The Prime contractor cannot pay more than 85% the cost of the contract to subcontractors for labor. |
| 21. |  | We’ve been going through the bid package for PN: 656-22-341 and just wanted to check in on a few things. From what we can see, the scope outlines the transformer replacements pretty clearly, but we’re not seeing the detailed specifications needed to build out an accurate equipment quote | The specifications were posted with the solicitation. Ask specific questions where more detail is required. Missing specification section 33 73 00 is included in the amendment. |
| 22. |  | Specifically, we weren’t able to locate the full sections for 26 12 19 (Pad-Mounted, Liquid- Filled, Medium-Voltage Transformers) and 33 73 00 (Utility Transformers), or any associated transformer documentation. Normally those would include the key details like ratings, voltages, impedance, losses, and configuration | These can be provided. Some of this information ratings, voltages, impedance, and configuration are on the sheets. Refer to EP601 and 602. Spec 26 12 19 begins at page 162 of 174 in the bid package. Spec 33 73 00 was missing and is issued as part of the amendment. |
| 23. |  | Could you point us to where those sections and drawings are included, or let us know if they’ll be issued in an addendum |  |
| 24. |  | Will certifications be required for medium voltage work | Yes, submit proof of The National Electric Safety Code (NESC) or equal training. |
| 25. |  | On the bollards, they talk about crash rated bollards | See specification 34 71 13 PASSIVE VEHICLE BARRIERS. See detail 4 on sheet EK501 |
| 26. |  | What is the expected down time on these transformers? a. Will it vary per transformer or is there an average that you would expect the building to be down? | It will vary with each transformer depending on size and function of the building. |
| 27. |  | Building off of the outage, can you schedule for like a federal holiday for those online to be closed? | Work will not be allowed on Federal Holidays. |
| 28. |  | Is this a trade partners/ example Buy American Act vs. Nafta | Buy American Act |
| 29. |  | Staging Area? | For staging, we will allow one semi trailer sized parking stall and one 48’X36’ area Contractor can fence and lock in the contractor parking lot East of B57. Location of which stall and which staging area will be determined closer to start of construction based on vacancies at that time. |
| 30. |  | Is there any factor except testing on any of the equipment that was provided? - Can you say a little about factory acceptance testing? - Is a representative needed to be able to see the work A factory representative for on-site tests? | - The government reserves the right to witness factory testing. An example is paragraph 2.5.1 of specification 33 73 00. - Field quality control acceptance tests require an on-site manufacturer’s representative when required in the specifications. An example is paragraph 3.2.1 of specification 33 73 00. |
| 31. |  | Were you going to be able to see the connection types? - Going to be terms full breaks, dead breaks? - Vaults? | - Refer to Note B of Demolition General Notes on sheet E-001. - No vaults |
| 32. |  | Then to go off of auto duration, you know if there was provisions for backup that was written down. | Question is not clear. |
| 33. |  | I’m also guessing that, probably gonna go with a more efficient unit. | A more efficient unit is preferred, though not a requirement unless in the specifications. |
| 34. |  | We may be changing well heights, that will determine the downtime a. How are we supposed to identify what type of termination types? Are we actually able to see this? | Yes, photos are available for most of the transformers with the bay doors open which show the terminations. |
| 35. |  | Can we confirm that anything is in a Raceway? | Concrete encased duct bank will remain and be used. |
| 36. |  | Are we fighting any sort of provisions? To protect those, should we be parking on a DUCT bank? a. Imagine Locates on the contractor. b. Anything more than the factory test is that necessary on site as well? | Concrete encased duct bank will remain and be used. - Locates and imaging are the responsibility of the contractor. - The tests required for Part 3 in the specifications need to be performed. |
| 37 |  | Will it be in TTR’s or other for the units again? | Yes, this should be part of factory testing. |
| 38. |  | Is there a witness that needs to be there? | Yes. |
| 39. |  | Do you have a site personnel member doing the switching? | VA staff with either open our MV loop, or deenergize the transformer, as required. Contractor will place their Lockout devices for the duration of their work. Coordinate at least 2 weeks in advance with COR. |
| 40. |  | Responsible for that procedures related as well as reinitiation. | See Answer to 39. |
| 41. |  | Do we need to have construction fencing? | It is the contractor’s responsibility to contain and protect each construction area during construction per the general conditions. |
| 42. |  | Cabling too short? When the cabling is too short | Medium voltage cables can’t be spliced. The intent is to set the transformer so that the MV cables can be re-used. Cables 480 volts line-to-line can be modified. |
| 43. |  | Concern when cable is destroyed through the process, want to see cables, terminations, and sizes. | Refer to GENERAL NOTES on most ED and ES series sheets. Damage during demolition shall be repaired or replaced at no additional cost to the VHA |
| 44. |  | Other than that, is there any cable that’s getting replaced, assumption is the cable are ok. | Design is based on reusing existing cables. |
| 45. |  | Will VA be taking possession of any of those transformers being removed? | We will retain TF1C, salvage, protect and return to VA Shops. All others to be removed from the site by Contractor. |
| 46. | 01 00 00 - 14 | During MV building transformer replacement, how long can normal power be shut down? Spec. section 01 00 00-14 indicates to maintain utility service at all times. | This will vary per building. Contractor to propose schedule for approval. Most of the buildings have backup generator power available. Please see included outage description for each building. |
| 47. | 01 00 00 - 17 | Spec section 0100 00-17 mentions PCB's. Do any of the current transformers contain PCB's? | No, none of the transformers contain PCBs |
| 48. | Division 26 | Will replaced building transformers require new ground rings? | No, connect to the existing ground |
| 49. | Division 26 | Will cable tests be required on MV cables if the cable requires no splicing i.e. cables are of sufficient length? | Yes, a record is needed of the cable condition before being reconnected. |
| 50. | Division 26 | Will secondary low-voltage cables require testing if they are long enough? | Yes, a record is needed of the cable condition before being reconnected. |
| 51. |  | Transformer specification indicates a Delta primary connection. Is that also the case for the two loop feed transformers? | These transformers are wye as shown on sheet EP601 |
| 52. | 26 05 73 | Spec. section 26 05 73 indicates to perform a power system study. There is a note about the study incorporating the MV loop and transformer feeders. Will any of the changes recommended from this study be a project change - if incorporated? | No, not as part of this project. |
| 53. | 34 71 13 | Will an Engineer be required for the bollard structure and bases as indicated in Spec. section 34 71 13? | Yes, as said in paragraph 2.2.A. |
| 54. | A1-3e | Request Clarification of adherence to "Buy American Act" | Please reference FARR 52.225-12 |
| 55. | A1-3e | Are all existing termination types accurately listed with Transformer details? | Detail 9 on sheet EK501 tries to show the existing terminations. Best to also look at the photos to see which termination type relates to which transformer. |
| 56. | A1-3e | Are all new transformer locations required to have ground rings? EK501 | Use existing grounding. |
| 57. | A1-3e | What fences require grounding? | No fences will need grounding |
| 58. | A1-3e | Will existing XFMR primary and secondary wire sizes be provided? | The included photos show cables. The cable markings are not readable. |
| 59. | A1-3a | Confirm this contractor is responsible to salvage from site all XFMR equipment. | We will retain TF1C, salvage, protect and return to VA Shops. All others to be removed from the site by Contractor. |
| 60. | A1-1a +b | Confirm existing primary and secondary conductors for new 6000kVA XFMR primary and secondary conductors are sufficient. | The primary and secondary conductors are adequate. |
| 61. | A1-3b | Will a large lay down area be provided for duration? | For staging, we will allow one semi trailer sized parking stall and one 48’X36’ area Contractor can fence and lock in the contractor parking lot East of B57. Location of which stall and which staging area will be determined closer to start of construction based on vacancies at that time. |
| 62. | A1-3e+f | Is the expectation onsite storage and staging of new XFMR is expected? If so, is there an area designated for secure contractor staging? | For staging, we will allow one semi trailer sized parking stall and one 48’X36’ area you can fence and lock in the contractor parking lot East of B57. Location of which stall and which staging area will be determined closer to start of construction based on vacancies at that time. |
| 63. | A1-3c | Is there anticipation dust control needs for ICRA? | Transformers are outdoors. |
| 64. | A1-3f | Requesting underground steam tunnel locations. | This is not a part of this project and will not be available. |
| 65. | A1-1a+b | What are the time limits on any/all outages? | Contractor to submit schedule for approval showing proposed duration of outages for each building. |
| 66. | A1-1b | Clarification from Engineer for Revision A clouds on EP602. Specifically, the cloud near bottom of page around equipment fuses upstream of XFMR fuses. | The cloud is to show some of the 4 way switches have fuses. |
| 67. | A1-4a | Are 3rd party compaction tests required? | Yes, where new transformer pads are installed. |
| 68. |  | Requesting Geo Tech Reports, if available. | No Geo Tech borings were done during design. |
| 69. |  | In Spec Section 26 12 19 - 7, 2.9 (D) states that transformer impedance shall be not less than 4.5%. The power one-line diagram on EP602, show multiple transformers with an impedance less than 4.5%. | Transformer impedance shall not be less than 4 ½% for sizes 150kVA and larger. Impedance shall be as shown on the drawings. |