Questions & Answers

| Vindicator Intrusion Detection System Installation Services, Tyndall AFB, FL. – SAM Notice ID FA481926Q0011 |  |  |
| --- | --- | --- |
| No. | Questions | Government Responses |
| 1. | How old is the facility? | CSA ~1984 SAPF ~1994 with Renovation in 2023 |
| 2. | How much square footage is in the facility? | Approximately 2500 sq ft |
| 3. | How stable is the power? | 100% stable – Whole facility UPS and Generator Power |
| 4. | Is there a dropped ceiling in all areas of installation? | All rooms with the exception of Comm Room 100 and Room 208 |
| 5. | What type of walls are in the perimeter areas? | Concrete |
| 6. | Do we need to drill between the walls, to run our cable infrastructure? | It depends – existing holes with fire caulk – new drilling will need MAJCOM coordination/approval as long as it is IAW with 705 standards. |
| 7. | Do we need to use conduit? | The contractor must provide all additional conduit, junction boxes, and pull boxes where required. All installation shall be IAW the approved equipment list, regulations and codes |
| 8. | If yes, what do you estimate the total conduit footage will be? | Depends on your runs |
| 9. | Are the door frames metal and concrete filled? | Yes |
| 10. | Please provide a comprehensive list of quantities of all IDS items needed (e.g. total number of motion sensors, glass breaks, etc.) per location. | It will be a 1 to 1 swap. Contractor will decide if more equipment is needed to ensure complete coverage and all installation shall be IAW the approved equipment list, regulations and codes. |
| 11. | Do you currently have existing IDS Sensors in your doors? | Yes |
| 12. | Please specify which doors. | All exterior doors |
| 13. | What is the manufacturer of the existing IDS system? | Honeywell Vindicator |
| 14. | Will we be able to reuse the existing cable? | NO, must install without impact to current system |
| 15. | Are Ceilings Suspended? | Yes, Suspended. All rooms with the exception of Comm Room 100 and Room 208 |
| 16. | Are there existing Cable Trays for wiring above ceilings? | Yes and No |
| 17. | Can Existing Wiring be utilized? | NO |
| 18. | Is a “UPS” required? | Yes but depending on Manufacturer requirements, please see approved listed attached in sow. Building will always have electricity. |
| 19. | If so, What Time/Power Duration is required? | 15 minutes to fully support the system and reporting |
| 20. | Are “Or Equal” Equipment substitutions allowed? | Depending on which equipment, IAW approved list attached and must be legal. |
| 21. | Is “Plenum Wire” acceptable? | Depends on manufacturer requirements IAW approved list attached. |
| 22. | Is “After Hours Access” for said work, available to contractor at no add’l cost to the Gov’t? | NO, see SOW for hours. During burn-in a technician should be in local area to respond. |
| 23. | What is the height of Exterior Cameras? (If any) | N/A (none required) |
| 24. | Please provide/post other “Q & A” requests. | Yes |
| 25. | Please provide a list of equipment and parts # that are to be installed. | All items on SOW are suggested and approved from gov’t. - 5 BMS - 2 access control devices with new technology IAW IFC (eg strike or mortis) See attachments 2 and 3 for 1-1 swap and at the contractor's discretion as area needs to be ADEQUATELY covered (new solutions are ok). |
| 26. | Are there pipe chases between floors? | Single floor only |
| 27. | What is the range of the budget for this project, and is it already appropriated? | Cannot answer this question |
| 28. | Because of the high cost of the parts can we bill when parts arrive on site, or in the alternative are progress payments allowed? | No |
| 29. | How many feet of new wire will have to be run? | Depends on how your company designs the system. As-builts are provided in SOW with intended locations for the hardware to be installed |
| 30. | What kind of cipher lock and quantities are required e.g. X-10 Newest Authorized by DoW | Newest Authorized by DoW, meeting 705 and 1404 requirements. |
| 31. | Please post the sign in sheet and Q&A's from the site visit. | posted |
| 32. | Please post the drawings and the key for the drawings. | Listed in SOW |
| 33. | Will Base Communications have network pathways built/configured for the new systems? | Coordinate with simpleSENCE & BDOC to plug into OT switch. |
| 34. | Will Base Communications provide new IP addresses assigned for this project with prior coordination and provide the switch with at least 6 available ports (2 in open storage, 4 in SCIF)? | NOT A SCIF, it’s a SAP Annex. Will need coordination with simpleSENCE & BDOC. |
| 35. | Will Base Communications personnel install conduit and data cabling from communications closets to the new panel locations? | No |
| 36. | If the vendor is responsible for new data connections, are there specified cable color coding standards that must be followed? | No as long as its within cable rules and IAW security directives and instruction |
| 37. | What is the distance between the electrical panel source and each new panel installation location? | It depends. Contractor to provide solution. |
| 38. | Is the new security installation required to comply with ICD 705 for all wiring and conduit? | Yes |
| 39. | Are all wired junctions required to include tamper protection? | Yes |
| 40. | Is the use of JB Weld (or an equivalent) required for securing all conduit connections? | As long as it complies with approved list |
| 41. | Will the ESS section provide all additional alarm points required to meet installation requirements? | Yes |
| 42. | Will you waive the 72-hour prior notice request to the vendor to the ESS section for preprogramming activities? | No |
| 43. | Will the vendor have access to existing ACS programming, or will this information be provided by the government? | Yes, requires comms approval |
| 44. | Is the vendor responsible for all system programming and setup, or will ESS handle any portion of the configuration? | Yes, installation and programming. |
| 45. | The SOW states that advance requests are required for access to ESS and the installation site; Will the vendor be allowed to request specific blocked dates and times for access? | Yes, and access will have to be approved by customer – normal duty hours |
| 46. | Is the 14-day advance notice requirement for site access still mandatory for all personnel, and can this be adjusted to avoid project delays? | Adjustable to keep on timeline if all parts are available |
| 47. | Will the 72-hour advance notice requirement for IDS and VCC programming be flexible to accommodate testing and necessary adjustments during installation? | No |
| 48. | What is the current ESS/BDOC firmware or system version in use? | Yes, we will provide upon award. |
| 49. | Due to space constraints with parallel systems, would the end user consider a phased installation approach (e.g., panel configuration completed first)? | It depends – This is a new independent system installed separately from current system. User will make additional space available as required depending on need (plenty of available space). |
| 50. | Will a SAW or separate V5 system be provided for the new installation, given that SCIF systems cannot reside on open storage systems, or is the vendor responsible for providing this? | Contractor will provide equipment, it's not a SCIF |
| 51. | Will DBIDS include including weekend coverage for the one-year warranty support period, to meet emergency service requirements as outlined in Section 1.2.1? | DBIDS only cover the installation period – any warranty work will require additional coordination for base access. |
| 52. | What is the expected project completion timeline? | Estimated completion by 150 days ARO. |
| 53. | Can the Government provide additional details on the current ESS architecture and BDOC head-end configuration? | No |
| 54. | Are there any known limitations to integrating new PCUs and Site Commanders into the existing system? | No |
| 55. | Will the Government provide access to existing system configuration files or databases? | Yes, as required after receipt of award |
| 56. | Can the Government provide the current Honeywell Vindicator firmware versions to ensure compatibility? | Yes, we will provide upon receipt of award |
| 57. | Can the Government confirm whether the V3 platform can support the number of additional IDS sensors required, given the Premise Controller point limitations? | Vendor shall provide new parallel installation. Replace and then remove – system can not be shut down at any time. |
| 58. | Can the Government confirm whether tamper circuits must remain discrete, or if a multistate configuration within the Honeywell Vindicator system is acceptable? | Listed IAW ICD 705 and 1404 |
| 59. | Can the Government confirm that existing penetrations through the concrete envelope may be reused for this effort? | On a non-interference basis and at no risk to current system. New penetrations shall require MAJCOM approval |
| 60. | Can the Government confirm that there is no motion alarm system located beneath the raised floor? | No motion sensor beneath the raised floor |
| 61. | Will the Government be responsible for provisioning the new system? | No |
| 62. | Can the Government confirm that the existing badge readers are HID or equivalent and compatible with the proposed Honeywell system, and that they will not be covered under warranty? | Treat like new build system w/ new badge readers required, no repurposed parts |
| 63. | Will the Government be responsible for all required connections to BDOC? | Yes, coordination through simpleSENCE will be required. Government will connect. |
| 64. | Are there any asbestos or hazardous material concerns in Building 503? | No - all hazardous materials have been remediated in the facility. |
| 65. | Will the Government provide access to existing conduit pathways, or should the Contractor assume new conduit runs? | Yes, new conduit will be required. All installation shall be IAW the approved equipment list, regulations and codes |
| 66. | Does the existing conduit have enough spare capacity for new cabling, or should the Contractor assume replacement? | Assume replacement if required |
| 67. | For Rooms 205/206 and 119, where walls were removed, is the Government amenable to reinstalling only one PIR per room? | Only if sufficient coverage is realized. Rooms 205/206 and 119 should have a one for one replacement. Rooms 100 and 208 require a mounting solution that does not require a suspended ceiling. |
| 68. | Should the Contractor install a new ceiling grid to permanently affix components? | Rooms 205/206 and 119 should have a one for one replacement. Rooms 100 and 208 require a mounting solution that does not require a suspended ceiling. Replacement required if damaged by contractor. |
| 69. | What are the expectations for maintaining continuous IDS coverage during installation? | Ensure full system control and coverage with current IDS until the new system is certified, approved, and released to the customer. |
| 70. | Are temporary systems or phased cutovers required? | No - current system will provide coverage until the new system is in place and certified. |
| 71. | Are there blackout periods or operational constraints? | No access outside of normal business hours; Monday through Friday 0700-1800 Access will not be allowed on Weekends, Holidays, and/or Goal days |
| 72. | Will the Government provide a formal Acceptance Test Plan (ATP), or must the Contractor provide one? | Contractor will provide test plan with government oversight and approval |
| 73. | Who is the approval authority for verification testing, Government acceptance, and 72-hour burn-in? | 3- part approval required: Alarm CDN End User |
| 74. | Can the Government clarify interface requirements between the IDS and ACS V3? | Yes, after receipt of award |
| 75. | Will ACS programming changes be required? | Yes |
| 76. | Are RMF or ATO requirements applicable? | Yes, in coordination with SimpleSENCE |
| 77. | Will the Government guide network accreditation and authorization? | Vendor will provide test plan with government oversight and approval |
| 78. | Are specific naming conventions or CAD standards required for as-builts? | Yes, will be provided after award and in coordination with SimpleSENCE |
| 79. | Should credentials be delivered in a secure, specific format? | Yes. Follow DBIDS submission process |
| 80. | Can the Government provide any existing as-built drawings? | Check updated SOW for new as-builts |
| 81. | What is the expected Period of Performance? | Estimated completion by 150 days ARO |
| 82. | Are there known long-lead items? | Vendor to identify long lead times for items |
| 83. | Will sales tax be required? | Sales tax for products delivered under this may be waived with exemption |
| 84. | What is the anticipated timeline for base access approval? | Typically,10 days and IAW SFS approval requirement |
| 85. | Will the Government issue a DD254 to allow SCI/SAP-eligible personnel to work unescorted? | CI/SAP-eligible personnel will be preferred but not required |
| 86. | If no DD254 is issued, will escorts be required, and who will supply them? | Escorts will be required as necessary; Gov’t will provide escort personnel during duty hours |