United States Department of the Interior

U. S. GEOLOGICAL SURVEY

Columbia Environmental Research Center (CERC) 4200 New Haven Road

Columbia, Missouri 65201

STATEMENT OF WORK

Administration Building (A3) Well Water Recirculation Pump

## GENERAL INFORMATION

  - INTRODUCTION. The Department of the Interior (DOI), U.S. Geological Survey (USGS), Columbia Environmental Research Center (CERC) 4200 New Haven Road, Columbia, MO 65202 has a requirement for an electrical upgrade to include but not limited to removing and replacing a centrifugal pump and installing a variable frequency drive (VFD) with supporting controls.

  - BACKGROUND. The Columbia Environmental Research Center (CERC) conducts research needed to address national and international environmental contaminant issues and the effects of habitat alterations on aquatic and terrestrial ecosystems. The Administration Building(A3) at CERC is a 34,019-square-foot research laboratory building that houses several research laboratories, office space, a research flume, and a 6,000-square-foot research wet laboratory. A3 currently has; one 10 hp centrifugal pump with a manual motor starter.

## DEFINITION/APPLICABLE DOCUMENTS.

    - Attachment 1_Pictures

    - Attachment 2_Pump Curve

  - SCOPE. The contractor shall provide all materials, labor, equipment, travel, and supervision necessary to remove and replace the existing centrifugal pump and install an appropriately sized VFD (Variable Frequency Drive) and supporting controls.

- WORK REQUIREMENTS

  - TECHNICAL REQUIREMENTS

    - Existing Site Conditions.

      - 10 hp, 3-phase, 230v, centrifugal pump- 4” end suction, 3” top discharge

      - Manual motor starter

## CONSTRUCTION.

      - All circuits shall be installed to the existing Local and National Electrical Code Standard.

      - Remove the current pump and replace with two (2) redundant inverter- duty centrifugal pumps that meet current needs and support future growth.

      - Remove the current motor starter and replace with a properly sized VFD and accurately sized circuit protection.

      - New pump(s) shall be capable of a minimum of 120 feet of head up to maximum of 200 feet of head.

      - New pump(s) shall be capable of flowing 200 gallons per minute of water.

      - The VFD shall have a bypass function.

      - The VFD shall have BACnet capabilities.

      - Install a digital flow meter with BACnet capabilities.

      - Install digital pressure gauges with BACnet capabilities on the suction and discharge piping.

      - Remove and replace the current piping to allow redundancy.

      - New piping shall have a bypass installed.

      - Pumps shall sit level and be easily accessed for maintenance/replacement.

## POST CONSTRUCTION TESTING AND COMMISSIONING.

      - The Contractor shall provide operational and maintenance training to the CERC maintenance staff.

      - The contractor shall be responsible for a 12-month warranty on the panelboards and transformer beginning on the start-up date.

## DRAWINGS.

      - Contractor shall produce all shop and drawings needed for the job performance.

      - The Contractor shall keep copies of the drawings and specifications on the job and shall at all times make these available to the USGS Technical Liaison upon request. Any item provided for in the specifications or drawings shall be considered as being shown or provided for in both. In any case of discrepancy in the figures or drawings, the matter shall be immediately brought to the attention of the USGS Technical Liaison, without whose decision said discrepancy shall not be adjusted by the Contractor, save only at its own risk and expense. The USGS Technical Liaison may furnish from time to time such additional drawings or other information as the USGS Technical Liaison may consider necessary.

      - The USGS Technical Liaison may, at any time, by written order, make changes in the drawings and/or specifications of this contract and within the general scope thereof. If such changes cause any increase in the amount due under this contract, or in the time required for its performance, the Contracting Officer shall approve such changes and issue a modification to reflect such changes in writing. Changes in the

scope of performance, or changes which result in increases in cost, must be approved by the Contracting Officer by modification.

      - Any measurement(s) provided by the owner are approximate. Exact measurement(s) are determined by the independent measurements made by the Contractor. There has been a certified electrical peak demand load test completed for the additional power requirements.

## GENERAL REQUIREMENTS

    - Schedule. Within five (5) calendar days after the notice to proceed is issued, the Contractor shall submit in writing to the USGS Technical Liaison a schedule of construction for the project. The schedule shall indicate the dates of the periods of time that the Contractor intends to be on site. The schedule shall indicate the dates that major components of the work will be accomplished. When preparing the schedule, the Contractor shall consider lead times for utility outages, permit requirements and material/ equipment procurement, and shall consider the permitted hours. The Contractor shall notify the USGS Technical Liaison immediately if any anticipated on-site date is expected to change from the original schedule. The Contractor shall be responsible for determining the labor staffing levels needed to complete the project by the established delivery date. Reference Utility/Service Interruptions in Section III. e. for power disruption occurrences.

  - WARRANTY. The Contractor shall warranty all workmanship to meet the specifications set forth in this Statement of Work. Additionally, the Contractor shall warranty all Contractor workmanship for a (minimum) period of 12 months from the date of Government acceptance.

## SUPPORTING INFORMATION.

  - GOVERNMENT FURNISHED PROPERTY (GFP): None.

  - SECURITY. Building access shall be coordinated with the Facility Manager or USGS Technical Liaison.

  - PLACE OF PERFORMANCE. USGS, Columbia Environmental Research Center (CERC), 4200 New Haven Road, Columbia, MO 65201

  - PERIOD OF PERFORMANCE. 30 days from Notice-to-Proceed (NTP)

  - SITE VISIT WILL BE CONDUCTED.

## SPECIAL CONSIDERATIONS

    - The CERC normal facility business hours are 7:00 AM to 4:00 PM, Monday thru Friday.

    - Utility/Service Interruptions: The Facility Manager and USGS Technical Liaison shall be notified not less than 5 business days in advance of any interruptions of building utility/services. The contractor shall describe in writing the work to be done and the time and duration of the interruption. No work shall be done until approval is received from the USGS Technical Liaison. Power disruptions shall be no more than 24 hours in a single instance.

      - The Contractor shall coordinate deenergizing and re-energizing of Utility Power concurrently with the USGS Technical Liaison and Utility five

business days in advance of the work that requires coordination with Utility power. Cost incurred by the deenergizing and re-energizing of Utility Power will be included in the Contractor’s quote.

    - The contractor shall be responsible for complying with all National, Federal, State and local laws, codes and regulations in connection with the execution of the contract.

    - Contractor is responsible for visiting the worksite to verify measurements and to ascertain the nature and location of the work to be performed and the general and local conditions which can affect the work or the cost thereof. Failure to do so will not relieve the contractor of his responsibility for estimating properly the difficulty or cost of successfully performing the work.

    - Occupancy: During construction the Government will occupy the existing facility. The contractor shall not restrict nearby pedestrian or vehicular traffic to this facility and shall coordinate construction with the Contracting Officer to minimize conflicts and to facilitate usage. The contractor shall perform the work so as not to interfere with ongoing operations.

    - Any changes affecting the scope of work shall be originated from and approved by the Contracting Officer.

    - All materials and workmanship shall be subject to the inspection and approval of the USGS Technical Liaison. All work unsatisfactorily performed shall be promptly corrected and made acceptable to the Government at no additional Cost.

    - Final inspection and acceptance shall be performed with the contractor, on site by the USGS Technical Liaison upon completion of job performance.

    - MATERIALS. The contractor shall furnish all supplies, materials, and equipment necessary for performance of the work included in this contract unless otherwise specified. Materials and supplies to be used shall be commercially available products of reputable manufacturers or suppliers and shall be of a quality to conform to applicable Federal Specifications.

    - SPECIFICATIONS. In any case of discrepancy in the specifications, the matter shall be immediately submitted to the Contracting Officer, without whose decision said discrepancy shall not be adjusted by the Contractor, save only at his own risk and expense. Any changes affecting the scope of the work shall originate from and be approved by the Contracting Officer.

    - SCHEDULING CONTRACT WORK. The contractor shall make necessary arrangement with the Facility Manager and USGS Technical Liaison to perform the work and shall arrange and schedule his work so that the minimum amount of interference with government activities will result.

    - USE OF BUILDING FACILITIES. The contractor may use utility services and toilet facilities of the building subject to approval of the Facility Manager.

    - CONDITIONS AFFECTING THE WORK. It will be the responsibility of the contractor to inspect the site, determine quality of work involved. Compare the

specifications with the work to be done, and inform themselves as to all conditions, including other work, if any, being performed. Failure to do so will in no way relieve the successful contractor from the necessity of furnishing any materials or performing any work that may be required to carry out the contract in accordance with the true intent and meaning of the specifications without additional cost to the Government.

    - EMPLOYEES. The contractor shall be responsible at all times for the supervision and control of the employees that may be assigned to render services under the contract. Fully qualified work personnel shall be available for work on the date this purchase order begins and shall be maintained throughout the period of performance.

    - LICENSES-PERMITS. The contractor shall, without additional expense to the Government, be responsible for obtaining any necessary licenses or permits, and for complying with any Federal, State, and Municipal laws, codes and regulations in connection with the execution of the work.

    - ACCIDENT PREVENTION AND FIRE HAZARDS. The contractor shall take all necessary precautions to prevent fires or injury to the public, building occupant(s), or damage to property of others during the performance of this contract. For the purpose of this contract, the public or building occupant shall include all persons not employed by the contractor or a subcontractor working under his/her direction. If welding is required, permission shall be obtained from the COTR.

    - INDEMNITY. The contractor shall confine all work on Government premises to areas authorized or approved by the Contracting Officer or COTR. The contractor shall save and keep harmless and indemnify the Government against any and all liability claims, and costs of whatsoever kind and nature of injury to or death of any person or persons and for loss or damage to any property (Government or otherwise) occurring in connection with or in any way incident to or arising out of the occupancy, use, service, operations, or performance of work in connection with this contract, resulting in whole or part from the negligent acts or omissions of the contractor.

    - GREEN ACQUISITIONS. The USGS is committed to promoting the natural environment and protecting the health and well-being of people. In the performance of work under this contract, the Contractor shall exert its best efforts to provide services in a manner that will promote the natural environment and protect health and well-being. Green purchasing or environmentally preferable contracting includes the initiatives described below:

      - Alternative Fuels and Vehicles are described at http://www.afdc.energy.gov/afdc/

      - Biobased Products are described at http://www.biopreferred.gov/

      - Energy efficient products are described at http://energystar.gov/products for Energy Star products and at

http://www.eere.energy.gov/femp/procurement for FEMP designated products

      - Environmentally Preferable Computers are described at http://www.epeat.net

      - Significant New Alternatives Program (SNAP) are described at http://www.epa.gov/snap/overview-snap

      - The Comprehensive Procurement Guidelines promote the use of recovered and recycled products at http://www3.epa.gov/epawaste/conserve/tools/cpg/index.htm

      - Water efficient products and services are described at http://www3.epa.gov/watersense/about_us/what_is_ws.htm